# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 23 June 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  82 F

RANGE: 78 to 87

SITE CONDITIONS: cloudy morning, heavy rain afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt (R&R)

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Paul Olivo – Materials

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local) parcial

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Safety					1

Foremen				3

Electricians				0

Operators				0                        Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				10

Helpers				4

Welders				2

Total:					35

- GENERAL ITEMS:

  - Contractor to work ½ day tomorrow and no work Friday, Saturday, or Sunday.

  - The core drilling of the 7EA foundation showed porosity in the concrete from about 8” to 12” into the foundation.  The cores will be tested tomorrow.  One core penetrated a conduit, even though we had a metal detector locate the installed bar and conduits before drilling.  We will repair after the cores are tested.

  - Contacted a pressure grouting company to come to site to prepare a quote and advise what is necessary to start this work as soon as possible.  No response today, have asked to locate another company.

  - Little work on 7FA foundation, the anchor bolts and Unisorb pre pour package are not on site.  Lack of anchor bolts is a day per day delay to schedule.

  - We poured 7EA stack this morning.

  - Will poured 7EA PEECC bases this morning.

  - The mud mat for oily water separator may pour next week.  We were not able today.

  - Kyle completed an audit of the drawings the contractor is using with no findings this week.

  - The PEECC rebar detail for the columns was rejected by Sidor’s engineering today, will require we re-bend the bar.  The details on the foundation are different than the details under general notes.

  - We prepared the PO for signature and hopefully will start excavation for duct bank next week.  We will modify the IFC sketches previously delivered by EDGI.

  - Need plot plan showing reduced BERM for Diesel tank, need to determine if moving the Over Head 13.8 line is necessary.  This is also essential in starting the storm drains.

  - Need to order Geo Tech Membrane for Treated fuel oil tank.  Commercial issue

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, will conclude the piping when possible.  Finished Soil Change order take off to finish the CO for Derwick

  - The erection of the crane is not completed.  CO 002 to Derwick pending for soils.

  - GSU embeds PO on hold commercial, when released need to include in the air freight from US with anchor bolts for 7FA

- CLIENT ISSUES/CONCERN:

  - Client is asking to move one person into our office at site.

  - Client advised they do not accept the response from EDGI regarding location of Treated Fuel tank.

  - Client has sent a flurry of e-mail to EDGI regarding engineering issues.

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor has provided one container for wood and trash, still require one for steel scrap.

- CIVIL:

  - 7EA stack foundation pour delayed until next Wednesday

  - Lack of anchor bolts for 7FA foundation continued delay; Contractor will be working on PEECC columns and oily water separator.

  - Lack Embeds for PEECC need by 28 June, the base for PEECC is poured.

  - Lack Piping for U/G.  Material on hold in Houston to ship PO INTL4475 Genoyer

  - Oily water separator water stop on site.

  - Lack of resolution for Treated Fuel Oil Tank location.

  - Preparing PO for local purchase for Geotech membrane.

  - Soils where crane must be located are not suitable for setting crane to install turbine and generator on 7EA.  Prepared CO number 002.

- CONCRETE FOUNDATIONS:

  - Work today on the 7FA was halted by contractor.

  - Issued RFP for 7FA Unisorb anchor bolts, local cancelled

  - Issued RFP for PEECC embeds. On hold

  - Contractor drilled cores to test for the 7EA.  Will test cores tomorrow24 June at 2PM, have asked Sidor to witness test.

  - Wrote change order CO002 based on contractor quotation for crane backfill and extended overhead asking for 14 day delay.  This might not be enough based on commercial issues.

- MECHANICAL:

5.1 The 7EA generator replacement jib base plate arrived at site at about 8AM. Jason Byrd has completed Welding Jib plate.

5.2 Will issue PO for start of 7EA stack repairs and erection, Monday (pending receipt of quotation from ISI.

5.3 Plan to set 7EA turbine and Generator if crane is available next week.

- PIPING:

6.1 Review ongoing of material takeoff for bulk order of piping.  Received the PO from Pam Arnold for Genoyer

6.2 Received BOM U/G piping from EDGI.  Sidor has indicated we should treat any area where crane can cross as a road crossing.

- ELECTRICAL:

  - Loaned 2000 lf of conduit to Site A.  They will order to replace it, will need it within 2 weeks.

  - Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed.  This is a safety issue.  On hold awaiting resolution of commercial issues, with all the rain we have asked this be turned on.

  - Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues, spoke to Sidor today for this and will prepare a CO to Derwick.

  - The embed plates for the GSU 7EA, PO prepared and quotation available to order the embed plates.  On hold

7.5 The sub contractor Coinserma prepared a new bid.  The execution of this scope will require a large amount of PES time to supervise this work.  We received and e-mail from EDGI, we will cancel the manholes drawings and use Sidor’s design.

7.6 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Commercial issues are resolved to local purchase materials

- Contractor increases manpower to work in all areas

- Contractor works two shifts

- The Underground and duct bank is started week of 7 June and does not slip more

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) see above

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) see above

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*)

* Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known.

9.3 Payment milestones

- Unit 100 – 7EA

Nov 29, 2010 (*)

- Unit 200 – 7FA

Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - The 7EA foundation concrete breaks are below acceptable; the core drilling has indicated an area in the suspect zone of porous concrete.  We are looking for a pressure grout company to grout this zone.  This can be done if necessary with Turbine and Generator on fdn.

  - Sidor provided crane setup now ongoing, crane expected to be completed next Monday.

  - Lack of materials (anchor bolts 7FA, embed plates 
PEECC 7EA

  - Changes in designs are impacting project progress/completion.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings new forecast 28 June, for issued for construction drawings

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - Unable to connect to internet today.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Will pour when crane moves after setting unit 100 turbine generator |
| Balance of FDN drawings | 25May10 | 3Jun10 |  |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 |  |
| U/G piping | 5May10 | 28May10 | comments |
| GSU 7FA | 21May10 | 2 Jun10 | Not critical |
| Duct Bank | 17May | 28 June 10 |  |
| Design essentially complete | 31 May | No forecast date | No forecast date |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

10.11.2 After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  Received a SK 102 for information showing elevation below grade for top of conduit

  - ISSUED DRAWINGS:

11. PICTURES:

Photo 1: Oily Water Separator Forming

Photo 2: Pour 7EA Stack

Photo 3: Sidor crane erection

Photo 4: 7EA PEECC rebar re-work, column horizontals 90 degree bends