# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 28 May 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  85 F

RANGE: 80 to 93

SITE CONDITIONS: Cool morning, Rain afternoon stopped work

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager  R&R

Melinda Siros - Doc Control

Ysrin Gomez – Local Safety (Local)

Jason Bird - TA/7EA (A&B)

Keith McMurray - Scheduler (A&B)

Felix Martinez - QA/QC (A&B) R&R

Mark Hanks - Electrical Supt

Kyle Roskam - Civil Supt

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local)

Paulo Gomez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Foremen				2

Electricians				0

Operators				0                        Surveyor				1

Carpenters				4    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				4

Helpers				2

Welders				2

Total:					21

- GENERAL ITEMS:

  - We are getting close to a work stoppage due to the lack of IFC design drawings. We are in continuous discussions with EDG on this issue.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold.

  - Superintendents are preparing a material takeoff of drawings at site using a grid on plot plan and will generate purchase orders request accordingly.

  - 7EA was poured, but had issues with concrete quality and rate of delivery. Sidor immediately informed us 5-27-2010 that Saturday pour is not an option based on the issues last night. This would be a schedule impact to the project.

  - Contractor working a skeleton crew today due to the late night pour of the 7EA

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.  Materials deliveries are seriously impacting the ability to start this work.  The coordinates are finally on the sketch so we can start pull boxes (manholes) when the pour of the 7EA is completed, and forms are removed.

  - Request for purchase for trash bins for site lay down area and construction site on hold.

  - Sidor to produce fire water flow rates for Plant B, no forecast date provided.

- CIVIL:

  - The shelves for document control are forecast for delivery on 5-28-10 for the Site B Office.

  - When locking up at night leave the A/Cs on for the electronic equipment. Lights will be left on due to the problems with turning them on in the mornings. The lights were inspected by PES electrical and they use very little electricity so it is not an issue to leave them on 24 hours a day.

  - Concrete issues; requested a meeting with Sidor and both concrete batch plants for planning the 7FA foundation.  The rate and quality of concrete (rejection of trucks) is a major issue for the larger pour.

- CONCRETE FOUNDATIONS:

  - Contractor informed us that the owner of the company has changed his mind and will not supply any additional people or materials for near future.

  - Pouring concrete for 7EA foundation. Pour completed at 12:05 AM.

  - Concrete placed for the7EA Turbine Foundation, placing forms and rebar for Generator Pedestal

  - No work today on the 7FA due to the lack of manpower.  The work is progressing very slowly due to the lack of manpower and materials.

  - The rate and quality of concrete (rejection of trucks) is a major issue for the larger pour of the 7FA.  Called Gene Phillips last night when we got a probable “cold” joint in the 7EA foundation under the aux module.

- MECHANICAL:

  - 7EA generator replacement jib base plate is being fabricated in Sedalia. Tom Koontz will ship by air freight to site as soon as it is complete. Current forecast is 5-29-10.

  - Requested ISI to provide insurance certifications.

- PIPING:

- ELECTRICAL:

  - On 5-22-10 contractor stated he would start survey on manholes 5-24-10.  On 26 May performed final check of 7EA embedded conduits with QC. All conduits are in good condition “ready for pour”.  The layout of the duct banks can now be started after receipt of the coordinates for one pull box.  Planned start 2 June.

  - Will add a lighting breaker panel changing for office trailers. Will task manpower to wire Sidor safety trailer.

  - Concorcio gave us a list of materials for the site construction power transformer installation

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Plant B schedule is being modified to reflect current design. Forecast completion is 5-28-10.

- CRITICAL AREAS OF CONCERN:

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations. Sidor has requested a 4-5 day prior notification for concrete so they will have time for the cement to be loaded into the hoppers and cool down to support the pours.

  - Concorcio Megavatio will not supply additional manpower or materials due to commercial issues.

  - Due to the commercial issues PES has begun releasing the staff of the site.

  - Meeting requested with Sidor and both concrete batch plant managers to discuss quality and rate of flow for the concrete for future pours.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.

    - Concorcio Megavatio has not started installing warning labels on equipment and machinery. Formal letter will be written to contractor on this issue if not addressed by the next site meeting.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 |  |
| Balance of FDN drawings | 25May10 | No new forecast date |  |
| Treated Fuel Tank updated drawings | 29May10 | No new forecast date |  |
| U/G piping | 5May10 | 24May10 |  |
| GSU 7FA | 21May10 | No new forecast date |  |

    - Plot plans and foundation drawings all need to be on the same foot print.  New revision issued, expect all drawings will be revisited.

    - 20-001 sheet 1 rev 11 Plant B Foundation Location Plan; added coordinates for foundations, still missing foundations, some foundations missing locations, cut top of site plot plan off (doesn’t affect foundations) and  TOC schedule added is missing some of the associated unit numbers, 5-15-10. Engineering informed us that there will be some drawing sheet numbers not used. They will clarify this on their drawings to help eliminate confusion.

    - After review of the duct bank drawings Pro Energy requested EDG assess depth of conduits leaving hand holes, perform an evaluation for areas where load bearing equipment will be set up (cranes, forklifts, etc) over duct banks and if RGS conduit should be used in these areas with steel reinforced cage, 5-20-10. Coordinances were requested to be added to the drawings, 5-25-10, received coordinates for one pull box 26 May10.

    - Underground piping. Forecast 5-5-2010. Received revised 5-14-10; Drawing were reviewed with EDG and comments have been forwarded to their office for resolution. Forecast delivery 5-24-10. Engineering made a guess that the new revision should be released today. They were unsure when they would be issued, 5-25-10.

    - 7EA GSU foundation section views. Step Up Transformer Plan and Conduit Penetration Details 20-04 sheet 4; Title on sheet 4 does specify GTG-100 and sheet 3 not issued, 5-15-10. Step Up Transformer Grounding Plan 20-04 sheet 5; still has excessive ground penetrations in foundations and does specify GTG-100, 5-15-10. GSU delivery is forecast for 6-5-10 and EDG was requested in meeting 5-19-10 to complete the designs so we can be ready to set upon cure of foundation. Conduits appear to be interring the foundation in the wrong location, 5-25-10.

    - 7FA GSU foundation detailed drawings, forecast 5-21-10. GSU delivery is forecast for 6-5-10 and EDG was requested in meeting 5-19-10 to complete the designs so we will be ready to set upon cure of foundation. Revision forecast for 5-25-10. Engineering was unsure if the revision would be issued today, 5-25-10.

    - Balance of foundation details, 5-25-2010. Engineering stated they did not know when the balance of the foundations would be issued, 5-25-10.

    - Grounding Plan (Drawings are under review and PES has some issues and concerns with the designs).

    - 20-60 sheet 13 rev 0; Issued with “Hold Compressor Has Changed”. Revision number was not changed on drawing so there are now two revision 0’s.

    - EDG forecast all designs to be complete by 5-31-10. EDG stated completion date is going to slip and will supply a new date. Engineering stated in today’s meeting, 5-25-10, that they did not know when the designs would be completed.

  - ISSUED DRAWINGS:

- PICTURES:

Picture 1: Rebar work on the 7FA

Picture 2: Concrete placed in the 7EA

Picture 3: Preparations for the Placement of concrete in the Generator Pedestal