# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 31 May 2010, Mon # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  92 F

RANGE: 77 to 96

SITE CONDITIONS: Cool morning, extremely hot and breathless afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt

Kyle Roskam - Civil Supt

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local) medical leave

Paulo Gomez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Foremen				2

Electricians				0

Operators				0                        Surveyor				1

Carpenters				4    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				14

Helpers				2

Welders				2

Total:					31

- GENERAL ITEMS:

  - Had a two (2) day delay for no concrete available on Saturday for 7EA pedestal.

  - We are getting close to a work stoppage due to the lack of IFC design drawings. We are in continuous discussions with EDG on this issue.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold.

  - Superintendents are preparing a material takeoff of drawings at site using a grid on plot plan and will generate purchase orders request accordingly.

  - 7EA was poured, but had issues with concrete quality and rate of delivery. Sidor immediately informed us 5-27-2010 that Saturday pour is not an option based on the issues last night. This would be a schedule impact to the project.

  - Prepared a list of anchor bolts and RFP for same for the 7FA unit 200.

  - Poured the pedestal for 7EA.  Concrete trucks were not available until after 4PM.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.  Materials deliveries are seriously impacting the ability to start this work.  The coordinates are finally on the sketch so we can start pull boxes (manholes) when the pour of the 7EA is completed, and forms are removed.

  - Request for purchase for trash bins for site lay down area and construction site on hold.

  - Sidor to produce fire water flow rates for Plant B, no forecast date provided.

- CIVIL:

  - The shelves for document control are forecast for delivery on 5-28-10 for the Site B Office.  On hold

  - Concrete issues; requested a meeting with Sidor and both concrete batch plants for planning the 7FA foundation.  The rate and quality of concrete (rejection of trucks) is a major issue for the larger pour.

- CONCRETE FOUNDATIONS:

  - Contractor informed us that the owner of the company has changed his mind and will not supply any additional people or materials for near future.

  - Work today on the 7EA with small crew of manpower.  The work is progressing very slowly due to the lack of manpower and materials.

  - Need a Change Order or PO for the work to form and Pour GSU for 7EA

  - Need a Change Order or PO for the work to form and Pour PeeCC for 7EA

  - Need a Change Order or PO for the work to form and Pour Stack for 7EA

- MECHANICAL:

  - 7EA generator replacement jib base plate is being fabricated in Sedalia. Tom Koontz will ship by air freight to site as soon as it is complete. Current forecast is 5-29-10.

  - Requested ISI to provide insurance certifications.

- PIPING:

- ELECTRICAL:

  - Started survey for manholes today.  Need information on the offset between MH 1 and MH2, sent scan to EDG.

  - Will add a lighting breaker panel changing for office trailers. Will task manpower to wire Sidor safety trailer. On Hold

  - Concorcio gave us a list of materials for the site construction power transformer installation. On hold

  - The drawings for the 7EA (unit 100) GSU are still wrong, anchor bolt details to follow.  We will red line and continue.  Requires a change order to Concorcio.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Plant B schedule is complete, but manpower report received from Sedalia, on Sat., of electrical hours is not reflected. Underground and duct bank is critical path.

- CRITICAL AREAS OF CONCERN:

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations. Sidor has requested a 4-5 day prior notification for concrete so they will have time for the cement to be loaded into the hoppers and cool down to support the pours.

  - Meeting requested with Sidor and both concrete batch plant managers to discuss quality and rate of flow for the concrete for future pours.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.

    - Concorcio Megavatio has not started installing warning labels on equipment and machinery. Formal letter will be written to contractor on this issue if not addressed by the next site meeting.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Issued new, but still oriented wrong |
| Balance of FDN drawings | 25May10 | 3Jun10 |  |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 |  |
| U/G piping | 5May10 | 28May10 |  |
| GSU 7FA | 21May10 | No new forecast date |  |

    - Plot plans and foundation drawings all need to be on the same foot print.  New revision issued, expect all drawings will be revisited.

    - 20-001 sheet 1 rev 11 Plant B Foundation Location Plan; added coordinates for foundations, still missing foundations, some foundations missing locations, cut top of site plot plan off (doesn’t affect foundations) and  TOC schedule added is missing some of the associated unit numbers,

    - After review of the duct bank drawings Pro Energy requested EDG assess depth of conduits leaving hand holes, perform an evaluation for areas where load bearing equipment will be set up (cranes, forklifts, etc) over duct banks and if RGS conduit should be used in these areas with steel reinforced cage, The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

    - Underground piping. Forecast 5-5-2010. Received revised 5-14-10; Drawing were reviewed with EDG and comments have been forwarded to their office for resolution. Forecast delivery 5-28-10.

    - 7EA GSU foundation section views. Step Up Transformer Plan and Conduit Penetration Details 20-04 sheet 4; Step Up Transformer Grounding Plan 20-04 sheet 5; still has excessive ground penetrations in foundations and does specify GTG-100, Conduits appear to be interring the foundation in the wrong location, 5-25-10.

    - 7FA GSU foundation detailed drawings, forecast 5-21-10. GSU delivery is forecast for 6-5-10 and EDG was requested in meeting 5-19-10 to complete the designs so we will be ready to set upon cure of foundation. Revision forecast for 5-25-10. Engineering was unsure if the revision would be issued today, 5-25-10.

    - Balance of foundation details, 5-28-2010.

    - Grounding Plan (Drawings are under review and PES has some issues and concerns with the designs).

    - EDG forecast all designs to be complete by 5-31-10. EDG stated completion date is going to slip and will supply a new date. Engineering stated they did not know when the designs would be essentially completed.

  - ISSUED DRAWINGS:

Unit 100 GSU still appears to be oriented wrong!

11.PICTURES:

Picture 1: Setting final for pedestal 7EA

Picture 2: Rebar work with small crew 7FA