# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 9 July 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  85 F

RANGE: 78 to 90

SITE CONDITIONS: thunderstorms

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled mechanical/piping (local ASAP)

Mark Hanks - Electrical Supt (A&B)

Unfilled elect. Field engineer (local ASAP)

Kyle Roskam - Civil Supt (A&B)

Unfilled -turnover engineer (need 15Jul)

Felix Martinez-QA/QC (A&B)

Unfilled QA/QC supervisor (local ASAP)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Paul Olivo – Materials

– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Safety					1

Foremen				3

Electricians				4

Operators				4                       Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				10

Helpers				4

Welders				2

Total:					43

- GENERAL ITEMS:

  - Prepared, reviewed, and sent meeting minutes from meeting with Mondher Labbane, regarding 7EA fdn.

  - Mondher provided a drawing of underground and utilities overlaid over the fdn drawings, for review and information only.

  - Had a discussion with Sidor, included Bill Lugo, Mondher Labbane, and Cole Franklin to discuss the diesel tank location and the berm for the fuel tank.  Advised Sidor of the cost associated with moving the tank, but Sidor wants to more than originally discusses, will review and prepare a new quote for official transmittal, via Derwick.

  - We are notified 30k is released for small purchases, and the 7FA bolts are released.  Prepared PO for RE500 Hilti epoxy to embed PEECC plates being prepared by ISI and generator enclosure.  
Prepared PO for Hilti core drill to drill 7EA enclosure bolts, Concorcio is about 30% higher than expected and the cost for core drill is less than the delta.

  - Contacted a pressure grouting company to come to site to prepare a quote and advise what is necessary to start this work as soon as possible.

  - Little work on 7FA foundation, the anchor bolts and Unisorb pre pour package are not on site.  Hope for delivery next week.  Lack of anchor bolts is a day per day delay to schedule.

  - We prepared the PO for signature and hopefully will start excavation for duct bank next week.  Received a drawing from Sidor for the pull boxes (manholes).  I cannot open it without AutoCAD, forwarded it to EDGI.

  - Need to order Geo Tech Membrane for Treated fuel oil tank.  PO prepared, Commercial issue

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - The dismounting of crane is not completed.  Sidor asked us to accelerate the anchor bolts for the 7FA, and assure we can install the 7FA before 15 Aug.  We asked for a sketch showing their proposals for setting the crane not received today.  Sidor will attempt to locate the super lift kit for the crane reported to be in either Chile or Columbia that will increase the crane capacity to 1400 tons and reduce the additional erection and disassembly.

  - GSU embeds PO on hold commercial, mechanical contractor prepared a quote for fabricating them at site.  Quote is acceptable, must ask QA to assure we receive mat’l cert. if we turn this on.

- CLIENT ISSUES/CONCERN:

  - Client advised they do not accept the response from EDGI regarding location of Treated Fuel tank.  Meeting held at site with Sidor engineering, and PEC.

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor has provided one container for wood and trash; still require one more for steel scrap and regular emptying of the both.

- CIVIL:

  - Lack of anchor bolts for 7FA foundation continued delay; Contractor will be working on oily water separator and possibly waste oil tank foundations (received revised drawings today).

  - PEECC fdn is poured, ISI manufacturing embeds.

  - Oily water separator wall forming continues.

  - Lack of resolution for Treated Fuel Oil Tank location.  Will prepare an estimate for moving the tank for CO to Derwick.

  - Contractor has prepared the 7FA silencer base fill and 7FA stack base fill for pouring the mud mats Monday 12 July.  Concrete ordered this morning.

  - Prepared PO for local purchase for Geotech membrane.

- CONCRETE FOUNDATIONS:

  - Work on the 7FA main slab halted, working on silencer and stack foundations.  Ready for mud mats

  - 7FA Unisorb and anchor bolts, released for shipment yesterday, expected available to ship 17 July.

  - PEECC embeds to be built by ISI (mechanical contractor)

  - Crane de mob ongoing see photos, delaying GSU excavation.

- MECHANICAL:

5.1 Will issue PO for start of 7EA stack repairs and erection, on hold.

- PIPING:

6.1 Issued PO for piping on hold

- ELECTRICAL:

  - Loaned 5100 linear feet of conduit to Site A.  They will order to replace it, will need it within 1 week.

  - Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed.  This is a safety issue.  This can be released with the $30k, with all the rain this is a safety issue.

  - Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issue spoke to and prepared a CO to Derwick.  Sidor indicated they have no transformers, we need a 175kVA transformer to replace the one taken from Site B to Site A after Site A failure.  We will need construction power now that we are staffing up.

7.4 The sub contractor Coinserma prepared a new bid.  The execution of this scope will require a large amount of PES time to supervise this work, need to have an electrical local field engineer full time for this.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Commercial issues are resolved to local purchase materials

- Contractor increases manpower to work in all areas

- Contractor works two shifts

- The Underground and duct bank is started week of 7 June and does not slip more

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) see above

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) see above

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*)

* Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known.

9.3 Payment milestones

- Unit 100 – 7EA

Nov 29, 2010 (*)

- Unit 200 – 7FA

Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - The 7EA foundation concrete breaks are below acceptable; the core drilling has indicated an area in the suspect zone of porous concrete.  We met with Mondher at site to discuss this and have determined there is little risk of slab failure.

  - Sidor provided crane now being disassembled, expect 4 days to finish (not finished today 4th day).

  - Lack of materials (anchor bolts 7FA, embed plates PEECC 7EA

  - Changes in designs are impacting project progress/completion.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.  Sidor indicated the lack of concrete is due to site B being second priority.

  - Duct Bank drawings new forecast 28 June, for issued for construction drawings

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Will pour when crane moves after setting unit 100 turbine generator |
| Balance of FDN drawings | 25May10 | 3Jun10 | No date |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 |  |
| U/G piping | 5May10 | 28May10 | comments |
| GSU 7FA | 21May10 | 2 Jun10 | Not critical |
| Duct Bank | 17May | 28 June 10 |  |
| Design essentially complete | 31 May | No forecast date | No forecast date |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

  - ISSUED DRAWINGS:

Received Manhole Dwg from Sidor

Received revised GA showing bollards locations and noted to the effect Sidor to mat any area they plan to use a crane.

11. PICTURES:

Photo 1: 7EA (unit 100) alignment

Photo 2: 7EA (unit 100) tarped

Photo 3: 7EA (unit 100) GSU delay for crane

Photo 4: 7FA (unit 200) stack and silencer ready for mud mat