# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 9 June 2010, Tuesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  80 F

RANGE: 77 to 89

SITE CONDITIONS: Cool morning, intermittent rain all afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local) medical leave

Paulo Gómez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Foremen				2

Electricians				0

Operators				2                        Surveyor				1

Carpenters				8    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					2

Plumbers				0                        Iron Workers				14

Helpers				2

Welders				2

Total:					39

- GENERAL ITEMS:

  - GSU for Site A damaged in transit.  Received no update this issue.

  - The fixators installed for 7EA.

  - Poured mud mat for 7EA stack.  Need anchor bolts by 15 June

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, will conclude the piping when possible

  - The electrical contractor gave a fixed price for about ¼ of the duct bank and three manholes.  I compared the the unit prices against by take off and against the Concorcio Megavatio, unit prices are less than ½ Concorcio.   I set up a meeting with the contractor for Wednesday afternoon after I have time for a review.

  - Batch plants advised there will be no concrete due to lack of cement 20 to 27 June.

  - Sidor crane finally started mobilization.  Will take a week to finalize.  Rain stopped mobilization.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7FA need first order of anchor bolts today on hold for commercial issues.  Bill Lugo to speak with Brett to release some field PO s to continue working.

  - Underground piping and duct bank drawings dwgs delayed to 11 June, will discard the sketches and provide IFC drawings.  This is a big issue

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor was asked to provide this, but never delivered.

  - Sidor to delivered fire water flow rates for Plant B, I forwarded the information to Shane D.

  - Sidor expressed concern for the drawings review process and the comments getting into the drawings.  We are reviewing drawings for completeness in hopes of forestalling delays

  - Commercial issues and causing a serious impact on purchasing materials to continue work.

- CIVIL:

  - Concrete issues; lack of cement 20 to 27 June, lack of proper cement type III only will be available , lack of anchor bolts for 7EA stack foundation, lack of anchor bolts for 7FA foundation and small crew from Concorcio Megavatio.

- CONCRETE FOUNDATIONS:

4.1 Work today on the 7FA with small crew of manpower.  The work is progressing very slowly due to the lack of manpower and materials.  The contractor will be ready to install anchor bolts and Unisorb starting Wednesday delayed for bolts.

4.2 Fixators for 7EA installed.  The 2 weeks delay would really set back production.

4.3 Contractor agreed to continue with all 7EA equipment including GSU, PEECC, and Stack.

4.4 Issued RFP for 7EA anchor bolts, delivery 5 days 71,000 Bs.

4.5 Issued RFP for PEECC embeds.

4.6 Received quotation for core drilling.  Bs44710. Or about $9000. USD

4.7 Need to write a letter to Concorcio advising them to install fill to set up the crane.  The fill is about 300 M3 at about BS90. (Bolivars per meter cubed)

- MECHANICAL:

5.1 7EA generator replacement jib base plate is finished in Sedalia. Tom Koontz   	has ship by air freight to site. Current forecast is this week.  This is critical, if the 	crane is installed and ready to set equipment on fdn.

5.2 Requested ISI to provide insurance certifications.  They expect to have insurance certificate and all Sidor documents by Tuesday.

5.3 Installing fixators on 7EA finished

- PIPING:

6.1Review ongoing of material takeoff for bulk order of piping.

- ELECTRICAL:

7.1 Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed. On hold awaiting resolution of commercial issues

7.2 Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues

7.3 The embeds for GSU are different than site “A”, will get the foundation changed to match “A” to create less problems because “B” is different.  We will red line and continue same as “A”.

7.4 The sub contractor Coinserma came to site for meetings regarding the duct bank work.  Coinserma prepared a fixed price bid against the drawings presently at site, it appears that approximately ¼ of the actual scope (scope of bid) would put the total for 100% of scope at cost $750K.  They planned the work to finish in accord with our schedule if they started today.  The review of the quote is about 30% high in my estimate, but about 30% of the cost for comparable work by Concorcio.  The commercial issue as well as the materials makes this impossible, if I could accept the price.  Drawings are forecast to delay no less than a week.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: 9.1General Schedule issues The schedule is predicated by the following: - Commercial issues are resolved to local purchase materials - Contractor increases manpower to work in all areas - Contractor works two shifts - The Underground and duct bank is started next week and does not slip more - Sedalia material delivers are forthcoming to meet demand 9.2 Milestone Payment Estimated Delivery - Completed Milestone Payments (50%) Complete - Gas Turbines on Foundation (10%) July 19, 2010 - Civil Foundations Complete (25%) Sep 15, 2010 (*) - Electrical/Mechanical Complete (10%) Dec 3, 2010 (*) - Start- up Complete and Ready to Export Power (5%) Dec 11, 2010 (*) Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known. 9.3 Payment milestones - Unit 100 – 7EA Nov 29, 2010 (*) - Unit 200 – 7FA Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - Sidor provided crane started to mobilize, I understand it takes a week to mobilize.

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings now forecast for Monday 11Jun10.

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to plan and execute

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Sent sketches to EDGI to show issue with duct bank connection to transformer |
| Balance of FDN drawings | 25May10 | 3Jun10 | slipped |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | slipped |
| U/G piping | 5May10 | 28May10 | slipped |
| GSU 7FA | 21May10 | 2 Jun10 | slipped |
| Duct Bank | Had sketch to use for bid review | 7 June 10 | Slipped forecast 11 June earliest |
| Design essentially complete | 31 May | No forecast date |  |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

    - After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  IF all is equal to drawings there is no room for piping to cross over duct banks.  The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

  - ISSUED DRAWINGS:

Electrical interconnect drawings

11. PICTURES:

Photo 1: 7FA Pedestal rebar ongoing

Photo 2: 7EA mud mat poured