NOTE: THIS DRAWING IS BASED ON THE ORIGINAL CABLE SUMMARY DRWG 377A4380 REV-C AND MODIFIED FOR DUAL FUEL AND SITE SPECIFIC REQUIRMENTS.

CABLE SUMMARY (GAS TURBINE)

CUSTOMER: EDC MARGATITA ISLAND

(UNITS 298034 & 298035)

AGM-02-0204-PLA-E-0006

NOTES

- "C" PREFIX INDICATES CABLE SUPPLIED BY OTHERS THAN GEGAS

TURBINE DIVISION. CONTROL CABLES WITH "C" PREFIX

CONTAIN A NOMINAL NUMBER OF SPARES.

- "C" PREFIX CABLES TO BE RATED NOT LESS THAN 90 DEG. C.

- CABLE GLANDS/STRESS RELIEFS FOR CONNECTING CABLES AT

JUNCTION BOXES/DEVICES ARE TO BE SUPPLIED BY OTHERS.

- BEND RADIUS - ALL BENDS SHALL BE SO MADE THAT THE CABLE

WILL NOT BE DAMAGED, AND THE RADIUS OF THE INNER EDGE OF

ANY BEND SHALL NOT BE LESS THAN SHOWN IN TABLE. THIS

RADIUS DOES NOT INCLUDE PULLING TENSION CALCULATION.

SEE M.L. ITEM 0435 FOR FURTHER DEFINITION.

- CABLES SUPPLIED BY OTHERS THAT ARE SHOWN ON THIS DWG.

ARE ONLY FOR THOSE WHICH INTERFACE WITH GAS TURBINE

SUPPLIED EQUIPMENT.

- MAKEUP OF "C' PREFIX CABLES ARE SUGGESTED TO ENSURE

SUFFICIENT CONDUCTOR COUNT.

- "C" PREFIX CABLES FOR LEVEL 4 AND LEVEL 5 POWER SUPPLY

ARE SIZED BY OTHERS.

- SEE OUTLINE, GAS TURBINE PACKAGE CONNECTION -

ELECTRICAL DIAG., M.L. ITEM 0301 FOR LOCATION OF CABLE

DESTINATION POINTS (JB'S, ETC.) WITHIN EACH ON-BASE

COMPARTMENT.

- CABLE TO BE INSTALLED WITH ADEQUATE SEPARATION

BETWEEN DIFFERENT LEVELS AND IN PROPER CONDUIT OR

RACEWAY MATERIAL, SEE M.L. ITEM 0435, AND IN ACCORDANCE

WITH LATEST ELECTRICAL CODES.

- GROUND CABLES ARE TO BE SUPPLIED ON ALL EQUIPMENT. TWO

CABLE CONNECTIONS ARE DIAGONALLY OPPOSED.

- ONE CABLE REQUIRED PER SITE.

- CABLE REQUIRED FOR UNITS 1 & 3 ONLY.

- CABLE REQUIRED FOR UNITS 2 & 4 ONLY.

- FOR ADDITIONAL COMMUNICATION CABLES SEE M.L. ITEM 4108.

- REFER TO DWG. 358B1001 FOR CABLE ROUTING.

LOCATION DESCRIPTIONS

001 - WELDING RECEPTACLE ONE

101 - TURBINE CONTROL PANEL (333)

102 - GENERATOR CONTROL PANEL (333)

108 - AUXILIARY RELAY PANEL

114 - JB001 ACCESSORY BASE LOW LEVEL (119)

115-JB002 ACCESSORY BASE LEVEL3(119)

118 - ACCESSORY BASE MOTORS (119)

119 - ACCESSORY BASE

114 - JB001 ACCESSORY BASE LOW LEVEL

115 - JB002 ACCESSORY BASE LEVEL 3

118 - ACCESSORY BASE MOTORS

149 - CRANKING MOTOR

348 - JB077A ACCESSORY BASE FP

392 - JB004 ACCESSORY BASE LEVEL 4

121 - TURBINE BASE

122 - TURBINE ROOF MOUNTED DEVICES

125 - JB055 TURBINE BASE LOW LEVEL

126 - JB056 TURBINE BASE LOW LEVEL

390 - JB034 TURBINE ROOF LOW LEVEL

122 - TURBINE ROOF MOUNTED DEVICES (121)

125 - JB055 TURBINE BASE LOW LEVEL (121)

126 - JB056 TURBINE BASE LOW LEVEL (121)

127 - JB085 LOAD GEAR COMPARTMENT LOW LEVEL (250)

128 - EXHAUST FRAME BLOWER 88TK-1

129 - EXHAUST FRAME BLOWER 88TK-2

133 - JB005C GENERATOR COMPARTMENT LEVEL 4 (134)

134 - GENERATOR COMPARTMENT

133 - JB005C GENERATOR COMPARTMENT LEVEL 4

135 - JB005A GENERATOR COMPARTMENT LOW LEVEL

136 - JB005B GENERATOR COMPARTMENT LEVEL 3

325 - JB163 GENERATOR COMPARTMENT LOW LEVEL

135 - JB005A GENERATOR COMPARTMENT LOW LEVEL (134)

136 - JB005B GENERATOR COMPARTMENT LEVEL 3 (134)

146 - METAL CLAD SWITCHGEAR

149 - CRANKING MOTOR (119)

151 - JB215 GENERATOR FILTER SEQUENCER

156 - FUEL GAS FLOW DEVICES

157 - TURBINE AIR INLET FILTER COMPARTMENT

449 - JB078 TURB. AIR INLET FILTER COMPARTMENT

158 - GAS SCRUBBER

563 - JB386 GAS SCRUBBER LEVEL 3

161 - COOLING WATER MODULE #1

428 - JB090 COOLING WATER MODULE LEVEL 3

438 - JB090A COOLING WATER MODULE LEVEL 4

171 - GAS FUEL (VALVE) MODULE

363 - JB130 GAS FUEL MODULE

441-JB131 GAS FUEL MODULE LEVEL4

172 - AIR PROCESS SKID

455 - JB297 AIR PROCESS SKID LEVEL 3

173 – JB72 WATER INJECTION SKID LEVEL 3

174 – JB79 WATER INJECTION SKID LEVEL 1

175 – WATER INJECTION SKID 480 VOLT SUPPLY

176 - LUBE OIL DEMISTER (TURBINE)

182 - MAIN TRANSFORMER (STEP UP)

183 - AUXILIARY POWER TRANSFORMER

LOCATION DESCRIPTIONS (continued)

201 - LIMIT AMP

208 - VIBRATION MONITOR PANEL (102) (333)

225 - RELATIVE HUMIDITY SENSOR

227 - HAZARDOUS GAS MONITOR (102) (333)

230 - JB019A TURBINE OFF BASE RACK LEVEL 3

231 - JB019B TURBINE OFF BASE RACK LEVEL 3

233 - JB020A TURBINE OFF BASE RACK LOW LEVEL

234 - JB020B TURBINE OFF BASE RACK LOW LEVEL

236 – TURBINE ROOF LOW LEVEL

250 - LOAD GEAR COMPARTMENT

127 - JB085 LOAD GEAR COMPARTMENT LOW LEVEL

387 - JB020G TURBINE COMPARTMENT LOW LEVEL

252 - WATER WASH SKID

456-JB010 WATERWASHSKID LEVEL3

254 - CUSTOMER DEVICES--PANELS

257 - JB037 PERFORMANCE MONITORING LOW LEVEL

280 - GENERATOR NEUTRAL ACCESSORY COMPARTMENT GNAC

581 - JB005N GEN. NEUTRAL ACCESSORIES COMP. LEVEL 3

283 - FIRE PROTECTION DEVICES

284 - FIRE PROTECTION PANEL

325 - JB163 GENERATOR COMPARTMENT LOW LEVEL (134)

329 - CRANKING MOTOR TRANSFORMER

333 - PACKAGED ELECTRICAL-ELECTRONIC CONTROL CENTER-PEECC

101 - TURBINE CONTROL PANEL

102 - GENERATOR CONTROL PANEL

208 - VIBRATION MONITOR PANEL

227 - HAZARDOUS GAS MONITOR

334 - PEECC MOTOR CONTROL CENTER

339 - JB298 PEECC LEVEL 3

562 - STATIC VOLTAGE REGULATOR--EX2000R

334 - PEECC MOTOR CONTROL CENTER (333)

335 - BUS DUCT

338 - CUSTOMER 480V SUPPLY

339 - JB298 PEECC LEVEL 3 (333)

348 - JB077A ACCESSORY BASE FP (119)

363 - JB130 GAS FUEL MODULE (171)

381 - JB021A TURBINE OFF BASE RACK LEVEL 4

387 - JB020G TURBINE COMPARTMENT LOW LEVEL (250)

390 - JB034 TURBINE ROOF LOW LEVEL (121)

392 - JB004 ACCESSORY BASE LEVEL 4 (119)

427 – LIQUID FUEL FORWARDING SKID JB01

428 - JB090 COOLING WATER MODULE LEVEL 3 (161)

429 – 88AB-1 MCC CUBICLE

430 – DEMIN WATER FORWARDING JB01

438 - JB090A COOLING WATER MODULE LEVEL 4 (161)

441 - JB131 GAS FUEL MODULE LEVEL 4 (171)

447 - INLET HEATING CONTROL VALVE

449 - JB078 TURB. AIR INLET FILTER COMPARTMENT (157)

455 - JB297 AIR PROCESS SKID LEVEL 3 (172)

456-JB010 WATER WASH SKID LEVEL 3 (252)

514 - CUSTOMER SWITCHGEAR

562 - STATIC VOLTAGE REGULATOR--EX2000R (333)

563 - JB386 GAS SCRUBBER LEVEL 3 (158)

581 - JB005N GEN. NEUTRAL ACCESSORIES COMP. LEVEL 3 (280)

611 - INLET HEATING ISOLATION VALVE

622 - FUEL GAS HEATER CONTROL PANEL

LOCATION DESCRIPTIONS (continued)

742 - SITE LIGHTS

751 - FLAME DETECTOR INTERFACE MODULE PRIMARY

752 - FLAME DETECTOR INTERFACE MODULE SECONDARY

753 - JB309 FUEL GAS HEATING SKID LEVEL 3

901 - CUSTOMER GROUND GRID

938 - CEMS SYSTEM

939 – UNIT AREA OUTDOOR LIGHTING

940 – DEMIN WATER FORWARDING JB02

941 – LIQUID FUEL FORWARDING JB02

942 – CUSTOMER SUPPLIED MCC

| CUSTOMER SUPPLIED CABLES |  | cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | C001 | 101 | 136 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |  |
|  |  | C006 | 101 | 363 | LEVEL(1) \ 36 COND |  | 18AWG | 1 CABLE-18 TW SHLD PAIRS | INSTRUMENTATION SIGNALS |  |  |
|  |  | C009A | 234 | 751 | LEVEL(3S) \ 8COND |  | 18AWG | 1 CABLE-4 TW SHLD PAIRS | FLAME DETECTORS 28FD (2WIRE) |  |  |
|  |  | C009B | 234 | 752 | LEVEL(3S) \ 8COND |  | 18AWG | 1 CABLE-4 TW SHLD PAIRS | FLAME DETECTORS 28FD (2WIRE) |  |  |
|  |  | C012 | 334 | 392 | LEVEL(4) \ 3COND |  | 4AWG | 1 CABLE | 125VDC SUPPLY 88QE-1 | 15 |  |
|  |  | C013C | 334 | 392 | LEVEL(4) \ 3COND |  | 10AWG | 1 CABLE | 3 PH SUPPLY 88TM-1 | 15 |  |
|  |  | C014 | 101 | 363 | LEVEL(3) \ 37 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |  |
|  |  | con | 101 | 135 | LEVEL(1) \ 36 COND |  | 18AWG | 1 CABLE-18 TW SHLD PAIRS | INSTRUMENTATION SIGNALS RTDS |  |  |
|  |  | C018 | 101 | 135 | LEVEL(1S) \ 18 COND |  | 18AWG | 1 CABLE-9 PAIR CHROM-ALUM T/C | THERMOCOUPLES |  |  |
|  |  | C022 | 227 | 363 | LEVEL(2) \ 9COND |  | 18AWG | 1 CABLE-3 TW SHLD TRIADS | GAS DETECTORS 45HA-7 45HA-8 |  |  |
|  |  | C027 | 118 | 334 | LEVEL(4) \ 3COND |  | 2AWG | 1 CABLE | 3 PH. SUPPLY 88QA-1 | 15 |  |
|  |  | C028 | 334 | 392 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY 88HQ-1 | 15 |  |
|  |  | C037 | 101 | 115 | LEVEL(3) \ 37 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS | 15 |  |
|  |  | C038 | 101 | 234 | LEVEL(1) \ 36 COND |  | 18AWG | 1 CABLE-18 TW SHLD PAIRS | INSTRUMENTATION SIGNALS |  |  |
|  |  | C039 | 101 | 233 | LEVEL(1S) \ 18 COND |  | 18AWG | 1 CABLE-9 PAIR CHROM-ALUM T/C | THERMOCOUPLES |  |  |
|  |  | C041 | 101 | 233 | LEVEL(1S) \ 18 COND |  | 18AWG | 1 CABLE-9 PAIRCHROM-ALUM T/C | THERMOCOUPLES |  |  |
|  |  | C042 | 101 | 230 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |  |
|  |  | C049 | 102 | 146 | LEVEL(3) \ 37 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS GEN BREAKER | 15 |  |
|  |  | C055A | 334 | 381 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY 23HT-1 |  |  |
|  |  | C055B | 334 | 381 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY 23HT-2 |  |  |
|  |  | C059 | 133 | 334 | LEVEL(4) \ 3COND |  | 10AWG | 1 CABLE | 3 PH. SUPPLY 23HG-1,-3,-5 |  |  |
|  |  | C071 | 128 | 334 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88TK-1 |  |  |
|  |  | C072 | 129 | 334 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88TK-2 |  |  |
|  |  | C073 | 101 | 387 | LEVEL(1S) \ 36 COND |  | 18AWG | 1 CABLE-18 PR CHROM-ALUM T/C | THERMOCOUPLES | 15 |  |
|  |  | C074 | 101 | 387 | LEVEL(1S) \ 36 COND |  | 18AWG | 1 CABLE-18 PR CHROM-ALUM T/C | THERMOCOUPLES | 15 |  |
|  |  | C076 | 101 | 135 | LEVEL(1) \ 18 COND |  | 18AWG | 1 CABLE-9 TW SHLD PAIRS | INSTRUMENTATION SIGNALS |  |  |
|  |  | C077 | 146 | 334 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY | 15 |  |
|  |  | C080 | 146 | 335 | LEVEL(3) \ 3COND |  | 12AWG | 1 CABLE | 23BO |  |  |
|  |  | C083 | 102 | 146 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | VT SIGNALS | 15 |  |
|  |  | C094B | 135 | 562 | LEVEL(1) \ 8COND |  | 18AWG | 1 CABLE-4 TW SHLD PAIRS | KA TO EXCITER |  |  |
|  |  | C096 | 101 | 363 | LEVEL(1) \ 36 COND |  | 18AWG | 1 CABLE-18 TW SHLD PAIRS | INSTRUMENTATION SIGNALS |  |  |

| CUSTOMER SUPPLIED CABLES (continued) .. |  | cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | C102 | 334 | 392 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY 23QT-1,-2 | 15 |  |
|  |  | C117A | 125 | 208 | LEVEL(1) \ 18 COND |  | 18AWG | 1 CABLE-6 TW SHLD TRIADS | PROXIMITORS |  |  |
|  |  | C117B | 126 | 208 | LEVEL(1) \ 18 COND |  | 18AWG | 1 CABLE-6 TW SHLD TRIADS | PROXIMITORS | 15 |  |
|  |  | C117C | 127 | 208 | LEVEL(1) \ 9COND |  | 18AWG | 1 CABLE-3 TW SHLD TRIADS | PROXIMITORS | 15 |  |
|  |  | C123 | 136 | 562 | LEVEL(3) \ 6COND |  | 10AWG | 1 CABLE | 64F EXCITER FIELD | 15 |  |
|  |  | C125 | 334 | 392 | LEVEL(4) \ 5COND |  | 10AWG | 1 CABLE | 3PH SUPPLY 23HA-3 & 23HT-3 | 15 |  |
|  |  | C128 | 101 | 231 | LEVEL(3) \ 6COND |  | 12AWG | 1 CABLE | 26HT-1,-3 |  |  |
|  |  | C135 | 284 | 348 | LEVEL(2S) \ 18 COND |  | 18AWG | 1 CABLE-9 TW SHLD PAIRS | FIRE DETECTORS CIRCUIT (A) |  |  |
|  |  | C136 | 284 | 348 | LEVEL(2S) \ 18 COND |  | 18AWG | 1 CABLE-9 TW SHLD PAIRS | FIRE DETECTORS CIRCUIT (B) |  |  |
|  |  | C145 | 208 | 325 | LEVEL(1) \ 18 COND |  | 18AWG | 1 CABLE-6 TW SHLD TRIADS | PROXIMITORS | 15 |  |
|  |  | C148 | 146 | 562 | LEVEL(3) \ 4COND |  | 10AWG | 1 CABLE | CONTROL CURRENT TRANSFORMERS | 15 |  |
|  |  | C149 | 334 | 441 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 1 PH. SUPPLY 23VS-1 |  |  |
|  |  | C161 | 115 | 339 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | MOTOR HEATERS, AC LIGHTS | 15 |  |
|  |  | C171 | 227 | 234 | LEVEL(2) \ 9COND |  | 18AWG | 1 CABLE-3 TW SHLD TRIADS | GAS DETECTORS 45HT-1 45HT-2 |  |  |
|  |  | C172 | 114 | 201 | LEVEL(1) \ 18 COND |  | 18AWG | 1 CABLE-6 TW SHLD TRIADS | RTDS 88CR-1 |  |  |
|  |  | C182 | 101 | 231 | LEVEL(3) \ 12 COND |  | 12AWG | 1 CABLE | 20TW DEVICES |  |  |
|  |  | C190 | 128 | 339 | LEVEL(3) \ 2COND |  | 10AWG | 1 CABLE | MOTOR HEATER 23TK-1 |  |  |
|  |  | C191 | 101 | 128 | LEVEL(3) \ 3COND |  | 12AWG | 1 CABLE | 63TK-1 |  |  |
|  |  | C192 | 129 | 339 | LEVEL(3) \ 2COND |  | 10AWG | 1 CABLE | MOTOR HEATER 23TK-2 |  |  |
|  |  | C193 | 101 | 129 | LEVEL(3) \ 3COND |  | 12AWG | 1 CABLE | 63TK-2 |  |  |
|  |  | C199 | 122 | 334 | LEVEL(4) \ 3COND |  | 8AWG | 1 CABLE | 3 PH. SUPPLY 88BT-1 |  |  |
|  |  | C199A | 122 | 339 | LEVEL(3) \ 2COND |  | 10AWG | 1 CABLE | MOTOR HEATER 23BT-1 |  |  |
|  |  | C200 | 101 | 233 | LEVEL(1S) \ 36 COND |  | 18AWG | 1 CABLE-18 PR CHROM-ALUM T/C | THERMOCOUPLES |  |  |
|  |  | C201 | 101 | 390 | LEVEL(1) \ 8COND |  | 18AWG | 1 CABLE-4 TW SHLD PAIRS | 96CD-1A 96CD-1B 96CD-1C |  |  |
|  |  | C216 | 339 | 363 | LEVEL(3) \ 3COND |  | 12AWG | 1 CABLE | AC LIGHTS |  |  |
|  |  | C217 | 339 | 363 | LEVEL(3) \ 2COND |  | 10AWG | 1 CABLE | DC STANDBY LIGHTING |  |  |
|  |  | C219 | 136 | 339 | LEVEL(3) \ 12 COND |  | 12AWG | 1 CABLE | LIGHTS --RECEPTACLES |  |  |
|  |  | C235A | 102 | 146 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | CURRENT TRANSFORMERS 21-23,60-62 | 15 |  |
|  |  | C235B | 102 | 146 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | CURRENT TRANSFORMERS 27-29, 48-50 | 15 |  |
|  |  | C235C | 108 | 146 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | CURRENT TRANSFORMERS 24-26 |  |  |
|  |  | C236A | 102 | 581 | LEVEL(3) \ 12 COND |  | 10AWG | 1 CABLE | CURRENT TRANSFORMERS 1-6,NGR | 15 |  |

CUSTOMER SUPPLIED CABLES (continued)

| cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C236B | 102 | 581 | LEVEL (3) \ 12 COND |  | 10 AWG | 1 CABLE | CURRENT TRANSFORMERS 7-9 | 15 |
| C236C | 102 | 146 | LEVEL (3) \ 12 COND |  | 10 AWG | 1 CABLE | CURRENT TRANSFORMERS 30-32 | 15 |
| C237 | 146 | 334 | LEVEL (4) \ 2 COND |  | 6 AWG | SINGLE CONDUCTORS | 125VDC BREAKER CLOSE CIRCUIT | 15 |
| C249 | 339 | 581 | LEVEL (3) \ 3 COND |  | 10 AWG | 1 CABLE | 23HG-20 | 15 |
| C251 | 334 | 392 | LEVEL (4) \ 3 COND |  | 6 AWG | 1 CABLE | 3 PH. SUPPLY – IGNITION TRANSFORMERS |  |
| C256 | 101 | 230 | LEVEL (3) \ 3 COND |  | 10 AWG | 1 CABLE | 120VAC SUPPLY – IGNITION TRANSFORMERS |  |
| C257 | 101 | 231 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C270 | 115 | 339 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | LIGHTS, 26QL-1 | 15 |
| C285 | 101 | 363 | LEVEL (1S) \ 6 COND |  | 18 AWG | 1 CABLE-3 PAIR CHROM-ALUM T/C | THERMOCOUPLES FTG-1A,- 1B,-2A,-2B |  |
| C401 | 183 | 254 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V TO CUSTOMER UNIT #1 | 11 |
| C402 | 334 | 939 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V UNIT LIGHTING |  |
| C403 | 334 | 742 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V SITE LIGHTING |  |
| C404 | 334 | 938 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V CEM LOADS |  |
| C406 | 182 | 334 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V ALTERNATIVE POWER TO STEPUP TRANS. COOLING | 13 |
| C407 | 182 | 334 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V NORMAL POWER TO STEPUP TRANS. COOLING | 12 |
| C408 | 001 | 334 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V WELDING OUTLETS |  |
| C409A | 182 | 334 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC TO LOAD BRTEAK CKT SWITCHER | 12 |
| C409B | 182 | 334 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC TO TRANSFORMER ANNUNCIATOR | 13 |
| C410A | 254 | 334 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC H2235 RELAY RACK IN ROCS TRAILER REGULAR | 12 |
| C410B | 254 | 334 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC H2235 RELAY RACK IN ROCS TRAILER BACKUP | 13 |
| C411 | 183 | 622 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V SUPPLY TO GAS HEATER CONTROL PANEL |  |
| C413 | 622 | 753 | LEVEL (3) \ 3 COND |  | 18 AWG | 1 CABLE-3 PAIR CHROM-ALUM T/C | THERMOCOUPLES |  |
| C414 | 622 | 753 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | GAS FUEL HEATER EMERGENCY STOP |  |
| C414A | 101 | 622 | LEVEL (1) \ 6 COND |  | 12 AWG | 1 CABLE | FUEL GAS HEATER CONTROLS |  |
| C415 | 183 | 338 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 480V SUPPLY TO AUX |  |
| C417A | 102 | 102 | LEVEL (3) \ 12 COND |  | 10 AWG | 1 CABLE | CT’S 7-9 & 30-31 SIGNALS GCP UNIT #2 TO GCP UNIT #1 | 11 |
| C418A | 102 | 102 | LEVEL (3) \ 12 COND |  | 10 AWG | 1 CABLE | CT’S 27-29 & 48-50 SIGNALS GCP UNIT #2 TO GCP UNIT #1 |  |
| C420A | 102 | 254 | LEVEL (3) \ 4 COND |  | 10 AWG | 1 CABLE | CUSTOMER CT’S 39-41 TO 87T | 13 |
| C420B | 102 | 254 | LEVEL (3) \ 4 COND |  | 10 AWG | 1 CABLE | CUSTOEMR CT’S 42-44 TO 87U | 12 |

CUSTOMER SUPPLIED CABLES (continued)

| cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C421 | 108 | 108 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | EVEN UNIT TO ODD UNIT CONTACTS |  |
| C421A | 108 | 108 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | ODD UNIT TO EVEN UNIT CONTACTS |  |
| C421B | 108 | 108 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | EVEN UNIT TO ODD UNIT CONTACTS |  |
| C421C | 108 | 108 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | ODD UNIT TO EVEN UNIT CONTACTS |  |
| C422 | 108 | 108 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | ODD UNIT TO EVEN UNIT CONTACTS |  |
| C422A | 108 | 108 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | EVEN UNIT TO ODD UNIT CONTACTS |  |
| C426 | 108 | 254 | LEVEL (1) \ 12 COND |  | 18 AWG | 1 CABLE-6 TW SHLD PAIRS | 96GR-1, 96AW-1, 96GG-2, 96GV-1 |  |
| C426A | 108 | 254 | LEVEL (1) \ 3 COND |  | 18 AWG | 1 CABLE-1 TW SHLD TRIAD | 96GG*2 |  |
| C428 | 101 | 146 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | 52G FAN ALARMS |  |
| C473 | 101 | 387 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 39V-3A | 15 |
| C474 | 101 | 387 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 39V-3B | 15 |
| C480 | 334 | 514 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | 120VAC FOR CUSTOMER AUX POWER SUBSTATION COMPARTMENT |  |
| C481 | 334 | 514 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC FOR CUSTOMER AUX POWER SUBSTATION |  |
| C512 | 101 | 449 | LEVEL (3) \ 7 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C513A | 101 | 157 | LEVEL (1S) \ 2 COND |  | 18 AWG | 1 CABLE-1 CHROM- ALUM T/C PAIR | AT-ID-1 THERMOCOUPLE |  |
| C513B | 101 | 157 | LEVEL (1S) \ 2 COND |  | 18 AWG | 1 CABLE-1 CHROM- ALUM T/C PAIR | AT-ID-2 THERMOCOUPLE |  |
| C513C | 101 | 157 | LEVEL (1S) \ 2 COND |  | 18 AWG | 1 CABLE-1 CHROM- ALUM T/C PAIR | AT-ID-3 THERMOCOUPLE |  |
| C515 | 339 | 449 | LEVEL (3) \ 3 COND |  | 6 AWG | 1 CABLE | 120/240VAC SUPPLY |  |
| C516A | 101 | 447 | LEVEL (3) \ 2 COND |  | 12 AWG | 1 CABLE | 20TH-1 |  |
| C516E | 101 | 611 | LEVEL (3) \ 2 COND |  | 12 AWG | 1 CABLE | 33TH-3 |  |
| C517A | 101 | 447 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 96TH-1 |  |
| C517B | 101 | 447 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 65EP-3 |  |
| C517D | 101 | 447 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 96BH-1 |  |
| C517E | 101 | 447 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 96BH-2 |  |
| C531 | 101 | 428 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C532 | 339 | 428 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C533 | 334 | 438 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88FC-1 |  |
| C534 | 334 | 438 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88FC-2 |  |
| C535 | 334 | 438 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88FC-3 |  |
| C537 | 334 | 438 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88WC-1 |  |

CUSTOMER SUPPLIED CABLES (continued)

| cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C538 | 334 | 438 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88WC-2 |  |
| C544 | 339 | 428 | LEVEL (3) \ 12 COND |  | 10 AWG | 1 CABLE | MOTOR HEATERS |  |
| C549 | 102 | 254 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-6 TW SHLD TRIADS | METERING |  |
| C549A | 108 | 254 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-6 TW SHLD TRIADS | METERING |  |
| C550A | 101 | 254 | LEVEL (3) \ 19 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C550B | 101 | 254 | LEVEL (3) \ 19 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C550C | 101 | 254 | LEVEL (3) \ 19 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C550D | 101 | 254 | LEVEL (3) \ 19 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C551A | 101 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C551B | 101 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | DIGITAL CONTROL SIGNALS OUT |  |
| C551C | 101 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | DIGITAL OUTPUTS TO CUSTOMER ALARM PANEL |  |
| C553A | 101 | 254 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-9 TW SHLD PAIRS | ANALOGS IN/OUT |  |
| C553B | 101 | 254 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-9 TW SHLD PAIRS | ANALOGS IN/OUT |  |
| C554 | 101 | 254 | LEVEL (3) \ 4 COND |  | 12 AWG | 1 CABLE | REMOTE EMERGENCY TRIP R5E |  |
| C575 | 149 | 201 | LEVEL (5) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88CR-1 |  |
| C583 | 183 | 334 | LEVEL (4) \ 6 COND |  |  | 2 PER PH. | 3PH. 800 AMP SUPPLY FEEDER MCC1-AC |  |
| C584 | 183 | 334 | LEVEL (4) \ 6 COND |  |  | 2 PER PH. | 3PH. 800 AMP SUPPLY FEEDER MCC2-AC |  |
| C590 | 101 | 201 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C591 | 108 | 183 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | CURRENT TRANSFORMERS 51TN-2 |  |
| C593 | 108 | 183 | LEVEL (3) \ 4 COND |  | 10 AWG | 1 CABLE | CURRENT TRANSFORMERS 50/51AT-2 |  |
| C596 | 201 | 334 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 125VDC CONTROL POWER |  |
| C598 | 201 | 329 | LEVEL (5) \ 3 COND |  |  | SIZED BY CUSTOMER | MEDIUM VOLTAGE SUPPLY |  |
| C607 | 101 | 225 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 96TD-1 |  |
| C607A | 225 | 339 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | 120VAC SUPPLY 96TD-1 |  |
| C610A | 102 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86G1 CONTACTS TO CUSTOMER |  |
| C610B | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86G2 CONTACTS TO CUSTOMER |  |
| C610C | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86RE CONTACTS TO CUSTOMER |  |
| C610D | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86AT CONTACTS TO CUSTOMER |  |
| C610E | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86BF CONTACTS TO CUSTOMER |  |
| C610F | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86G-1 CONTACTS TO CUSTOMER |  |
| C610FA | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86G-2 CONTACTS TO CUSTOMER |  |

CUSTOMER SUPPLIED CABLES (continued)

CUSTOMER SUPPLIED CABLES (continued)

| cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C610FB | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86BF CONTACTS TO CUSTOMER |  |
| C610FC | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86RE CONTACTS TO CUSTOMER |  |
| C610H | 102 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | 86T1 CONTACTS TO CUSTOMER |  |
| C610HA | 102 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | AUX 86T-1 CONTACTS TO CUSTOMER |  |
| C610J | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | 86AT CONTACTS TO CUSTOMER |  |
| C610V | 102 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CUSTOMER INTERLOCKS |  |
| C610W | 108 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CUSTOMER INTERLOCKS |  |
| C611 | 105 | 254 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CUSTOMER TRIPS AND PERMISSIVES |  |
| C611A | 105 | 254 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | CUSTOMER TRIPS |  |
| C615D | 101 | 156 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIR | 96FM-1A |  |
| C667-1 | 101 | 456 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS UNIT #1 | 11 |
| C667-2 | 101 | 456 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS UNIT #1 |  |
| C667-3 | 101 | 456 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS UNIT #1 |  |
| C667-4 | 101 | 456 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS UNIT #1 |  |
| C669 | 183 | 252 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. 480V SUPPLY WATER WASH SKID | 11 |
| C671 | 101 | 176 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | 63QV-1 |  |
| C672 | 176 | 334 | LEVEL (4) \ 3 COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88QV-1 |  |
| C672A | 176 | 339 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | MOTOR HEATER 23QV-2 |  |
| C678 | 101 | 257 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIRS | 5 TWO WIRE TRANSDUCER PACKAGE |  |
| C725 | 339 | 455 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | CONTROL POWER SUPPLY |  |
| C727 | 101 | 455 | LEVEL (3) \ 6 COND |  | 12 AWG | 1 CABLE | 63AD-4 |  |
| C743 | 102 | 201 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | 59CM RELAY |  |
| C745A | 146 | 329 | LEVEL (5) \ 3 COND |  |  | SIZED BY CUSTOMER | 13.8KV TO TRANSFORMER PRIMARY |  |
| C745B | 183 | 329 | LEVEL (5) \ 3 COND |  |  | SIZED BY CUSTOMER | 13.8KV TO TRANSFORMER PRIMARY |  |
| C776 | 136 | 151 | LEVEL (3) \ 5 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C777 | 136 | 151 | LEVEL (3) \ 2 COND |  | 12 AWG | 1 CABLE | 120VAC SUPPLY 34GF-1 |  |
| C809 | 334 | 441 | LEVEL (4) \ 3 COND |  | 10 AWG | 1 CABLE | 3 PH. SUPPLY 88VL-2 |  |
| C809A | 339 | 441 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | MOTOR HEATER 23VL-2 |  |
| C817 | 334 | 441 | LEVEL (4) \ 3 COND |  | 10 AWG | 1 CABLE | 3 PH. SUPPLY 88VL-1 |  |
| C817A | 339 | 441 | LEVEL (3) \ 2 COND |  | 10 AWG | 1 CABLE | MOTOR HEATER 23 VL-1 |  |
| C819 | 101 | 563 | LEVEL (3) \ 19 COND |  | 12 AWG | 1 CABLE | 71GS-1, -2A, -2B, -2C |  |

CUSTOMER SUPPLIED CABLES (continued)

| cable number | to | from | level I #cond | diameter I bend rad | gauge | Makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C849 | 201 | 339 | LEVEL (3) \ 3 COND |  | 10 AWG | 1 CABLE | 23LC HEATER |  |
| C870 | 101 | 284 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C871 | 284 | 339 | LEVEL (3) \ 3 COND |  | 12 AWG | 1 CABLE | 120VAC SUPPLY |  |
| C872 | 284 | 339 | LEVEL (3) \ 12 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| C874 | 284 | 339 | LEVEL (4) \ 3 COND |  | 10 AWG | 1 CABLE | 3 PH SUPPLY 88RC-1 |  |
| S875 | 115 | 101 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| S876 | 114 | 101 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-9 TW SHLD PAIRS | CONTROL SIGNALS |  |
| S877 | 174 | 101 | LEVEL (1) \ 18 COND |  | 18 AWG | 1 CABLE-9 TW SHLD PAIRS | CONTROL SIGNALS |  |
| S878 | 236 | 101 | LEVEL (1) \ 12 COND |  | 18 AWG | 1 CABLE-6 TW SHLD PAIRS | CONTROL SIGNALS |  |
| S879 | 173 | 101 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| C880 | 942 | 101 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| S881 | 429 | 101 | LEVEL(3) \ 8 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| S882 | 231 | 101 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| C883 | 942 | 101 | LEVEL(3) \ 19 COND |  | 12AWG | 1 CABLE | CONTROL SIGNALS |  |
| S884 | 392 | 429 | LEVEL(4) \ 3COND |  | 4 AWG | 1 CABLE | 3 PH. SUPPLY 88AB-1 |  |
| C885 | 175 | 183 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88WN-1 |  |
| S886 | 115 | 429 | LEVEL(4) \ 2COND |  | 10AWG | 1 CABLE | 3 PH. SUPPLY 23AB-1 |  |
| C887 | 941 | 942 | LEVEL(4)\ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P203A |  |
| C888 | 941 | 942 | LEVEL(4)\ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P203B |  |
| C889 | 940 | 942 | LEVEL(4)\ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P400A |  |
| C890 | 940 | 942 | LEVEL(4)\ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P400B |  |
| S891 | 430 | 101 | LEVEL(3) \ 4 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| S892 | 430 | 101 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIRS | CONTROL SIGNALS |  |
| S893 | 427 | 101 | LEVEL(3) \ 4 COND |  | 12 AWG | 1 CABLE | CONTROL SIGNALS |  |
| S894 | 427 | 101 | LEVEL (1) \ 2 COND |  | 18 AWG | 1 CABLE-1 TW SHLD PAIRS | CONTROL SIGNALS |  |

CUSTOMER SUPPLIED GROUND CABLES

| cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CG1007 | 254 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1008 | 333 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG1031 | 230 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1032 | 231 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1033 | 2333 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1034 | 234 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1038 | 381 | 901 | LEVEL (4) \ 1 COND |  | 1/0 AWG | BARE CONDUCTOR | GROUND GRID CABLE |  |
| CG1051 | 280 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG1059 | 335 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG902 | 157 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG906 | 182 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG907 | 146 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG910 | 161 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG914 | 121 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG915 | 119 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG920 | 134 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG926 | 171 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG927 | 176 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG928 | 252 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE | 11 |
| CG929 | 172 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG931 | 183 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG933 | 201 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG954 | 158 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG964 | 128 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG965 | 129 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |
| CG983 | 283 | 901 | LEVEL (4) \ 2 COND |  | 4/0 AWG | BARE CONDUCTORS | GROUND GRID CABLE |  |

001   WELDING RECEPTACLE ONE

| cable | to | lev | #cnd | gauge |
| --- | --- | --- | --- | --- |
| C408 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |

101     TURBINE CONTROL PANEL

| 101 TURBINE CONTROL PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | gauge |
| C1001 | 136 JB005B GENERATOR COMPARTMENT LEVEL 3 | 3 | 19 | 12 AWG |
| C006 | 363 JB130 GAS FUEL MODULE | 1 | 36 | 18 AWG |
| C014 | 363 JB130 GAS FUEL MODULE | 3 | 37 | 12 AWG |
| C017 | 135 JB005A GENERATOR COPARTMENT LOW FUEL LEVEL | 1 | 36 | 18 AWG |
| C018 | 135 JB005A GENERATOR COPARTMENT LOW FUEL LEVEL | 1S | 18 | 18 AWG |
| C037 | 115 JB002 ACCESSORY BASSE LEVEL 3 | 3 | 37 | 12 AWG |
| C038 | 234 JB020B TURBINE OFF BASE RACK LOW LEVEL | 1 | 36 | 18 AWG |
| C039 | 233 JB020A TURBINE OFF BASE RACK LOW LEVEL | 1S | 18 | 18 AWG |
| C041 | 233 JB020A TURBINE OFF BASE RACK LOW LEVEL | 1S | 18 | 18 AWG |
| C042 | 230 JB019A TURBINE OFF BASE RACK LEVEL 3 | 3 | 19 | 12 AWG |
| C073 | 387 JB020G TURBINE COMPARTMENT LOW LEVEL | 1S | 36 | 18 AWG |
| C074 | 387 JB020G TURBINE COMPARTMENT LOW LEVEL | 1S | 36 | 18 AWG |
| C076 | 135 JB005A GENERATOR COMPARTMENT LOW LEVEL | 1 | 18 | 18 AWG |
| C096 | 363 JB130 GAS FUEL MODULE | 1 | 36 | 18 AWG |
| C128 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 | 3 | 6 | 12 AWG |
| C182 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 | 3 | 12 | 12 AWG |
| C191 | 128 EXHAUST FRAME BLOWER 88TK-1 | 3 | 3 | 12 AWG |
| C193 | 128 EXHAUST FRAME BLOWER 88TK-2 | 3 | 3 | 12 AWG |
| C200 | 233 JB020A TURBINE OFF BASE RACK LOW LEVEL | 1S | 36 | 18 AWG |
| C201 | 390 JB034 TURBINE ROOF LOW LEVEL | 1 | 8 | 18 AWG |
| C256 | 230 JB019A TURBINE OFF BASE RACK LEVEL 3 | 3 | 3 | 10 AWG |
| C257 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 | 3 | 12 | 12 AWG |
| C285 | 363 JB130 GAS FUEL MODULE | 1S | 6 | 18 AWG |
| C414A | 622 FUEL GAS HEATER CONTROL PANEL | 3 | 7 | 12 AWG |
| C428 | 146 METALCLAD SWITCHGEAR | 3 | 6 | 12 AWG |
| C473 | 387 JB020G TURBINE COMPARTMENT LOW LEVEL | 1 | 2 | 18 AWG |
| C474 | 387 JB020G TURBINE COMPARTMENT LOW LEVEL | 1 | 2 | 18 AWG |
| C512 | 449 JB078 TURB. AIR INLET FILTER COMPARTMENT | 3 | 7 | 12 AWG |
| C513A | 157 TURBINE AIR INLET FILTER COMPARTMENT | 1S | 2 | 18 AWG |
| C513B | 157 TURBINE AIR INLET FILTER COMPARTMENT | 1S | 2 | 18 AWG |
| C513C | 157 TURBINE AIR INLET FILTER COMPARTMENT | 1S | 2 | 18 AWG |
| C516A | 447 INLET HEATING CONTROL VALVE | 3 | 2 | 12 AWG |
| C516E | 611 INLET HEATING ISOLATION VALVE | 3 | 2 | 12 AWG |
| C517A | 447 INLET HEATING CONTROL VALVE | 1 | 2 | 18 AWG |
| C517B | 447 INLET HEATING CONTROL VALVE | 1 | 2 | 18 AWG |
| C517D | 447 INLET HEATING CONTROL VALVE | 1 | 2 | 18 AWG |
| C517E | 447 INLET HEATING CONTROL VALVE | 1 | 2 | 18 AWG |
| C531 | 428 JB090 COOLING WATER MODULE LEVEL 3 | 3 | 6 | 12 AWG |
| C550A | 254 CUSTOMER DEVICES--PANELS | 3 | 19 | 12 AWG |
| C550B | 254 CUSTOMER DEVICES--PANELS | 3 | 19 | 12 AWG |
| C550C | 254 CUSTOMER DEVICES--PANELS | 3 | 19 | 12 AWG |
| C550D | 254 CUSTOMER DEVICES--PANELS | 3 | 19 | 12 AWG |
| C551A | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C551B | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C551C | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C553A | 254 CUSTOMER DEVICES--PANELS | 1 | 18 | 18 AWG |
| C553B | 254 CUSTOMER DEVICES--PANELS | 1 | 18 | 18 AWG |
| C554 | 254 CUSTOMER DEVICES--PANELS | 3 | 4 | 12 AWG |
| C590 | 201 LIMIT AMP | 3 | 6 | 12 AWG |
| C607 | 225 RELATIVE HUMIDITY SENSOR | 1 | 2 | 18 AWG |
| C615D | 156 FUEL GAS FLOW DEVICES | 1 | 2 | 18 AWG |
| C667-1 | 456 JB010 WATER WASH SKID LEVEL 3 | 3 | 12 | 12 AWG |
| C667-2 | 456 JB010 WATER WASH SKID LEVEL 3 | 3 | 12 | 12 AWG |
| C667-3 | 456 JB010 WATER WASH SKID LEVEL 3 | 3 | 12 | 12 AWG |
| C667-4 | 456 JB010 WATER WASH SKID LEVEL 3 | 3 | 12 | 12 AWG |
| C671 | 176 LUBE OIL DEMISTER (TURBINE) | 3 | 3 | 12 AWG |
| C678 | 257 JB037 PERFORMANCE MONITORING LOW LEVEL | 1 | 18 | 18 AWG |
| C727 | 455 JB297 AIR PROCESS SKID LEVEL 3 | 3 | 6 | 12 AWG |
| C819 | 563 JB386 GAS SCRUBBER LEVEL 3 | 3 | 19 | 12 AWG |
| C870 | 284 FIRE PROTECTION PANEL | 3 | 12 | 12 AWG |
| S875 | 115 JB002 ACCESSORY BASE LEVEL 3 | 3 | 19 | 12 AWG |
| S876 | 114 JB001 ACCESSORY BASE LOW LEVEL | 1 | 18 | 18 AWG |
| S877 | 174 JB79 WATER INJECTION SKID LEVEL 1 | 1 | 18 | 18 AWG |
| S878 | 236 TURBINE ROOF LOW LEVEL | 1 | 12 | 18 AWG |
| S879 | 173 JB72 WATER INJECTION SKID LEVEL 3 | 3 | 19 | 12 AWG |
| C880 | 942 CUSTOMER SUPPLIED MCC | 3 | 19 | 12 AWG |
| S881 | 429 88AB-1 MCC CUBICLE | 3 | 8 | 12 AWG |
| S882 | 231 JB019B TURBINE OFF BASE LEVEL-3 | 3 | 19 | 12 AWG |
| C883 | 942 CUSTOMER SUPPLIED MCC | 3 | 19 | 12 AWG |
| S891 | 430 DEMIN WATER FORWARDING JB01 | 3 | 4 | 12 AWG |
| S892 | 430 DEMIN WATER FORWARDING JB01 | 1 | 2 | 18 AWG |
| S893 | 427 LIQUID FUEL FORWARDING JB01 | 3 | 4 | 12 AWG |
| S894 | 427 LIQUID FUEL FORWARDING JB01 | 1 | 2 | 18 AWG |

102   GENERATOR CONTROL PANEL

| 102 GENERATOR CONTROL PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C049 | 146 METALCLAD WITCHGEAR | 3 | 37 | 12 AWG |
| C083 | 146 METALCLAD WITCHGEAR | 3 | 12 | 10 AWG |
| C235A | 146 METALCLAD WITCHGEAR | 3 | 12 | 10 AWG |
| C235B | 146 METALCLAD WITCHGEAR | 3 | 12 | 10 AWG |
| C236A | 581 JB005N GEN. NUETRAL ACCESSORIES COMP. LEVEL 3 | 3 | 12 | 10 AWG |
| C236B | 581 JB005N GEN. NUETRAL ACCESSORIES COMP. LEVEL 3 | 3 | 12 | 10 AWG |
| C236C | 146 METALCLAD WITCHGEAR | 3 | 12 | 10 AWG |
| C417A | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C418A | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C420A | 254 CUSTOMER DEVICES--PANELS | 3 | 4 | 10 AWG |
| C420B | 254 CUSTOMER DEVICES--PANELS | 3 | 4 | 10 AWG |
| C549 | 254 CUSTOMER DEVICES--PANELS | 1 | 18 | 18 AWG |
| C610A | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610H | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610HA | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610V | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C611 | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C611A | 254 CUSTOMER DEVICES--PANELS | 3 | 6 | 12 AWG |
| C743 | 201 LIMIT AMP | 3 | 2 | 10 AWG |

108     AUXILARY REPLAY PANEL

| 108 AUXILARY REPLAY PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C235C | 146 METAL CLAD SWITCHGEAR | 3 | 12 | 10 AWG |
| C421 | 108 AUXILIARY PANEL | 3 | 12 | 12 AWG |
| C421A | 108 AUXILIARY PANEL | 3 | 12 | 12 AWG |
| C421B | 108 AUXILIARY PANEL | 3 | 12 | 12 AWG |
| C421C | 108 AUXILIARY PANEL | 3 | 12 | 12 AWG |
| C422 | 108 AUXILIARY PANEL | 3 | 6 | 12 AWG |
| C422A | 108 AUXILIARY PANEL | 3 | 6 | 12 AWG |
| C426 | 254 CUSTOMER DEVICES--PANELS | 1 | 12 | 18 AWG |
| C426A | 254 CUSTOMER DEVICES--PANELS | 1 | 3 | 18 AWG |
| C549A | 254 CUSTOMER DEVICES--PANELS | 1 | 18 | 18 AWG |
| C591 | 183 AUXILIARY POWER TRANSFORMER | 3 | 2 | 10 AWG |
| C593 | 183 AUXILIARY POWER TRANSFORMER | 3 | 4 | 10 AWG |
| C610B | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610C | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610D | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610E | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610F | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610FA | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610FB | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610FC | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610J | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |
| C610W | 254 CUSTOMER DEVICES--PANELS | 3 | 12 | 12 AWG |

114   JB001  ACCESSORY BASE   LOW LEVEL

| 114 JB001 ACCESSORY BASE LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C172 | 201 LIMIT AMP | 1 | 18 | 18 AWG |
| S876 | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |

115     JB002   ACCESSORY BASE   LEVEL 3

| 115 JB001 ACCESSORY BASE LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C037 | 101 TURBINE CONTROL PANEL | 3 | 37 | 12 AWG |
| C161 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 10 AWG |
| C270 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 12 AWG |
| S875 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| S886 | 429 88AB-1 MCC CUBICLE | 3 | 2 | 10 AWG |

118     ACCESSORY BASE MOTORS

| 118 ACCESSORY BASE MOTORS |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C027 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 2 AWG |

119     ACCESSORY BASE

| 119 ACCESSORY BASE |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| CG915 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

121     TURBINE BASE

| 121 TURBINE BASE |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| CG914 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

122     TURBINE ROOF MOUNTED DEVICES

| 122 TURBINE ROOF MOUNTED DEVICES |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C199 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C199A | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |

125     JB055   TURBINE BASE   LOW LEVEL

| 125 JB055 TURBINE BASE LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C117A | 208 VIBRATION MONITOR PANEL | 1 | 18 | 18 AWG |

126     JB056   TURBINE BASE   LOW LEVEL

| 126 JB056 TURBINE BASE LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C117B | 208 VIBRATION MONITOR PANEL | 1 | 18 | 18 AWG |

127     JB085   LOAD GEAR COMPARTMENT   LOW LEVEL

| 127 JB085 LOAD GEAR COMPARTMENT LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | Gauge |
| C117C | 208 VIBRATION MONITOR PANEL | 1 | 9 | 18 AWG |

128     EXHAUST FRAME BLOWER   88TK-1

| 128 EXHAUST FRAME BLOWER 88TK-1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C071 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C190 | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |
| C191 | 101 TURBINE CONTROL PANEL | 3 | 3 | 12 AWG |
| CG964 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

129     EXHAUST FRAME BLOWER   88TK-2

| 129 EXHAUST FRAME BLOWER 88TK-2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C072 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C192 | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |
| C193 | 101 TURBINE CONTROL PANEL | 3 | 3 | 12 AWG |
| CG965 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

133     JB005C    GENERATOR COMPARTMENT   LEVEL 4

| 133 JB005C GENERATOR COMPARTMENT LEVEL 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C059 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 10 AWG |

134     GENERATOR COMPARTMENT

| 134 GENERATOR COMPARTMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG920 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

135     JB005A    GENERATOR COMPARTMENT   LOW LEVEL

| 135 JB005A GENERATOR COMPARTMENT LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C017 | 101 TURBINE CONTROL PANEL | 1 | 36 | 18 AWG |
| C018 | 101 TURBINE CONTROL PANEL | 1S | 18 | 18 AWG |
| C076 | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |
| C094B | 562 STATIC VOLTAGE REGULATOR—EX2000R | 1 | 8 | 18 AWG |

136     JB005B   GENERATOR COMPARTMENT   LEVEL 3

| 136 JB005B GENERATOR COMPARTMENT LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C001 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C123 | 562 STATIC VOLTAGE REGULATOR--EX2000R | 3 | 6 | 10 AWG |
| C219 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 12 AWG |
| C776 | 151 JB215 GENERATOR FILTER SEQUENCER | 3 | 5 | 12 AWG |
| C777 | 151 JB215 GENERATOR FILTER SEQUENCER | 3 | 2 | 12 AWG |

146     METALCLAD SWITCHGEAR

| 146 METALCLAD SWITCHGEAR |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C049 | 102 GENERATOR CONTROL PANEL | 3 | 37 | 12 AWG |
| C077 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C080 | 335 BUS DUCT | 3 | 3 | 12 AWG |
| C083 | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C148 | 562 STATIC VOLTAGE REGULATOR--EX2000R | 3 | 4 | 10 AWG |
| C235A | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C235B | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C235C | 108 AUXILIARY RELAY PANEL | 3 | 12 | 10 AWG |
| C36C | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C237 | 334 PEECC MOTOR CONTROL CENTER | 4 | 2 | 6 AWG |
| C428 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG |
| C745A | 329 CRANKING MOTOR TRANSFORMER | 5 | 3 |  |
| CG907 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

149     CRANKING MOTOR

| 149 CRANKING MOTOR |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C575 | 201 LIMIT LAMP | 5 | 3 |  |

151     JB215   GENERATOR FILTER SEQUENCER

| 151 JB215 GENERATOR FILTER SEQUENCER |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C776 | 136 JB005B GENERATOR COMPARTMENT LEVEL 3 | 3 | 5 | 12 AWG |
| C777 | 136 JB005B GENERATOR COMPARTMENT LEVEL 3 | 3 | 2 | 12 AWG |

156     FUEL GAS FLOW DEVICES

| 156 FUEL GAS FLOW DEVICES |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C615D | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |

157     TURBINE AIR INLET FILTER COMPARTMENT

| 157 TURBINE AIR INLET FILTER COMPARTMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C513A | 101 TURBINE CONTROL PANEL | 1S | 2 | 18 AWG |
| C513B | 101 TURBINE CONTROL PANEL | 1S | 2 | 18 AWG |
| C513C | 101 TURBINE CONTROL PANEL | 1S | 2 | 18 AWG |
| CG902 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

158     JB005B   GAS SCRUBBER

| 158 JB005B GAS SCRUBBER |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG954 | 901 CUSTOMER GROUND PANEL | 4 | 2 | 4/0 AWG |

161     COOLING WATER MODULE #1

| 161 COOLING WATER MODULE #1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG910 | 901 CUSTOMER GOUND GRID | 4 | 2 | 4/0 AWG |

171     GAS FUEL (VALVE) MODULE

| 171 GAS FUEL (VALVE) MODULE |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG926 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

172     AIR PROCESS SKID

| 172 AIR PROCESS SKID |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG929 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

173    JB72 WATER INJECTION SKID LEVEL 3

| 173 JB72 WATER INJECTION SKID LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S879 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |

174     JB79 WATER INJECTION SKID LEVEL 1

| 174 JB79 WATER INJECTION SKID LEVEL 1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S877 | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |

175     WATER INJECTION SKID 480 VOLT SUPPLY

| 175 WATER INJECTION SKID 480 VOLT SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C885 | 183 AUXILIARY POWER TRANSFORMER | 1 | 3 | CUST |

176     LUBE OIL DEMISTER (TURBINE)

| 176 LUBE OIL DEMISTER (TURBINE) |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C671 | 101 TURBINE CONTROL PANEL | 3 | 3 | 12 AWG |
| C672 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C672A | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |
| CG927 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

182    MAIN TRANSFORMER (STEP UP)

| 182 MAIN TRANSFORMER (STEP UP) |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C406 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C407 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C409A | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |
| C409B | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |
| CG906 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

183    AUXILARY POWER TRANSFORMER

| 183 AUXILARY POWER TRANSFORMER |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C401 | 254 CUSTOMER DEVICES--PANELS | 4 | 3 |  |
| C411 | 622 FUEL GAS HEATER CONTROL PANEL | 4 | 3 |  |
| C415 | 338 CUSTOMER 480V SUPPLY | 4 | 3 |  |
| C583 | 334 PEECC MOTOR CONTROL CENTER | 4 | 6 |  |
| C584 | 334 PEECC MOTOR CONTROL CENTER | 4 | 6 |  |
| C591 | 108 AUXILIARY RELAY PANEL | 3 | 2 | 10 AWG |
| C593 | 108 AUXILIARY RELAY PANEL | 3 | 4 | 10 AWG |
| C669 | 252 WATER WASH SKID | 4 | 3 |  |
| C745B | 329 CRANKING MOTOR TRANSFORMER | 5 | 3 |  |
| CG931 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |
| C885 | 175 WATER INJECTION SKID 480 VOLT SUPPLY | 4 | 3 | CUST |

201     LIMIT AMP

| 201 LIMIT AMP |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C172 | 114 JB001 ACCESSORY BASE LOW LEVEL | 1 | 18 | 18 AWG |
| C575 | 149 CRANKING MOTOR | 5 | 3 |  |
| C590 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG |
| C596 | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |
| C598 | 329 CRANKING MOTOR TRANSFORMER | 5 | 3 |  |
| C743 | 102 GENERATOR CONTROL PANEL | 3 | 2 | 10 AWG |
| C849 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 10 AWG |
| CG933 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

208     VIBRATION MONITOR PANEL

| 208 VIBRATION MONITOR PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C117A | 125 JB055 TURBINE BASE LOW LEVEL | 1 | 18 | 18 AWG |
| C117B | 126 JB056 TURBINE BASE LOW LEVEL | 1 | 18 | 18 AWG |
| C117A | 127 JB085 LOAD GEAR COMPARTMENT LOW LEVEL | 1 | 9 | 18 AWG |
| C145 | 325 JB163 GENERATOR COMPARTMENT LOW LEVEL | 1 | 8 | 18 AWG |

225     RELATIVE HUMIDITY SENSOR

| 225 RELATIVE HUMIDITY SENSOR |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C607 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |
| C607A | 339 JB298 PEEC LEVEL 3 | 3 | 3 | 12 AWG |

227     HAZARDOUS GAS MONITOR

| 227 HAZARDOUS GAS MONITOR |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C022 | 363 JB130 GAS FUEL MODULE | 2 | 9 | 18 AWG |
| C171 | 234 JB020B TURBINE OFF BASE RACK LOW LEVEL | 2 | 9 | 18 AWG |

230     JB019A   TURBINE OFF BASE RACK   LEVEL 3

| 230 JB019A TURBINE OFF BASE RACK LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C042 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C256 | 101 TURBINE CONTROL PANEL | 3 | 3 | 10 AWG |
| CG1031 | 901 CUSTOMER GROUND GRID | 4 | 1 | 1/0 AWG |

231     JB019B   TURBINE OFF CASE RACK   LEVEL 3

| 231 JB019B TURBINE OFF BASE RACK LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C128 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG |
| C182 | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| C257 | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| CG1032 | 901 CUSTOMER GROUND GRID | 4 | 1 | 1/0 AWG |
| S882 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |

233     JB020A   TURBINE OFF BASE RACK   LOW LEVEL

| 233 JB020A TURBINE OFF BASE RACK LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C039 | 101 TURBINE CONTROL PANEL | 1S | 18 | 18 AWG |
| C041 | 101 TURBINE CONTROL PANEL | 1S | 18 | 18 AWG |
| C200 | 101 TURBINE CONTROL PANEL | 1S | 36 | 18 AWG |
| CG1033 | 901 CUSTOMER GROUND GRID | 4 | 1 | 1\/ AWG |

234     JB020B   TURBINE OFF BASE RACK   LOW LEVEL

| 234 JB020B TURBINE OFF BASE RACK LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C009A | 751 FLAME DETECTOR INTERFACE MODULE PRIMARY | 3S | 8 | 18 AWG |
| C009B | 752 FLAME DETECTOR INTERFACE MODULE SECONDARY | 3S | 8 | 18 AWG |
| C038 | 101 TURINE CONTROL PANEL | 1 | 36 | 18 AWG |
| C171 | 227 HAZARDOUS GAS MONITOR | 2 | 9 | 18 AWG |
| CG1034 | 901 CUSTOMER GRUOND GRID | 4 | 1 | 1/0 AWG |

236     TURBINE ROOF LOW LEVEL

| 236 TURBINE ROOF LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S878 | 101 TURBINE CONTROL PANEL | 1 | 12 | 18 AWG |

252     WATER WASH SKID

| 252 WATER WASH SKID |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C669 | 183 AUXILIARY POWER TRANSFORMER | 4 | 3 |  |
| CG928 | 901 CUSTOMER GRUOND GRID | 4 | 2 | 4/0 AWG |

254     CUSTOMER DEVICES--PANELS

| 254 CUSTOMER DEVICES - PANELS |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C401 | 183 AUXILIARY POWER TRANSFORMER | 4 | 3 |  |
| C410A | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |
| C410B | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |
| C420A | 102 GENERATOR CONTROL PANEL | 3 | 4 | 10 AWG |
| C420B | 102 GENERATOR CONTROL PANEL | 3 | 4 | 10 AWG |
| C426 | 108 AUXILIARY RELAY PANEL | 1 | 12 | 18 AWG |
| C426A | 108 AUXILIARY RELAY PANEL | 1 | 3 | 18 AWG |
| C549 | 102 GENERATOR CONTROL PANEL | 1 | 18 | 18 AWG |
| C549A | 108 AUXILIARY RELAY PANEL | 1 | 18 | 18 AWG |
| C550A | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C550B | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C550C | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C550D | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C551A | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| C550B | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| C551C | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| C553A | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |
| C553B | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |
| C554 | 101 TURBINE CONTROL PANEL | 3 | 4 | 12 AWG |
| C610A | 102 GENERATOR CONTROL PANEL | 3 | 12 | 12 AWG |
| C610B | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610C | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610D | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610E | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610F | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610FA | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610FB | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610FC | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610H | 102 GENERATOR CONTROL PANEL | 3 | 12 | 12 AWG |
| C610HA | 102 GENERATOR CONTROL PANEL | 3 | 12 | 12 AWG |
| C610J | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C610V | 102 GENERATOR CONTROL PANEL | 3 | 12 | 12 AWG |
| C610W | 108 AUXILIARY RELAY PANEL | 3 | 12 | 12 AWG |
| C611 | 102 GENERATOR CONTROL PANEL | 3 | 12 | 12 AWG |
| C611A | 102 GENERATOR CONTROL PANEL | 3 | 6 | 12 AWG |
| CG1007 | 901 CUSTOMER GROUND GRID | 4 | 1 | 1/0 AWG |

257     JB037   PERFORMANCE MONITORING   LOW LEVEL

| 257 JB037 PERFORMANCE MONITORING LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C678 | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG |

280    GENERATOR NEUTRAL ACCESSORY COMPARTMENT  GNAC

| 280 GENERATOR NEUTRAL ACCESSORY COMPARTMENT GNAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG1051 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

283     FIRE PROTECTINO DEVICES

| 283 FIRE PROTECTION DEVICES |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG983 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

284     FIRE PROTECTION PANEL

| 284 FIRE PROTECTION PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C135 | 384 JB077A ACCESSORY BASE FP | 2S | 18 | 18 AWG |
| C136 | 384 JB077A ACCESSORY BASE FP | 2S | 18 | 18 AWG |
| C870 | 101 TURBINE CONTROL PANEL | 3 | 12 | 12 AWG |
| C871 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 12 AWG |
| C872 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 12 AWG |
| C874 | 339 JB298 PEECC LEVEL 3 | 4 | 3 | 10 AWG |

325     JB163   GENERATOR COMPARTMENT   LOW LEVEL

| 325 JB163 GENERATOR COMPARTMENT LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C145 | 208 VIBRATION MONITOR PANEL | 1 | 18 | 18 AWG |

329     CRANKING MOTOR TRANSFORMER

| 329 CRANKING MOTOR TRANSFORMER |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C598 | LIMIT AMP | 5 | 3 |  |
| C745A | METALCLAD SWITCHGEAR | 5 | 3 |  |
| C745B | AUXILIARY POWER TRANSFORMER | 3 | 3 |  |

333     PACKAGED ELECTRICAL-ELECTRONIC CONTROL CENTER-PEECC

| 333 PACKAGED ELECTRICAL-ELECTRONIC CONTROL CENTER-PEECC |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| CG1008 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

334    PEECC MOTOR CONTROL CENTER

| 334 PEECC MOTOR CONTROL CENTER |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C012 | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 4 AWG |
| C013C | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 10 AWG |
| C027 | 118 ACCESSORY BASE MOTORS | 4 | 3 | 2 AWG |
| C028 | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 8 AWG |
| C055A | 381 JB021A TURBINE OFF CASE RACK LEVEL 4 | 4 | 3 | 8 AWG |
| C055B | 381 JB021A TURBINE OFF CASE RACK LEVEL 4 | 4 | 3 | 8 AWG |
| C059 | 133 JB005C GENERATOR COMPARTMENT LEVEL 4 | 4 | 3 | 10 AWG |
| C071 | 128 EXHAUST FRAME BLOWER 88TK-1 | 4 | 3 |  |
| C072 | 129 EXHAUST FRAME BLOWER 88TK-2 | 4 | 3 |  |
| C077 | 146 METALCLAD SWITCHGEAR | 4 | 3 | 8 AWG |
| C102 | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 8 AWG |
| C125 | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 5 | 10 AWG |
| C149 | 441 JB131 GAS FUEL MODULE LEVEL 4 | 4 | 3 | 8 AWG |
| C199 | 122 TURBINE ROOF MOUNTED DEVICES | 4 | 3 | 8 AWG |
| C237 | 146 METALCLAD SWITCHGEAR | 4 | 2 | 6 AWG |
| C251 | 392 J004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 6 AWG |
| C402 | 939 UNIT AREA OUTDOOR LIGHTING | 4 | 3 |  |
| C403 | 742 SITE LIGHTS | 4 | 3 |  |
| C404 | 938 CEMS SYSTEM | 4 | 3 |  |
| C406 | 182 MAIN TRANSFORMER (STEP UP) | 4 | 3 |  |
| C407 | 182 MAIN TRANSFORMER (STEP UP) | 4 | 3 |  |
| C408 | 001 WELDING RECEPTACLE ONE | 4 | 3 |  |
| C409A | 182 MAIN TRANSFORMER (STEP UP) | 3 | 2 | 10 AWG |
| C409B | 182 MAIN TRANSFORMER (STEP UP) | 3 | 2 | 10 AWG |
| C410A | 254 CUSTOMER DECIVES--PANELS | 3 | 2 | 10 AWG |
| C410B | 254 CUSTOMER DECIVES--PANELS | 3 | 2 | 10 AWG |
| C480 | 514 CUSTOMER SWITCHGEAR | 3 | 3 | 12 AWG |
| C481 | 514 CUSTOMER SWITCHGEAR | 3 | 2 | 10 AWG |
| C533 | 438 JB090A COOLING WATER MODULE LEVEL 4 | 4 | 3 |  |
| C534 | 438 JB090A COOLING WATER MODULE LEVEL 4 | 4 | 3 |  |
| C535 | 438 JB090A COOLING WATER MODULE LEVEL 4 | 4 | 3 |  |
| C537 | 438 JB090A COOLING WATER MODULE LEVEL 4 | 4 | 3 |  |
| C538 | 438 JB090A COOLING WATER MODULE LEVEL 4 | 4 | 3 |  |
| C583 | 183 AUXILIARY POWER TRANSFORMER | 4 | 6 |  |
| C584 | 183 AUXILIARY POWER TRANSFORMER | 4 | 6 |  |
| C596 | 201 LIMIT AMP | 3 | 2 | 10 AWG |
| C672 | 176 LUBE OIL DEMISTER (TURBINE) | 4 | 3 |  |
| C809 | 441 JB131 GAS FUEL MODULE LEVEL 4 | 4 | 3 | 10 AWG |
| C817 | 441 JB131 GAS FUEL MODULE LEVEL 4 | 4 | 3 | 10 AWG |

335     BUS DUCT

| 335 BUS DUCT |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C080 | 146 METALCLAD SWITCHGEAR | 3 | 3 | 12 AWG |
| CG1059 | 901 CUSTOMER GROUND GRID | 4 | 2 | 4/0 AWG |

338     CUSTOMER 480V SUPPLY

| 338 CUSTOMER 480V SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C415 | 183 AUXILIARY POWER TRANSFORMER | 4 | 3 |  |

339     JB298   PEECC   LEVEL 3

| 339 JB298 PEECC LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C161 | 115 JB002 ACCESSORY BASE LEVEL 3 | 3 | 12 | 10 AWG |
| C190 | 128 EXHAUST FRAME BLOWER 88TK-1 | 3 | 2 | 10 AWG |
| C192 | 129 EXHAUST FRAME BLOWER 88TK-2 | 3 | 2 | 10 AWG |
| C199A | 122 TURBINE ROOF MOUNTED DEVICES | 3 | 2 | 10 AWG |
| C216 | 363 JB130 GAS FUEL MODULE | 3 | 3 | 12 AWG |
| C217 | 363 JB130 GAS FUEL MODULE | 3 | 2 | 10 AWG |
| C219 | 136 JB005B GENERATOR COMPARTMENT LEVEL 3 | 3 | 12 | 12 AWG |
| C249 | 581 JB005N GEN. NEUTRAL ACCESSORIES COMP. LEVEL 3 | 3 | 3 | 10 AWG |
| C270 | 115 JB002 ACCESSORY BASE LEVEL 3 | 3 | 12 | 12 AWG |
| C515 | 449 JB078 TURB. AIR INLET FILTER CMOPARTMENT | 3 | 3 | 6 AWG |
| C532 | 428 JB090 COOLING WATER MODULE LEVEL 3 | 3 | 12 | 12 AWG |
| C544 | 428 JB090 COOLING WATER MODULE LEVEL 3 | 3 | 12 | 10 AWG |
| C607A | 225 RELATIVE HUMIDITY SENSOR | 3 | 3 | 12 AWG |
| C672A | 176 LUBE OIL DEMISTER (TURBINE) | 3 | 2 | 10 AWG |
| C725 | 455 JB297 AIR PROCESS SKID LEVEL 3 | 3 | 3 | 12 AWG |
| C809A | 441 JB131 GAS FUEL MODULE LEVEL 4 | 3 | 2 | 10 AWG |
| C817A | 441 JB131 GAS FUEL MODULE LEVEL 4 | 3 | 2 | 10 AWG |
| C849 | 201 LIMIT AMP | 3 | 3 | 10 AWG |
| C871 | 284 FIRE PROTECTION PANEL | 3 | 3 | 12 AWG |
| C872 | 284 FIRE PROTECTION PANEL | 3 | 12 | 12 AWG |
| C874 | 284 FIRE PROTECTION PANEL | 4 | 3 | 10 AWG |

348     JB077A   ACCESSORY BASE  FP

| 348 JB077A ACCESSORY BASE FP |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C135 | 284 FIRE PROTECTION PANEL | 2S | 18 | 18 AWG |
| C136 | 284 FIRE PROTECTION PANEL | 2S | 18 | 18 AWG |

363    JB130   GAS FUEL MODULE

| 363 JB130 GAS FUEL MODULE |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C006 | 101 TURBINE CONTROL PANEL | 1 | 36 | 18 AWG |
| C014 | 101 TURBINE CONTROL PANEL | 3 | 37 | 12 AWG |
| C022 | 227 HAZARDOUS GAS MONITOR | 2 | 9 | 18 AWG |
| C096 | 101 TURBINE CONTROL PANEL | 1 | 36 | 18 AWG |
| C216 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 12 AWG |
| C217 | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |
| C285 | 101 TURBINE CONTROL PANEL | 1S | 6 | 18 AWG |

381   JB021A   TURBINE OFF BASE RACK   LEVEL 4

| 381 JB021A TURBINE OFF BASE RACK LEVEL 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C055A | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C055B | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| CG1038 | 901 CUSTOMER GROUND GRID | 4 | 1 | 1/0 AWG |

387     JB020G   TURBINE COMPARTMENT   LOW LEVEL

| 387 JB020G TURBINE COMPARTMENT LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C073 | 101 TURBINE CONTROL PANEL | 1S | 36 | 18 AWG |
| C074 | 101 TURBINE CONTROL PANEL | 1S | 36 | 18 AWG |
| C473 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |
| C474 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |

390     JB034   TURBINE ROOF   LOW LEVEL

| 390 JB034 TURBINE ROOF LOW LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C201 | 101 TURBINE CONTROL PANEL | 1 | 8 | 18 AWG |

392     JB004 ACCESSORY BASE LEVEL 4

| 392 JB004 ACCESSORY BASE LEVEL 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C012 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 4 AWG |
| C012C | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 10 AWG |
| C028 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C102 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C125 | 334 PEECC MOTOR CONTROL CENTER | 4 | 5 | 10 AWG |
| C251 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 6 AWG |
| S884 | 429 88AB-1 MCC CUBICLE | 4 | 3 | 4 AWG |

427     LIQUID FUEL FORWARDING SKID JB01

| 427 LIQUID FUEL FORWARDING SKID JB01 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S893 | 101 TURBINE CONTROL PANEL | 3 | 4 | 12 AWG |
| S894 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |

428     JB090  COOLING WATER MODULE   LEVEL 3

| 428 JB090 COOLING WATER MODULE LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C531 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG |
| C532 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 12 AWG |
| C544 | 339 JB298 PEECC LEVEL 3 | 3 | 12 | 10 AWG |

429 88AB-1 MCC CUBICLE

| 429 88AB-1 MCC CUBICLE |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S884 | 392 JB004 ACCESSORY BASE LEVEL 4 | 4 | 3 | 4 AWG |
| S886 | 115 JB002 ACCESSORY BAST LEVEL 3 | 3 | 2 | 10 AWG |
| S881 | 101 TURBINE CONTROL PANEL | 3 | 8 | 12 AWG |

430     DEMIN WATER FORWARDING JB01

| 430 DEMIN WATER FORWARDING JB01 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| S891 | 101 TURBINE CONTROL PANEL | 3 | 4 | 12 AWG |
| S892 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |

438     JB090A  COOLING WATER MODULE   LEVEL 4

| 438 JB090A COOLING WATER MODULE LEVEL 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | Gauge |
| C533 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C534 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C535 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C537 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |
| C538 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |

441     JB131   GAS FUEL MODULE   LEVEL 4

| 441 JB131 GAS FUEL MODULE LEVEL 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | Gauge |
| C149 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 8 AWG |
| C809 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 10 AWG |
| C809A | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |
| C817 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 | 10 AWG |
| C817A | 339 JB298 PEECC LEVEL 3 | 3 | 2 | 10 AWG |

447     INLET HEATING CONTROL VALVE

| 447 INLET HEATING CONTROL VALVE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C516A | 101 TURBINE CONTROL PANEL | 3 | 2 | 18 AWG |
| C517A | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |
| C517 | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |
| C517D | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |
| C517E | 101 TURBINE CONTROL PANEL | 1 | 2 | 18 AWG |

449     JB078   TURB. AIR INLET FILTER COMAPRTMENT

| 449 JB078 TURBINE AIR INLET FILTER COMPARTMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C512 | 101 TURBINE CONTROL PANEL | 3 | 7 | 12 AWG |
| C515 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 6 AWG |

455     JB297   AIR PROCESS SKID   LEVEL 3

| 455 JB297 AIR PROCESS SKID LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C725 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 12 AWG |
| C727 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG |

456     JB010  WATER WASH SKID   LEVEL 3

| 456 JB010 WATER WASH SKID LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C667-1 | 101 TURBINE CONTROL PANEL | 1 | 12 | 12 AWG |
| C667-2 | 101 TURBINE CONTROL PANEL | 1 | 12 | 12 AWG |
| C667-3 | 101 TURBINE CONTROL PANEL | 1 | 12 | 12 AWG |
| C667-4 | 101 TURBINE CONTROL PANEL | 1 | 12 | 12 AWG |

514     CUSTOMER SWITCHGEAR

| 514 CUSTOMER SWITCHGEAR |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C480 | 334 PEECC MOTOR CONTROL CENTER | 3 | 3 | 12 AWG |
| C481 | 334 PEECC MOTOR CONTROL CENTER | 3 | 2 | 10 AWG |

562    STATIC VOLTAGE REGULATOR--EX2000R

| 562 STATIC VOLTAGE REGULATOR – EX2000R |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C094B | 135 JB005A GENERATOR COMPARTMENT LOW LEVEL | 1 | 8 | 18 AWG |
| C123 | 136 JB005B GENERATOR COMPARTMENT LEVEL 3 | 3 | 6 | 10 AWG |
| C148 | 146 METALCLAD SWITCHGEAR | 3 | 4 | 10 AWG |

563     JB386   GAS SCRUBBER   LEVEL 3

| 563 JB386 GAS SCRUBBER LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C819 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |

581    JB005N   GEN. NEUTRAL ACCESSORIES COMP.  LEVEL 3

| 581 JB005N GENERATOR NEUTRAL ACCESSORIES COMPARTMENT LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C236A | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C236B | 102 GENERATOR CONTROL PANEL | 3 | 12 | 10 AWG |
| C249 | 339 JB298 PEECC LEVEL 3 | 3 | 3 | 10 AWG |

611     INLET HEATING ISOLATIN VALVE

| 611 INLET HEATING ISOLATION VALVE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C516E | 101 TURBINE CONTROL PANEL | 3 | 2 | 12 AWG |

622     FUEL GAS HEATER CONTROL PANEL

| 622 FUEL GAS HEATER CONTROL PANEL |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C411 | 183 AUXILIARY POWER TRANSFORMER | 4 | 3 |  |
| C413 | 753 JB309 FUEL GAS HEATING SKID LEVEL 3 | 1 | 6 | 18 AWG |
| C414 | 753 JB309 FUEL GAS HEATING SKID LEVEL 3 | 3 | 3 | 12 AWG |
| C414A | 101 TURBINE CONTROL PANEL | 3 | 7 | 12 AWG |

742     SITE LIGHTS

| 742 SITE LIGHTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C403 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |

751     FLAME DETECTOR INTERFACE MODULE   PRIMARY

| 751 FLAME DETECTOR INTERFACE MODULE PRIMARY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C009A | 234 JB020B TURBINE OFF BASE RACK LOW LEVEL | 3S | 8 | 18 AWG |

752    FLAME DETECTOR INTERFACE MODULE   SECONDARY

| 752 FLAME DETECTOR INTERFACE MODULE SECONDARY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C009B | 234 JB020B TURBINE OFF BASE RACK LOW LEVEL | 3S | 8 | 18 AWG |

753     JB309   FUEL GAS HEATING SKID   LEVEL 3

| 753 JB309 FUEL GAS HEATING SKID LEVEL 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable | to | lev | #cnd | gauge |
| C413 | 622 FUEL GAS HEATER CONTROL PANEL | 1 | 6 | 18 AWG |
| C414 | 622 FUEL GAS HEATER CONTROL PANEL | 3 | 3 | 12 AWG |

901     CUSTOMER GROUND GRID

| 901 CUSTOMER GROUND GRID |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | gauge |
| CG1007 | 254 CUSTOMER DECIVES--PANELS | 4 | 1 | 1/0 AWG |
| CG1008 | 333 PACKAGED DELECTRICAL-ELECTRIC CONTROL CENTER-PEECC | 4 | 2 | 4/0 AWG |
| CG1031 | 230 JB019A TURBINE OFF BASE RACK LEVEL 3 | 4 | 1 | 1/0 AWG |
| CG1032 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 | 4 | 1 | 1/0 AWG |
| CG1033 | 233 JB020A TURBINE OFF BASE RACK LOW LEVEL | 4 | 1 | 1/0 AWG |
| CG1034 | 234 JB020B TURBINE OFF BASE RACK LOW LEVEL | 4 | 1 | 1/0 AWG |
| CG1038 | 381 JB021A TURBINE OFF BASE RACK LEVEL 4 | 4 | 1 | 1/0 AWG |
| CG1051 | 280 GENERATOR NEUTRAL ACCESSORY COMPARTMENT GNAC | 4 | 2 | 4/0 AWG |
| CG1059 | 335 BUS DUCT | 4 | 2 | 4/0 AWG |
| CG902 | 157 TURBINE AIR INLET FILTER COMPARTMENT | 4 | 2 | 4/0 AWG |
| CG906 | 182 MAIN TRANSFORMER (STEP UP) | 4 | 2 | 4/0 AWG |
| CG907 | 146 METALCLAD SWITCHGEAR | 4 | 2 | 4/0 AWG |
| CG910 | 161 COOLING WATER MODULE #1 | 4 | 2 | 4/0 AWG |
| CG914 | 121 TURBINE BASE | 4 | 2 | 4/0 AWG |
| CG915 | 119 ACCESSORY BASE | 4 | 2 | 4/0 AWG |
| CG920 | 134 GENERATOR COMPARTMENT | 4 | 2 | 4/0 AWG |
| CG926 | 171 GAS FUEL (VALVE) MODULE | 4 | 2 | 4/0 AWG |
| CG927 | 176 LUBE OIL DEMISTER (TURBINE) | 4 | 2 | 4/0 AWG |
| CG928 | 252 WATER WASH SKID | 4 | 2 | 4/0 AWG |
| CG929 | 172 AIR PROCESS SKID | 4 | 2 | 4/0 AWG |
| CG931 | 183 AUXILIARY POWER TRANSFORMER | 4 | 2 | 4/0 AWG |
| CG933 | 201 LIMIT AMP | 4 | 2 | 4/0 AWG |
| CG954 | 158 GAS SCRUBBER | 4 | 2 | 4/0 AWG |
| CG964 | 128 EXHAUST FRAME BLOWER 88TK-1 | 4 | 2 | 4/0 AWG |
| CG965 | 129 EXHASUT FRAME BLOWER 88TK-2 | 4 | 2 | 4/0 AWG |
| CG983 | 283 FIRE PROTECTION DEVICES | 4 | 2 | 4/0 AWG |

938    CEMS SYSTEM

| 938 CEMS SYSTEM |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | gauge |
| C404 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |

939    UNIT AREA OUTDOOR LIGHTING

| 939 UNIT AREA OUTDOOR LIGHTING |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | to | lev | #cnd | gauge |
| C402 | 334 PEECC MOTOR CONTROL CENTER | 4 | 3 |  |

940     DEMIN WATER FORWARDING JB02

| 940 DEMIN WATER FORWARDING JB02 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C889 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST |
| C890 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST |

941     LIQUID FUEL FORWARDING JB02

| 941 LIQUID FUEL FORWARDING JB02 |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C887 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST |
| C888 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST |

942     CUSTOMER SUPPLIED MCC

| 942 CUSTOMER SUPPLIED MCC |  |  |  |  |
| --- | --- | --- | --- | --- |
| cable | To | lev | #cnd | Gauge |
| C880 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C883 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG |
| C887 | 941 DEMIN WATER FORWARDING JB02 | 4 | 3 | CUST |
| C888 | 941 DEMIN WATER FORWARDING JB02 | 4 | 3 | CUST |
| C889 | 940 LIQUID FUEL FORWARDING JB02 | 4 | 3 | CUST |
| C890 | 940 LIQUID FUEL FORWARDING JB02 | 4 | 3 | CUST |

Notes

1 “C” PREFIX INDICATES CABLE SUPPLIED BY OTHERS THAN GE-GAS TURBINE DEVISION. CONTROL CABLES WITH “C”

PREFIX CONTAIN A NOMINAL NUMBER OF SPARES.

2 “C”  PREFIX CABLES TO BE RATED NOT LESS THAN 90 DEC. C.

3 CABLE GLANDS/STRESS RELIEFS FOR CONNECTING CABLES AT JUNTION BOXES/DEVICES ARE TO BE SUPPLIED BY

OTHERS.

4 BEND RADIUS – BENDS SHALL BE SO MADE THAT CABLE WILL NOT BE DAMAGED. AND RADIUS OF THE INNER EDGE

OF ANY BEND SHALL NOT BE LESS THAN SHOWN IN TABLE.  THIS RADIUS DOES NOT INCLUDE PULLING TENSINO

CALCULATION.  SEE M.L. TIEM 0435 FOR FURTHER DEFINITION.

5 CABLES SUPPLIED BY OTHERS THAT ARE SHOWN ON THIS DWG. ARE ONLY FOR THOSE WHICH INTERFACE WITH

GAS TURBINE SUPPLIED EQUIPMENT.

6 MAKEUP OF “C” PREFIX CABLES ARE SUGGESTED TO ENSURE SUFFICIENT CONDUCTOR COUNT.

7 “C” PREFIX CABLES FOR LEVEL 4 AND LEFEL 5 POWER SUPPLY ARE SIZED BY OTHERS.

8 SEE OUTLINE. GAS TURBINE PACKAGE CONNECTION – ELECTRICAL DIAG.. M.L. ITEM 0301 FOR LOCATION OF CABLE

DESTINATION POINTS (JB’S. ETC.) WITHIN EACH ON-BASE COMPARTMENT.

9 CABLE TO BE INSTALLED WITH ADEQUATE SEPARATION BETWEEN DIFFERENT LEVELS AND IN PROPER CONDUIT

OR RACEWAY MATERIAL. SEE M.L. ITEM 0435. AND IN ACCORDANCE WITH LATEST ELECTRICAL CODES.

10 GROUND CABLES ARE TO BE SUPPLIED ON ALL EQUIPMENT.  TWO CABLE CONNECTIONS ARE DIAGONALLY

OPPOSED.

11 ONE CABLE REQUIRED PER SITE.

12 CABLE REQUIRED FOR UNITS 1 & 3 ONLY.

13 CABLE REQUIRED FOR UNITS 2 & 4 ONLY.

14 FOR ADDITIONAL COMMUNICATION CABLES SEE M.L. ITEM 4108.

15 REFER TO DWG. 358B1001 FOR CABLE ROUTING.