NOTES:

- DRAFT THAT INCLUDES DUAL FUEL DEVICES.

- SYSTEM PARAMETERS AND SPECIFICATIONS ARE BASED ON GE DRAWING 377A3127 (PROVIDED BY CUSTOMER). INCLUDING REQUIRMENTS FOR DUAL FUEL SYSTEMS PER CUSTOMER SCOPE OF WORK.

DEVICE SUMMARY (GAS TURBINE)

System                               Title

0415                                   CONTROL DEVICES – TURBINE

0416			    LUBE OIL SYSTEM

0417                                   COOL & SEAL AIR SYSTEM

0418                                   TRIP OIL SYSTEM

0419                                   CONTROL AIR

0420                                   COOLING WATER SYSTEM

0421                                   STARTING SYSTEM

0422                                   GAS FUEL SYSTEM

0424			    LIQUID FUEL SYSTEM

0425			    ATOMIZING AIR SYSTEM

0426                                   FIRE PROTECTION SYSTEM

0432                                   INLET AIR HEATING

0434                                   HYDRAULIC SUPPLY SYSTEM

0436                                   HEAT & VENT SYSTEM

0440                                   LOAD EQUIPMENT

0442                                   TURBINE & COMPRESSOR WASH

0453                                   COOLING WATER SYSTEM

0461                                   WATER WASH UNIT

0462			    WATER INJECTION SYSTEM

0469                                   INLET GUIDE VANE SYSTEM

0471                                   INLET AND EXHAUST

0474                                   HAZARDOUS GAS DETECTION

0477                                   FUEL PURGE

0484                                   GAS SCRUBBER

0485                                   GAS HEATER

0492                                   PERFORMANCE MONITOR

SWITCH SETTINGS

CONTACT CONDITION                                                      ADDITIONAL CONTACTS

NO -  NORMALLY OPEN                                                CEC -    ADDITIONAL CONTACT:

NORMALLY CLOSED

ELECTRICALLY COMMON

NC -   NORMALLY CLOSED                                            CES -    ADDITIONAL CONTACT:

NORMALLY CLOSED

ELECTRICALLY SEPARATE

() -     PARENTHESIS INDICATES SETS OF                    OEC -    ADDITIONAL CONTACT:

CONTACTS                                                                          NORMALLY OPEN

ELECTRICALLY COMMON

OES -    ADDITIONAL CONTACT:

NORMALLY OPEN

ELECTRICALLY SEPARATE

EXAMPLE:  NORM = (2) NO-CEC

DEVICE               	SYSTEM 	SETTINGS

20AA-1             	 0425      	ATOMIZING AIRBYFASS VALVE

NORM= 1 TO 3 OPEN; 2 CLOSED

20AB-1              	0425                	STARTING ATOMIZING AIR COMPRESSOR ISO  SOLENOID VALVE

NORM=1 TO 3 OPEN; 2 CLOSED

20AP-1        	0419             	APU SHUTOFF VALVE

DE-ENERGIZED: 1 TO 2 CLOSED

ENERGIZED: 1 TO 2 OPEN

120 VAC; 60 HZ

PROTECTS DESSICANT FROM OVER TEMPERATURE

20BP-1            		0477    	       PURGE SYSTEM BYPASS SOLENOID VALVE

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

BY-PASS ORIFICE VALVE ACTUATION. FOR

LIQUID PURGE PRESSURE RATIO CONTROL

20CB-1             	0417           	COMPRESSOR BLEED SOL 3 WAY VALVE

NORM=B TO C OPEN; A CLOSED

20CF-1                    	0424                    Liquid Fuel pump Clutch Solenoid

norm=de-energized and disengaged

20FD-1                    	0427         	Fuel Forwarding STOP Solenoid Valve

Energized to OPEN; Fail closed on Power Loss

125vdc, 13.5 AMP in RUSH, 0.1 AMP Holding

20FG-1               	0418                    FUEL GAS STOP VALVE SOLENOID VALVE

NORM=OPEN; ENERGIZE TO CLOSE

20FK-1                        0424              	MULTIPORT FUEL VALVE SOLENOID

NORM=P TO PLUGGED; A-CLOSED; B OPEN; T DRAIN

20FL-1             	0418            	LIQUID FUEL STOP VALVE SOLENOID VALVE

NORM=OPEN; ENERGIZE TO CLOSE

20FP-1                   	0426          	FIRE PROTECTION-INITIAL DISCH SOLENOID VALVE  (ZONE 1)

INITIAL DISCHARGE (ZONE 1)

20FP-1E                	0426            	FIRE PROTECTION-EXTENDED DISCH SOLENOID VALVE (ZONE 1)

EXTENDED DISCHARGE (ZONE 1)

20FP-2                   	0426           	FIRE PROTECTION-INITIAL DISCH SOLENOID VALVE (ZONE 2)

INITIAL DISCHRAGE (ZONE 2)

20FP-2E                     	0426         	FIRE PROTECTION-EXTENDED DISCH SOLENOID VALVE (ZONE 2)

EXTENDED DISCHARGE (ZONE 2)

20FP-3                  	0426           	FIRE PROTECTION-INITIAL DISCH SOLENOID VALVE (ZONE 3)

INITIAL DISCHARGE (ZONE 3)

20FP-3E                     	0426   	FIRE PROTECTION-EXTENDED DISCH SOLENOID  VALVE (ZONE 3)

EXTENDED DISCHARGE (ZONE 3)

20HR-1              	0421          	HYDRAULIC RACHET STROKE SOL 4 WAY VALVE

PART OF TORQUE CONVERTOR

NORM=RETURN  POSITION; ENERGIZE TO STROKE

20PG-1                   	0477              	GAS FUEL SYSTEM PURGE SOLENOID VALVE

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

PRIMARY GAS FUEL PURGE

20PG-2                  	0477                 	GAS FUEL SYSTEM PURGE SOLENOID VALVE

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

PRIMARY GAS FUEL PURGE

20PG-3                 	0477              	GAS FUEL SYSTEM PURGE SOLENOID VALVE

NORM = 1 TO 3 OPEN, 2 CLOSED, PRESS AT 2

20PG-4          	0477                 	GAS FUEL SYSTEM PURGE SOLENOID VALVE

NORM = 1 TO 3 OPEN, 2 CLOSED, PRESS AT 2

20PL-1                     	0477            	LIQUID FUEL SYSTEM PURGE SOLENOID VALVE

PRIMARY LIQUID FUEL

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

20PL-2          	0477                  	LIQUID FUEL SYSTEM PURGE SOLENOID VALVE

NORM= 1 TO 3 OPEN; 2 CLOSED, PRESSURE AT 2

20PL-3                   	0477              	LIQUID FUEL SYSTEM PURGE SOLENOID VALVE

PRIMARY LIQUID FUEL

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

20PL-4                      	0477             	LIQUID FUEL SYSTEM PURGE SOLENOID VALVE

NORM= 1 TO 3 OPEN; 2 CLOSED, PRESSURE AT 2

20 TH-1               	0432                	INLET HEATING CONTROL VALVE TRIP SOLENOID VALVE

DE-ENERGIZED TO TRIP VA20-1

ENERGIZED TO OPERATE VA20-1

20TU-1             	0421             	TORQUE CONVERTER FILL/DRAIN SOLENOID VALVE

NORM=OPEN; ENERGIZE TO CLOSE

PART OF TORQUE CONVERTOR

20TV-1              	0418           	TURBINE COMPRESSOR IGV SOLENOID VLAVE

NORM=OPEN; ENERGIZE TO CLOSE

20TW-1          	 0442            	OFF-LINE COMPRESSOR WASH WATER INJ SOL (MOTOR) VALVE

115 VAC; 50/60 HZ 2.000A;

20TW-3                  	0442          	ON-LINE COMPRESSOR WASH WATER INJ SOL  (MOTOR) VALVE

115 VAC; 50/60 HZ; 2.000 A;

20VG-1               	0422        	FUEL GAS VENT SOLENOID VALVE

NORM=OPEN; ENERGIZE TO CLOSE

20VG-2               	0477           	FUEL GAS VENT SOLENOID VALVE

NORM=1 TO 3 OPEN; 2 CLOSED; PRESS AT 2

PRIMARY GAS PURGE VENT VALVE.

20VG-3              	0477            	FUEL GAS VENT SOLENOID VALVE

SOLEN. NORM= 1 TO 3 OPEN; 2 CLOSED; PRESS AT 2

20WN-1	0462	WATER INJECTION SOLENOID STOP VALVE

NORM=CLOSED; ENERGIZE TO OPEN

20WP-1                  	0477                	WATER INJECTION SYSTEM PURGE SOLENOID VALVE

PRI+SEC WATER PURGE SYSTEM

NORM=1 TO 3 OPEN; 2 CLOSED; PRESSURE AT 2

23AB-1                   	0425             	HEATER-STARTING ATOMIZING AIR COMPRESSOR MOTOR

60.00 W; 120 VAC; 1 PH; 60 HZ;

23AP-1                  	0419         	APU HEAT TRACING

100.0 W; 120 VAC; 1 PH; 60 HZ;

23BT-1         	0436                   	HEATER-TURBINE COMPT FAN MOTOR

200.00 W; 120 VAC; 1 PH; 60 HZ;

23CR-1                     	0421                	HEATER-CRANKING MOTOR

800.0 W; 120 VAC; 1 PH; 60 HZ;

23FC-1                   	0453            	HEATER-WATER COOLING FAN MOTOR

60.00 W; 120 VAC; 1 PH; 60 HZ;

23FC-2 	0453	HEATER-WATER COOLING FAN MOTOR

60.00 W; 120 VAC; 1 PH; 60 HZ;

23FC-3	0453	HEATER-WATER COOLING FAN MOTOR

60.00 W; 120 VAC; 1 PH; 60 HZ;

23FD-1	0427		LIQUID FUEL FORWARDING PUMP #1

MOTOR WINDING HEATERS

100Watt, 220 VAC, 1 phase, 60 Hertz

23FD-2	0427		LIQUID FUEL FORWARDING PUMP #2

MOTOR WINDING HEATERS

100Watt, 220 VAC, 1 phase, 60 Hertz

23FH-5	0485	FUEL HEATER

500.0 KW; 480 VAC; 3 PH; 60 HZ;

ISA DEVICE NAME: EH-1

23HA-1                    	0436         	SPACE HEATER- ACCESSORY COMPARTMENT

20.00 KW; 480 VAC; 3 PH; 60 HZ;

HEATING FOR FREEZE PROTECTION

23HA-2                  	0436       	SPACE HEATER- ACCESSORY COMPARTMENT

20.00 KW; 480 VAC; 3 PH; 60 HZ;

HEATING FOR FREEZE PROTECTION

23HA-3	0436	SPACE HEATER-ACCESSORY COMPARTMENT

3.600 KW; 480 VAC; 1 PH; 60 HZ;

HEATING FOR HUMIDITY CONTROL

23HG-1	0440	SPACE HEATER-GENERATOR

2.250 KW; 480 VAC; 3 PH; 60 HZ;

23HG-3                   	0440              	SPACE HEATER-GENERATOR

2.250 KW; 480 VAC; 3 PH; 60 HZ;

23HG-5                   	0440                 	SPACE HEATER-GENERATOR

2.250 KW; 480 VAC; 3 PH; 60 HZ;

23HQ-1	0434	HEATER-HYDRAULIC OIL PUMP MOTOR

75.00 W; 110 VAC; 1 PH; 60 HZ;

23HT-1  	0436            	SPACE HEATER-TURBINE COMPARTMENT

30.00 KW; 480 VAC; 3 PH; 60 HZ;

HEATING FOR FREEZE PROTECTION

23HT-2     	0436        	SPACE HEATER-TURBINE COMPARTMENT

30.00 KW; 480 VAC; 3 PH; 60 HZ;

HEATING FOR FREEZE PROTECTION

23HT-3	0436	SPACE HEATER-TURBINE COMPARTMENT

3.600 KW; 480 VAC; 1 PH; 60 HZ;

HEATING FOR HUMIDITY CONTROL

23QA-1	0416	HEATER-AUX LUBE OIL PUMP MOTOR

75.00 W; 110 VAC; 1 PH; 60 HZ;

23QT-1	0416	IMMERSION HEATER-LUBE OIL TANK

15.00 KW; 460 VAC; 3 PH; 60 HZ;

23QT-2	0416	IMMERSION HEATER-LUBE OIL TANK

15.00 KW; 460 VAC; 3 PH; 60 HZ;

23QV-2A	0416	SPACE HEATER-FOR 88QV-1A

75.00 W; 110 VAC; 1 PH; 60 HZ;

23TK-1	0417	TURBINE SHELL & EXHAUST FRAME BLOWER MOTOR HEATER

100.0 W; 120 VAC; 1 PH; 50/60 HZ;

HEATER TO BE DUAL RATED 100/120V 50/60HZ

23TK-2	0417	TURBINE SHELL & EXHAUST FRAME BLOWER MOTOR HEATER

100.0 W; 120 VAC;  1PH; 50/60 HZ;

HEATER TO BE DUAL RATED 100/120V 50/60HZ

23TW-1	0461	HEATER-WATER WASH PUMP MOTOR

60.00 W; 120 VAC; 1 PH; 60 HZ;

(PART OF 88TW-1)

23VL-1	0422	HEATER-GAS VALVE COMPT VENT FAN MOTOR

30.00 W; 120 VAC; 1 PH; 60 HZ;

23VL-2	0422	HEATER-GAS VALVE COMPT VENT FAN MOTOR

30.00 W; 120 VAC; 1 PH; 60 HZ;

23VS-1	0422	SPACE HEATER-VALVE COMPARTMENT

3.600 KW; 480 VAC; 3 PH; 60 HZ;

23WC-1	0453	HEATER-COOLING WATER PUMP MOTOR

100.0 W; 120 VAC; 1 PH; 60 HZ;

23WC-2	0453	HEATER-COOLING WATER PUMP MOTOR

100.0 W; 120 VAC; 1 PH; 60 HZ;

23WK-1	0461	IMMERSION HEATER WATER WASH

25.00 KW; 480 VAC; 3 PH; 60 HZ;

23WK-2	0461	IMMERSION HEATER WATER WASH

25.00 KW; 480 VAC; 3 PH; 60 HZ;

23WS-1	0461	WATER WASH SKID SPACE HEATER

10.00 KW; 480 VAC; 3 PH; 60 HZ;

23WN-1	0462	WATER INJECTION PUMP MOTOR SPACE HEATER

26AD-1                     	0419        	APU COOLING FAN TEMPERATURE SWITCH

INCREASING: 110.0+-5.000 F OR 43.33+-2.778 C

(DECREASING 100.0+-5.000 F OR 37.78+-2.778 C)

PREVENTS OVER HEATING OF THE DESICCANT AIR DRY

26AP-1	0419	APU THERMOSTAT

DECREASING: 45.00+-5.000 F OR 7.222+-0.5556 C

CONTROLLER FOR HEAT TRACING 23AP-1

26AP-2  	0419        	APU OVER TEMPERATURE SWITCH

INCREASING: 160.0+-5.000 F OR 71.11+-2.778 C

(DECREASING: 120.0+-5.000 F OR 48.89 +-2.778 C

NORM=(1) NC-OEC;

CONTROLS 20AP-1

26BT-1	0436	TURBINE COMPARTMENT TEMP SWITCH

INCREASING: 115.0+-5.000 F OR 46.11+-2.778 C

NORM=NC-OEC;

26BT-2	0436	TURBINE COMPARTMENT TEMP SWITCH

INCREASING; 300.0+-5.000 F OR 148.9+-2.778 C

NORM=NC-OEC;

26FH-5	0485	HEATER 23FH-5 ELEMENT OVERTEMPERATURE

TYPE K THERMOCOUPLE

UNGROUNDED;

HEATER ELEMENT OVERTEMPERATURE

ISA DEVICE NAME: TE-1H

26HA-1   	0436	ACCESSORY COMPARTMENT THERMOSTAT

DECREASING: 50.00+-2.000 F OR 10.00+-1.111 C

NORM=NC-OEC;

26HA-3	0436	ACCESSORY COMPARTMENT THERMOSTAT

DECREASING: 100.0+-2.000 F OR 37.78+-1.111 C

NORM=NC-OEC;

26HT-1  	0436   	TURBINE COMPARTMENT THERMOSTAT

DECREASING: 50.00+-2.000 F OR 10.00+-1.111 C

NORM=NC-OEC;

26HT-3	0436	TURBINE COMPARTMENT THERMOSTAT

DECREASING: 100.0+-2.000 F OR 37.78+-1.111 C

NORM=NC-OEC;

26QA-1	0416	LUBE OIL HEADER HIGH TEMP ALARM

INCREASING: 165.0+-3.000 F OR 73.89+-1.667 C

(DECREASING: 159.0+-3.000 F OR 70.56+-1.667 C)

NORM=(1) NC-OEC;

26QL-1	0416	LUBE OIL TANK TEMP HEATERS ON/OFF

DECREASING: 70.00+-3.000 F OR 21.11+-1.667 C

(INCREASING: 84.00+-8.000 F OR 28.89+-4.444 C)

NORM=(1) NC-OEC;

26QN-1	0416	LUBE OIL TANK TEMP-NORMAL

DECREASING: 60.00+-3.000 F OR 15.56+-1.667 C

(INCREASING: 61.25+-0.7500 F OR 16.25+-0.4167 C)

NORM=(1) NO=CEC;

26QT-1A	0416	LUBE OIL HEADER HIGH TEMP TRIP

INCREASING: 175.0+-3.000 F OR 79.44+-1.667 C

(DECREASING: 169.0+-3.000 F OR 76.11+-1.667 C)

NORM=(1) NC-OEC;

26QT-1B	0416	LUBE OIL HEADER HIGH TEMP TRIP

INCREASING: 175.0+-3.000 F OR 79.44+-1.667 C

(DECREASING: 169.0+-3.000 F OR 76.11+-1.667 C)

NORM=(1) NC-0EC;

26TW-4	0461	-5 TO 50 MV, TEMPERATURE ELEMENT FOR TANK TEMPERATURE

INCREASING: 180.0+-5.000 F OR 82.22+-2.778 C

(DECREASING: 52.00+-2.000 F OR 11.11+-1.111 C)

THIRD SETPOINT 65F +/-2F INCREASING

26VS-1	0422	THERMOSTAT-GAS FUEL MODULE

INCREASING: 40.00+-5.000 F OR 4.444+-2.778 C

26VW-3	0461	TEMPERATURE ELEMENT FOR COMPT. SPACE HEATER AND VENT FAN

TYPE J THERMOCOUPLE

1 ELEMENT;

OPERATE VENT FAN AT 95 DEGREES F INCREASING,

OPERATE SPACE HEATER AT 65 DECREES F DECREASING,

ALARM AT 43 DEGREES F  DECREASING,

ALARM AT 130 DEGREES F INCREASING

27AD-1      	0419  	APU LOSS OF POWER ALARM

WIRE TO MK V / MK VI

27TF-1	0471	TURBINE INLET AIR FILTER UNDERVOLTAGE

NORM=(2) NO-CEC;

28FD-3P	0415	FLAME DETECTOR COMBUSTION CHAMBER #3-PRIMARY ZONE

28FD-3S	0415	FLAME DETECTOR COMBUSTION CHAMBER #3-SECONDARY ZONE

28FD-4P	0415	FLAME DETECTOR COMBUSTION CHAMBER #4-PRIMARY ZONE

28FD-4S	0415	FLAME DETECTOR COMBUSTION CHAMBER #4-SECONDARY ZONE

28FD-7P	0415	FLAME DETECTOR COMBUSTION CHAMBER #7-PRIMARY ZONE

28FD-7S	0415	FLAME DETECTOR COMBUSTION CHAMBER #7-SECONDARY ZONE

28FD-8P	0415	FLAME DETECTOR COMBUSTION CHAMBER #8-PRIMARY ZONE

28FD-8S	0415	FLAME DETECTOR COMBUSTION CHAMBER #8-SECONDARY ZONE

2FP-1	0426	FIRE PROTECTION-INITIAL DISCHARGE TIMER (ZONE 1)

INITIAL DISCHARGE

2FP-1E	0426	FIRE PROTECTION-EXTENDED DISCHARGE TIMER (ZONE1)

EXTENDED DISCHARGE

2FP-2	0426	FIRE PROTECTION-INITIAL DISCHARGE TIMER (ZONE 2)

INITIAL DISCHARGE

2FP-2E	0426	FIRE PROTECTION-EXTENDED DISCHARGE TIMER (ZONE 2)

EXTENDED DISCHARGE

2FP-3	0426	FIRE PROTECTION-INITIAL DISCHARGE TIMER (ZONE 3)

INITIAL DISCHARGE

2FP-3E	0426	FIRE PROTECTION-EXTENDED DISCHARGE TIMER (ZONE3)

EXTENDED DISCHARGE

30FH	0485	HEATER-ANNUNCIATOR

GANG ALARM TO MARK V FOR HEATER FAILURE

OPEN TO MARK VI TO ALARM

30SG-1	0415	DIAGNOSTIC IGNITION EXCITER SWITCH

NO-CEC; CLOSE TO ALARM ON EXCITER FAILURE

30WN-1		0426 WATER INJECTION VFD CONTROLLER FAULT DETECTION

NORM=(1) NC=OEC

PART OF 97WN-1, CONTACT OPENS IN EVENT OF 97WN-1 FAULT

33BQ-1	0417	BEARING SEALING AIR VALVE-LIMIT SWITCH

NORM=(2) NO-CEC;

SWITCH CONT CLOSED WITH VA14 IN 5TH STG POS.

33CB-1	0417	COMPRESSOR BLEED VALVE LIMIT SWITCH

CLOSED WITH VALVE OPEN – SPST

33CB-2	0417	COMPRESSOR BLEED VALVE LIMIT SWITCH

CLOSED WITH VALVE OPEN – SPST

33FK-1	0424 	MULTIPORT FUEL VALVE LIMIT SWITCH

CONTACT CLOSED WHEN VALVE IS CLOSED

33FK-2 	0424 	MULTIPORT FUEL VALVE LIMIT SWITCH

NORM=CLOSED; OPENS WHEN VH9-2 OPENS

33FL-1 	0424 	LIQUID FUEL STOP VALVE LIMIT SWITCH

NORM=NO-CES; CLOSED WITH VALVE CLOSED;

33FL-2 	0424 	LIQUID FUEL STOP VALVE LIMIT SWITCH

NORM=NO-CES; CLOSED WITH VALVE OPEN;

33FP-1A	0426	FIRE PROTECTION-LOCK-OUT VALVE POSITION/LIMIT SWITCH

33GC-1A	0440	FIRE DOOR LIMIT SWITCH – GENERATOR

NO-CEC SWITCH CLOSED WHEN DOOR IS FULLY OPEN

33GC-1B	0440	FIRE DOOR LIMIT SWITCH – GENERATOR

NO-CEC SWITCH CLOSED WHEN DOOR IS FULLY OPEN

33GC-1C	0440	FIRE DOOR LIMIT SWITCH – GENERATOR

NO-CEC SWITCH CLOSED WHEN DOOR IS FULLY OPEN

33GC-2	0440	FIRE DOOR LIMIT SWITCH – GENERATOR

NC-CEC SWITCH CLOSED WHEN DOOR IS OPEN

33GC-3	0440	FIRE DOOR LIMIT SWITCH – GENERATOR

NC-CEC SWITCH CLOSED WHEN DOOR IS OPEN

33PG-1 	0477 	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

PART OF VA13 VALVE.

NORM= (2) NC-OES; CLOSED WITH VALVE CLOSED

33PG-2 	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

THIS DEVICE IS SUPPLIED AS PART OF VA13 						NORM=(2) NO-CES; CLOSED WITH VALVE OPEN

33PG-3 	0477 	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

NORM=(2) NC-OES; CLOSED WITH VALVE CLOSED;

THIS DEVICE IS SUPPLIED AS PART OF VA13

33PG-4 	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

PART OF VA13 VALVE.

NORM= (2) NO-CES; CLOSED WITH VALVE OPEN

33PG-5	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

NORM=(2) NC-OES; CLOSED WITH VALVE CLOSED;

33PG-6	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

NORM=(2) NO-CES; CLOSED WITH VALVE OPEN;

33PG-7	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

NORM=(2) NC-OES; CLOSED WITH VALVE CLOSED;

33PG-8	0477	FUEL GAS SYSTEM PURGE VALVE LIMIT SWITCH

NORM=(2) NO-CES; CLOSED WITH VALVE OPEN;

SUPPLIED AS PART OF VA-13

33PL-1 	0477 	LIQUID FUEL SYSTEM PURGE VALVE LIMIT SWITCH

CLOSED WITH VALVE IN OPEN POSITION

PRIMARY OIL PURGE

33PL-2 	0477	LIQUID FUEL SYSTEM PURGE VALVE LIMIT SWITCH

CONTACT CLOSED WITH VALVE IN OPEN POSITION

SECONDARY OIL PURGE

33TH-3	0432	INLET HEATING ISOLATION VALVE LIMIT SWITCH

CONTACT CLOSED WITH VM15-1 FULL OPEN

33TM-1	0421	TORQUE ADJUSTER TORQUE SWITCH-MIN TRAVEL

PART OF TORQUE CONVERTOR

CONTACT OPENS AT LOW, LOW LIMIT

33TM-2	0421	TORQUE ADJUSTER TORQUE SWITCH-MAX TRAVEL

PART OF TORQUE CONVERTOR

CONTACT OPENS AT HIGH, HIGH LIMIT

33TM-4	0421	TORQUE ADJUSTER LIMIT SWITCH-MAX TRAVEL

CONTACT OPENS AT HIGH, HIGH LIMIT

PART OF TORQUE CONVERTOR

33TM-5	0421	TORQUE ADJUSTER LIMIT SWITCH-LOW TORQUE LIMIT

PART OF TORQUE CONVERTOR

CONTACT OPENS AT PURGE SPEED

33TM-7	0421	TORQUE ADJUSTER LIMIT SWITCH-ACCEL TORQUE

CONTACT OPENS AT HIGH LIMIT

PART OF TORQUE CONVERTOR

33TM-8	0421	TORQUE ADJUSTER LIMIT SWITCH-FIRING TORQUE

PART OF TORQUE CONVERTOR

CONTACT OPENS AT LOW LIMIT

33VG-4 	0422 	GAS FUEL VBNT VAL VB-LIMIT SWITCH

NORM=(1) NO-CEC,

SWITCH CLOSES WHEN VALVE CLOSES

33WP-1 	         0477	WATER INJECTION SYSTEM PURGE VALVE LIMIT SWITCH

CONTACT CLOSED WITH VALVE IN OPEN POSITION

34AD-1	0419	AIR DRYER

HEATLESS AIR DRYER

120 V / 60 HZ SINGLE PHASE POWER, 100W

34TF-1	0471	TURBINE INLET AIR FILTER-SELF CLEANING SEQUENCER

120V; 60/50 HZ; 15A SUPPLY REQUIRED

39FC-1	0453	VIBRATION SWITCH-COOLING WATER FAN

NORM=(2) NC-OEC;

MOTOR TRIP AND ALARM

39FC-2	0453	VIBRATION SWITCH-COOLING WATER FAN

NORM=(2) NC-OEC;

MOTOR TRIP AND ALARM

39FC-3	0453	VIBRATION SWITCH-COOLING WATER FAN

NORM=(2) NC-OEC;

MOTOR TRIP AND ALARM

39V-1A	0415	VIBRATION SENSOR TURBINE

OUTPUT AT 1 IN/SEC = 150.0 MV

LOCATED AT GAS TURBINE BEARING #1 (AIR INLET END)

39V-1B	0415	VIBRATION SENSOR TURBINE

OUTPUT AT 1 IN/SEC = 150.0 MV

LOCATED AT GAS TURBINE BEARING #1 (AIR INLET END)

39V-2A	0415	VIBRATION SENSOR TURBINE

OUTPUT AT 1 IN/SEC = 150.0 MV

LOCATED AT GAS TURBINE BEARING #2 (MIDDLE BEARING)

39V-3A	0415	VIBRATION SENSOR TURBINE

OUTPUT AT 1 IN/SEC = 150.0 MV

LOCATED AT GAS TURBINE BEARING #3 (EXHAUST END)

39V-3B	0415	VIBRATION SENSOR TURBINE

OUTPUT AT 1 IN/SEC = 150.0 MV

LOCATED AT GAS TURBINE BEARING #3 (EXHAUST END)

39V-4A	0440	VIBRATION SENSOR GENERATOR

OUTPUT AT 1 IN/SEC = 150.0 MV

39V-4B	0440	VIBRATION SENSOR GENERATOR

OUTPUT AT 1 IN/SEC = 150.0 MV

39V-5A	0440	VIBRATION SENSOR GENERATOR

OUTPUT AT 1 IN/SEC = 150.0 MV

39VS-101	0440	VIBRATION SENSOR (NON-CONT) GEN COLLECTOR END

B-N 3300 SERIES

39VS-102	0440	VIBRATION SENSOR (NON-CONT) GEN COLLECTOR END

B-N 3300 SERIES

39VS-11	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #1 (AIR INLET

END)

39VS-12	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #2 (MIDDLE

BEARING)

39VS-21	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #2 (MIDDLE

BEARING)

39VS-22	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #2 (MIDDLE

BEARING)

39VS-23	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #2 (MIDDLE

BEARING)

39VS-24	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #2 (MIDDLE

BEARING)

39VS-31	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #3 (EXHAUST

END BEARING)

39VS-32	0415	VIBRATION SENSOR (NON-CONTACTING)

OUTPUT AT 1 MIL = 200.0 MV

PROXIMITY PROBE FOR GAS TURBINE SHAFT NEAR BEARING #3 (EXHAUST

END BEARING)

39VS-91	0440	VIBRATION SENSOR (NON-CONT) GEN COUPLING END

B-N 3300 SERIES

39VS-92	0440	VIBRATION SENSOR (NON-CONT) GEN COUPLING END

B-N 3300 SERIES

43HR-1	0434	HYDRAULIC RATCHET CONTROL SWITCH

NORM=(1) NO-CES;

43MRFP-1A	0426	FIRE PROTECTION-MANUAL DISCHARGE SWITCH (ZONE 1)

CO2 RELEASE SWITCH (ZONE 1)

43MRFP-2A	0426	FIRE PROTECTION-MANUAL DISCHARGE SWITCH (ZONE 2)

CO2 RELEASE SWITCH (ZONE 2)

43MRFP-3A	0426	FIRE PROTECTION-MANUAL DISCHARGE SWITCH (ZONE 3)

CO2 RELEASE SWITCH (ZONE 3)

43WK-1	0461	WATER TEMP SETPOINT SWITCH (HOT-COLD)

43WK-2	0461	OPERATION SETPOINT SWITCH (AUTO-MANUAL)

45FA-1A	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT

INCREASING: 325.0 F OR 162.8 C

NORM=(2) NO-CEC;

45FA-1B	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT

INCREASING; 325.0 F OR 162.8 C

NORM=(2) NO-CEC;

45FA-2A	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT						INCREASING; 325.0 F OR 162.8 C

NORM=(2) NO-CEC;

45FA-2B	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT

INCREASING; 325.0 F OR 162.8 C

NORM=(2) NO-CEC;

45FA-5A	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT

INCREASING; 325.0 F OR 162.8 C

NORM=(2) NO-SPST;

45FA-5B  	0426	FIRE DETECTOR-ACCESSORY COMPARTMENT

INCREASING: 325.0 F OR 162.8 C

NORM=(1) NO-SPST;

45FGC-3A	0426	FIRE DETECTOR – GEN COLLECTOR COMPT

INCREASING: 725.0 F OR 385.0 C

NORM=(2) NO-CEC

45FGC-3B	0426	FIRE DETECTOR – GEN COLLECTOR COMPT

INCREASING: 725.0 F OR 385.0 C

NORM=(2) NO-CEC

45FLC-20A	0426	FIRE DETECTOR

INCREASING; 725.0 F OR 385.0 C

NORM=(2) NO-CEC

#3 BEARING TUNNEL

45FLC-20B	0426	FIRE DETECTOR

INCREASING; 725.0 F OR 385.0 C

NORM=(2) NO-CEC

#3 BEARING TUNNEL

45FLC-21A	0426	FIRE DETECTOR-LOAD GEAR COMPARTMENT

INCREASING; 725.0 F OR 385.0 C

NORM=(2) NO-CEC;

45FLC-21B	0426	FIRE DETECTOR-LOAD GEAR COMPARTMENT

INCREASING; 725.0 F OR 385.0 C

NORM=(2) NO-CEC;

45FT-1A	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45FT-1B	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45FT-2A	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45FT-2B	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45FT-3A	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45FT-3B	0426	FIRE DETECTOR-TURBINE COMPARTMENT

INCREASING; 600.0 F OR 315.6 C

NORM=(2) NO-CEC;

45HA-7 	0474	COMBUSTIBLE GAS DETECTOR

OFF BASE GAS COMPARTMENT

45HA-8	0474	COMBUSTIBLE GAS DETECTOR

OFF BASE GAS COMPARTMENT

45HT-1	0474	COMBUSTIBLE GAS DETECTOR-TURBINE COMPARTMENT

45HT-2	0474	COMBUSTIBLE GAS DETECTOR-TURBINE COMPARTMENT

45SCC-A	0426	SMOKE DETECTOR-PEECC

WIRED TO MARK V FOR ALARM

45SCC-B	0426	SMOKE DETECTOR-PEECC

WIRED TO MARK V FOR ALARM

45SGC-3A	0426	SMOKE DETECTOR-GENERATOR COLLECTOR COMPARTMENT

WIRED TO MARK V FOR ALARM

45SGC-3B	0426	SMOKE DETECTOR-GENERATOR COLLECTOR COMPARTMENT

WIRED TO MARK V FOR ALARM

49WS-1	0461	WATER WASH SKID HEATER OVERLOAD

(INTEGRAL PART OF 23WS-1)

4FH	0485	MASTER CONTROL RELAY-HEATER

STAGE WITH 30FH AND 52FH CONTACT CLOSURES.

DRY CONTACT CLOSES FOR HEATER START

PERMISSIVE FROM MARK V

4WW-1	0461	ON LINE WATER WASH MASTER CONTROL RELAY

52FH	0485	HEATER-MANUAL MODE CONTACT

LOCATED IN HEATER CONTROL PANEL

OPEN CONTACT INDICATES OPEN BREAKER

ISA DEVICE NAME: HS-EH

62FP-1	0426	FIRE PROTECTION-CO2 TIMER RESET SWITCH (ZONE 1)

62FP-2	0426	FIRE PROTECTION-CO2 TIMER RESET SWITCH (ZONE 2)

62FP-3	0426	FIRE PROTECTION-CO2 TIMER RESET SWITCH (ZONE 3)

63AD-1A 	0425	MAIN ATOMIZING AIR COMPRESSOR DIFF PRESSURESWITCH

DECREASING: 15.00+-1.000 PSID OR 1.055+0.0703 KG/CM2D

NORM=(2) NO-CEC;

63AD-1B                    0425 	ATOMIZING AIR COMP DIFF PRESSURE SWITCH

DECREASING: 15.00+-1.000 PSID OR 1.055+-0.0703 KG/CM2D			NORM=(2) NO-CEC;

63AD-1C 	0425 	ATOMIZING AIR COMP DIFF PRESSURE SWITCH

DECREASING: 15.00+-1.000 PSID OR 1.055+-0.0703 KG/CM2D			NORM=(2) NO-CEC;

63AD-4	0419	APU LOW PRESSURE SWITCH

DECREASING: 85.00+-5.000 PSIG OR 5.976+-0.3515 KG/CM2G

APU LOW PRESSURE ALARM INDICATES INSUFFICENT

AIR AVAILABLE FOR NORMAL DEVICE OPERATION, OPENS TO ALARM

63AF-1 	0425	ATOMIZING AIR FILTER DIFFERENTIAL PRESSURE 						SWITCH INCREASING: 3.500+-0.5000 PSID OR 0.2461 +-0.0352 KG/CM2D

NORM=(2) NC-OEC;

63BQ-1 	0440	BEARING SEALING AIR PUMP PRESSURE-ALARM

INCREASING: -1.000INH2O OR -25.40 MMH2O

(DECREASING: -1.100+-0.100INH2O OR -27.94MMH2O)

NO-CEC CONTACT OPENS ON LOSS OF VACUUM

63CA-1	0471	INLET AIR FILTER COMPRESSED AIR PRESSURE SWITCH

DECREASING: 60.00+-5.000 PSIG OR 4.218+-0.3515 KG/CM2G

NORM=(2) NO-CEC; CLOSED WHEN PRESSURIZED

63FD-1A	0424	FUEL FORWARDING HEADER PRESSURE

DECREASING: 60+-1.0 PSIG; DECR=OPEN, INCR=CLOSE

63FD-1B	0427	FUEL FORWARDING PUMP SUCTION PRESSURE

DECREASING: 1.0 PSIG +-0.25 PSIG; DECR=OPEN, INCR=CLOSE

63FD-3	0427	LIQUID FUEL PRESSURE NORMAL (AT METERING SPOOL)

DECREASING: 35+-1.0PSIG; DECR=OPEN, INCR=CLOSE

63FGD-1 	0422	FUEL GAS STRAINER DP SWITCH

INCREASING: 00+-1.000 PSID OR 1.055+-0.0703 KG/CM2D

(DECREASING 13.75+-1.250 PSID OR 0.9667+-00879 KG/CM2D)				NORM=(1) NC-OEC; SPDT;

63FL-2 	0424 	LIQUID FUEL PRESSURE SWITCH

DECREASING: 30.00+-2.000 PSIG OR 2.109+-0.1406 KG/CM2

NORM=(2) NO-CEC;

FOR PROTECTION OF MAIN 	FUEL PUMP

63FP-1 	0426 	PRESSURE SW-C02

DECREASING: 275.0+-5.000 PSIG OR 19.33+-0.3515 KG/CM2G

(INCREASING: 325.0+-5.000 PSIG OR 22.85+-0.3515 KG/CM2G)

ABNORMAL PRESSURE ALARM SWITCH

63HF-1	0434	HYDRAULIC OIL FILTER DIFF PRESSURE ALARM

INCREASING: 60.00+-3.000 PSID OR 4.218+-0.2109 KG/CM2D

(DECREASING: 57.50+-2.000 PSID OR 4.043+-0.1406 KG/CM2D)

NORM=(1) NC-OEC;

63HG-1	0418	HYDRAULIC OIL TRIP PRESSURE SW GAS STOP VALVE

DECREASING: 20.00+-1.000 PSIG OR 1.406+-0.0703 KG/CM2G

(INCREASING: 20.60+-0.5000 PSIG OR 1.448+-0.0352 KG/CM2G)

NORM=NO-CEC;

63HG-2	0418	HYDRAULIC OIL TRIP PRESSURE SW GAS STOP VALVE

DECREASING: 20.00+-1.000 PSIG OR 1.406+-0.0703 KG/CM2G

(INCREASING: 20.60+-0.5000 PSIG OR 1.448+-0.0352 KG/CM2G)

NORM=NO-CEC;

63HG-3	0418	HYDRAULIC OIL TRIP PRESSURE SW GAS STOP VALVE

DECREASING: 20.00+-1.000 PSIG OR 1.406+-0.0703 KG/CM2G

(INCREASING: 20.60+-0.5000 PSIG OR 1.448+-0.0352 KG/CM2G)

NORM=NO-CEC;

63HL-1 	0418 	 HYDRAULIC OIL TRIP CIRCUIT PRESSURE-LIQUID FUEL SYS					DECREASING: 20.00+-1.000 PSIG OR 1.406+-0.0703 KG/CM2G				(INCREASING 20.60+-0.5000 PSIG OR 1.448+-0.0352 KG/CM2G) 				NORM=NO-CEC;

63HL-2 	0418	 HYDRAULIC OIL TRIP CIRCUIT PRESSURE-LIQUID FUEL 					SYS DECREASING: 20.00+-1.000 PSIG OR 1.406+-						0.0703 KG/CM2G (INCREASING 20.60+-0.5000 PSIG 						OR 1.448+-00352 KG/CM2G) NORM=NO-CEC;

63HL-3 		0418	HYDRAULIC OIL TRIP CIRCUIT PRESSURE-LIQUID FUEL SYS

DECREASING: 20.00+-1.000 PSIG OR 1.406+-0.0703 KG/CM2G

(INCREASING 20.60+-0.5000 PSIG OR 1.448+-0.0352 KG/CM2G)

NORM=NO-CEC;

63HQ-1 	0434	LOW HYDRAULIC OIL SUPPLY PRESS-ALARM

DECREASING: 1350+-15.00 PSIG OR 94.91+-1.055 KG/CM2G

(INCREASING 1375+-10.00 PSIG OR 	96.67+-0.7031 KG/CM2G)

NORM=(1) NO-CEC;

63HR-1	0421	HYDRAULIC RATCHET FORWARD STROKE PRESSURE SWITCH

INCREASING: 108.0+-93.00 PSIG OR 7.593+-6.539 KG/CM2G

(DECREASING: 98.00+-93.00 PSIG OR 6.890+-6.539 KG/CM2G)

PART OF TORQUE CONVERTOR (362A1855P001)

CUSTOM CONTROLS UL/CSA DIV1

MODEL 6900PE32

CONTACTS OPEN ON INCREASING PRESSURE AND CLOSE ON

DECREASING PRESSURE

63HR-2	0421	HYDRAULIC RATCHET PRESSURE SWITCH RETURN STROKE

INCREASING: 108.0+-93.00 PSIG OR 7.593+-6.539 KG/CM2G

(DECREASING: 98.00+-93.00 PSIG OR 6.890+-6.539 KG/CM2G)

CUSTOM CONTROLS UL/CSA DIV1

MODEL NUMBER 6900PE32

PART OF TORQUE CONVERTOR (362A1855P001)

CONTACTS OPEN ON INCREASING PRESSURE AND CLOSE ON

DECREASING PRESSURE

63LF-1	 0424	LIQUID FUEL OIL FILTER-DIFF PRESSURE

INCREASING: 15.00+-1.000 PSID OR 1.055+-0.0703 KG/CM2D			NORM=NC-CEC;

63LF-2	0427	DUPLEX STRAINER DIFF PRESS SWITCH

INCREASING: 5.0+-0.5PSID; DECR: 4.0+-0.5PSID

63LF-8	0424	LIQ. FUEL DIFF. PRESS SWITCH

INCREASING: 25.00+-1.000 PSID OR 1.758+-0.0703 KG/CM2D

NORM=NC-CEC;

DIFFERENTIAL PRESSURE ACROSS LIQUID FUEL PUMP CONICAL STRAINER

63LF-9 	0424 	LIQ. FUEL DIFF. PRESS SWITCH

INCREASING: 25.00+-1.000 PSID OR 1.758+-0.0703 KG/CM2D

NORM=NC-	CEC;

DIFFERENTIAL PRESSURE ACROSS FLOW DIVIDER CONICAL STRAINER

63PG-1 	0477 	FUEL GAS SYSTEM PURGE PRESSURE SWITCH

INCREASING: 50.00+-1.000 PSIG OR 3.515+-0.0703KG/CM2G

(DECREASING 46.00+-3000 PSIG OR 3.234+-0.2109 KG/CM2G)

PRIMARY GAS FUEL 	SYSTEM

63PG-2	0422	GAS FUEL SYSTEM PURGE PRESSURE SWITCH

INCREASING: 50.00+-1.000 PSIG OR 3.515+-0.0703 KG/CM2G

(DECREASING: 46.00+-3.000 PSIG OR 3.234+-0.2109 KG/CM2G)

NORM=(2) NO-CEC;

TRANSFER GAS FUEL SYSTEM

63QA-1  	0416  	LOW LUBE OIL PRESSURE-AUX PUMP START

DECREASING: 70.00+-1.000 PSIG OR 4.921 +-0.0703 KG/CM2G

(INCREASING: 71.80+-1.200 PSIG OR  5.048+-0.0844 KG/CM2G)

NORM=(1) NO-CEC;

SECONDARY SETTING MUST BE GREATER THAN PRIMARY

63QQ-1  	0416 	MAIN LUBE OIL FILTER DIFFERENTIAL PRESSURE-ALARM

INCREASING: 15.00+-1.000 PSID OR 1.055+-	0.0703 KG/CM2D

(DECREASING 14.40+-0.4000 PSID OR 1.012+-00281 KG/CM2D)

NORM=(1) NC-OEC;

SECONDARY SETTING MUST BE LESS THAN PRIMARY

63QT-2A	0440	LOW LUBE OIL PRESSURE-TRIP LOAD

DECREASING: 8.000+-0.3000 PSIG OR 0.5625+-0.0211 KG/CM2G

(INCREASING: 9.000+-0.5000 PSIG OR 0.6328+-0.0352 KG/CM2G)

(2) NO-CEC CONTACTS OPEN ON LOW OIL PRESS

63QT-2B	0440	LOW LUBE OIL PRESSURE-TRIP LOAD

DECREASING: 8.000+-0.3000 PSIG OR 0.5625+-0.0211 KG/CM2G

(INCREASING: 9.000+-0.5000 PSIG OR 0.6328+-0.0352 KG/CM2G)

(2) NO-CEC CONTACTS OPEN ON LOW OIL PRESS

63QV-1	0416	LUBE OIL TANK AIR PRESSURE SWITCH

DECREASING: -5.000 INH2O OR -127.0 MMH2O

NORM=(1) NO-CEC;

63TF-1	0471	TURBINE INLET AIR FILTER-EXCESSSIVE PRESSURE DROP ALARM

INCREASING: 6.000+-0.2500 INH2O OR 152.4+-6.350 MMH2O

NORM=(2) NC-OES;

63TF-2A	0471	TURBINE INLET AIR FILTER-EXCESSIVE PRESSURE DROP

INCREASING: 8.000+-0.2500 INH2O OR 203.2+-6.350 MMH2O

NORM=(2) NC-OEC;

63TF-2B	0471	TURBINE INLET AIR FILTER-EXCESSIVE PRESSURE DROP

INCREASING: 8.000+-0.2500 INH2O OR 203.2+-6.350 MMH2O

NORM=(2) NC-OEC;

63TK-1	0417	TURBINE SHELL & EXHAUST FRAME BLOWER DSCH PRESSURE SW

DECREASING: 25.00+-0.8000 INH2O OR 635.0+-20.32 MMH2O

(INCREASING: 28.00 INH2O OR 711.2 MMH2O)

NORM=(2) NO-CEC;

63TK-2	0417	TURBINE SHELL & EXHAUST FRAME BLOWER DSCH PRESURE SW

DECREASING: 25.00+-0.8000 INH2O OR 635.0+-20.32 MMH20

(INCREASING: 28.00 INH2 OR 711.2 MMH2O)

NORM=(2) NO-CEC;

63TW-1	0461	TURBINE/COMPRESSOR WASH WATER PRESSURE

DECREASING: 98.0+-2.000 PSIG OR 6.890+-0.1406 KG/CM2G

NORM=(2) NO-CEC;

63TW-2	0461	TURBINE/COMPRESSOR WASH WATER PRESSURE-PUMP TRIP

INCREASING: 4.000 INHG OR 101.6 MMHG

OR 0.138 KG/CM2

OPENS ON INCREASING VACUUM 4 INHGV (DEC PRESS)

CLOSED AT ATMOSPHERIC PRESSURE

NORM=NC-OEC;

63VL-3	0422	GAS VALVE COMPT DIFFERENTIAL PRESSURE SWITCH

DECREASING: 0.2000+-0.0500 INH2O OR 5.080+-1.270 MMH2O

(INCREASING: 0.4000+-0.0500 INH2O OR 10.16+-1.270 MMH2O)

63VL-4	0422	GAS VALVE COMPT VENT FAN DIFF PRESSURE SWITCH

DECREASING: 0.2000+-0.0500 INH2O OR 5.080+-1.270 MMH2O

(INCREASING: 0.4000+-0.0500 INH2O OR 10.16+-1.270 MMH2O)

63VL-5	0422	GAS VALVE COMPT VENT FAN DIFF PRESSURE SWITCH

DECREASING: 0.2000+-0.0500 INH2O OR 5.080+-1.270 MMH2O

(INCREASING: 0.4000+-0.0500 INH2O OR 10.16+-1.270 MMH2O)

63WC-1	0453	LOW COOLING WATER PRESSURE

DECREASING: 38.00+-1.000 PSIG OR 2.672+-0.0703 KG/CM2G

ALARM & AUX PUMP START

NORM=NO-CEC;

63WN-1	0462	WATER INJECTION PRESSURE

DECREASING: 9.00+-1.00 PSIA OR 9.00+-1.00PSIA

(INCREASING: 10.00+-1.00 PSIA OR 10.00 +- 1.00 PSIA)

NORM=(1) NO-CEC; OPENS ON DECR ABS INLET PRESURE

MANUAL DEVICE SETTING REQUIRED

63WN-3	0462	WATER INJECTION DIFFERENTIAL PRESSURE

INCREASING: 15.00+-1.00 PSID OR 15.00 +- 1.00 PSID

(DECREASING: 13.50+-1.00 PSID OR 13.50+-1.00PSID)

NORM=(1) NC-OEC; OPENS ON INCR FW-1 PRESSURE DIFFERENTIAL

65EP-3	0432	ELECTRO-PNEUMATIC TRANSDUCER

POSITIONER INPUT: 4.0MA FOR VA20-1 FULL CLOSED

20.0MA FOR VA20-1 FULL OPEN

65FP-1 	0424 	LIQUID FUEL PUMP (BYPASS VALVE) SERVO VALVE

65GC-1	0422	GAS CONTROL VALVE SERVO VALVE

RATED FLOW: 2.500 GPM AT 1000 PSID

65GC-2	0422	GAS CONTROL VALVE SERVO VALVE

RATED FLOW: 1.000 GPM AT 1000 PSID

65GC-3	0422	GAS CONTROL VALVE SERVO VALVE

RATED FLOW: 2.500 GPM AT 1000 PSID

71GS-1	0484	HIGH GAS SCRUBBER LEVEL

125VDC

SPDT

0.5 AMP CONTINUOUS SERVICE

OPEN CONTACT TO ALARM MARK V

71GS-2A	0484	HIGH GAS SCRUBBER LEVEL TRIP

125VDC

SPDT

0.5 AMP CONTINUOUS SERVICE

OPEN CONTACT TO TRIP MARK V

ISA DEVICE NAME: LSHH 2A

71GS-2B	0484	HIGH GAS LEV

125VDC

0.5 AMP CONTINUOUS SERVICE

SPDT

OPEN CONTACT TO TRIP MARK V

ISA DEVICE NAME: LSHH 2B

71GS-2C	0484	HIGH GAS SCRUBBER LEVEL TRIP

125VDC

SPDT

0.5 AMP CONTINUOUS SERVICE

OPEN CONTACT TO TRIP MARK V

ISA DEVICE NAME: LSHH-2C

71QH-1   	0416 	HIGH LUBE OIL LEVEL-ALARM

NORM=(1) NC-OEC;

71 QL-1  	 0416  	LOW LUBE OIL LEVEL-ALARM

NORM=(1) NO-CEC;

71TW-1	0461	WATER TANK WATER LEVEL CONTROL

NORM=(2) NC-OEC;

DECREASING: 15+-1 IN H20 OR 0.0381+-0.0025 KG/CM2

MAGNETIC LEVEL SWITCH SET 15 INCHES ABOVE THE BOTTOM OF

THE WATER TANK

71WG-1	0440	HIGH WATER (LIQUID) LEVEL IN GENERATOR

NC CONTACT OPENS ON HIGH LIQUID LEVEL IN GEN

71WL-1	0453	LOW COOLING WATER LEVEL SWITCH

NORM=(2) NO-CEC;

77FD-1	0424	Flow Divider Mag Speed PICKUP

GAP: 0.0090+-0.0010 IN or 0.2286+-0.0254 MM

77FD-2	0424	Flow Divider Mag Speed PICKUP

GAP: 0.0090+-0.0010 IN or 0.2286+-0.0254 MM

77FD-3	0424	FLOW DIVIDER MAG SPEED PICKUP

GAP: 0.0090+-0.0010 IN or 0.2286+-0.0254 MM

77HT-1	0415	HIGH PRESSURE SET MAGNETIC PICKUP (OVERSPEED)

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MM

77HT-2	0415	HIGH PRESSURE SET MAGNETIC PICKUP (OVERSPEED)

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MM

77HT-3	0415	HIGH PRESSURE SET MAGNETIC PICKUP (OVERSPEED)

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MM

77NH-1	0415	HIGH PRESSURE SET MAGNETIC PICKUP-SPEED

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MMH2O

77NH-2	0415	HIGH PRESSURE SET MAGNETIC PICKUP-SPEED

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MMH2O

77NH-3	0415	HIGH PRESSURE SET MAGNETIC PICKUP-SPEED

GAP: 0.0500+-0.0050 IN OR 1.270+-0.1270 MMH2O

77RP-11	0415	SHAFT ANGULAR POSITION INDICATOR (KEYPHASOR) BEARING#1

80FP-1	0426	FIRE PROTECTION-INITIAL DISCH PRESSURE SWITCH (ZONE 1)

MANUAL RESET (ZONE 1)

80FP-2	0426	FIRE PROTECTION-INITIAL DISCH PRESSURE SWITCH (ZONE 2)

MANUAL RESET (ZONE 2)

80FP-3	0426	FIRE PROTECTION-INITIAL DISCH PRESSURE SWITCH (ZONE 3)

MANUAL RESET (ZONE 3)

80WW-1	0461	FLOW SWITCH-WATER WASH SKID

CONTACT OPENS AT 2 GPM OR 0.45M3/HR ON INCR FLOW

NORM=NC-OEC;

WATER WASH FLOW EXISTS RELAY TO TURBINE CONTROL SYSTEM AND

CONTROL SIGNAL NAME IS L80WWN. WIRE TO MARK V/MARK VI

86WWX	0461	WATER WASH SKID TRIP ALARM RELAY

88AB-1 	0425 	STARTING ATOMIZING AIR COMPRESSOR MOTOR

30.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88AD-1 	0419 	FAN MOTOR, APU HEAT EXCHANGER

0.5000 HP; 1725 RPM; 120 VAC; I PH; 60 HZ;

COOLS APU HEAT EXCHANGER MOTOR RATING

88BQ-1	0440	BEARING DRAIN ENLARGEMENT EXHAUSTER

1.5 HP; 3600 RPM; 460/480 VAC; 1PHASE; 60HZ

88BT-1	0436	COOLING AIR FAN MOTOR-TURBINE COMPARTMENT

15.00 HP; 1200 RPM; 460 VAC; 3 PH; 60 HZ;

88CR-1	0421	STARTING MOTOR

800.0 HP; 3600 RPM; 2300/4160 VAC; 3 PH; 60 HZ;

88FC-1	0453	COOLING WATER FAN MOTOR

25.00 HP; 1800 RPM; 460 VAC; 3 PH; 60 HZ;

88FC-2	0453	COOLING WATER FAN MOTOR

25.00 HP; 1800 RPM; 460 VAC; 3 PH; 60 HZ;

88FC-3	0453	COOLING WATER FAN MOTOR

25.00 HP; 1800 RPM; 460 VAC; 3 PH; 60 HZ;

88HA-1	0436 	ACCESSORY COMPT SPACE HEATER BLOWER MOTOR (PT OF 23HA-1)

0.2500 HP; 1725 RPM; 460 VAC; 3 PH; 60 HZ;

88HA-2 	0436 	ACCESSORY COMPT SPACE HEATER BLOWER MOTOR (PT OF 23HA-2)

0.2500 HP; 1725 RPM; 460 VAC; 3 PH; 60 HZ;

88HQ-1	0434	HYDRAULIC SUPPLY PUMP MOTOR

20.00 HP; 1750 RPM; 460 VAC; 3 PH; 60 HZ;

88JS-1	0462	WATER INJECTION SKID COOLING AIR FAN MOTOR

0.5HP; 1800 RPM; 120VAC; 1 PH; 60HZ

88FD-1	0427	LIQUID FUEL FORWARDING PUMP #1 MOTOR

25HP; 3600RMP; 480VAC; 3 PH; 60 Hertz

88FD-2	0427	LIQUID FUEL FORWARDING PUMP #2 MOTOR

25HP; 3600 RPM; 480VAC; 3 PH; 60 Hertz

88HT-1 	0436 	TURBINE COMPARTMENT SPACE HTR BLOWER MOTOR (PT OF 23HT-1)

0.5000 HP; 1725 RPM; 460 VAC; 3 PH; 60 HZ;

88HT-2	0436 	TURBINE COMPARTMENT SPACE HTR BLOWER MOTOR (PT OF 23HT-2)

0.5000 HP; 1725 RPM; 460 VAC; 3 PH; 60 HZ;

88QA-1	0416	AUXILIARY LUBE OIL PUMP MOTOR

60.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88QE-1	0416	EMERGENCY LUBE OIL PUMP MOTOR

7.500 HP; 1750 RPM; 120 VDC;

88QV-1A 	0416 	LUBE MIST SEPARATOR OR ELIMINATOR MOTOR

10.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88RC-1A	0426	FIRE PROTECTION-C02 REFRIGERATION COMPRESSOR MOTOR

1.500 HP; 1750 RPM; 480 VAC; 3 PH; 60 HZ;

TOLLERANCE ON ELECTRICAL OPERATING RANGE (+-10%)

88TK-1	0417	TURBINE SHELL & EXHAUST FRAME BLOWER MOTOR

60.00 HP; 3600 RPM; 480 VAC; 3 PH; 60 HZ;

88TK-2	0417	TURBINE SHELL & EXHAUST FRAME BLOWER MOTOR

60.00 HP; 3600 RPM; 480 VAC; 3 PH; 60 HZ;

88TM-1	0421	TORQUE/SPEED ADJUSTER DRIVE MOTOR

0.3900 HP; 1800 RPM; 480 VAC; 3 PH; 60 HZ;

PART OF TORQUE CONVERTOR

88TW-1	0461	TURBINE/COMPRESSOR WASH WATER PUMP MOTOR

15.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88VL-1	0422	GAS VALVE COMPT VENT FAN MOTOR

3.000 HP; 3600 RPM; 480 VAC; 3 PH; 60 HZ;

88VL-2	0422	GAS VALVE COMPT VENT FAN MOTOR

3.000 HP; 3600 RPM; 480 VAC; 3 PH; 60 HZ;

88VW-1	0461	WATER WASH UNIT VENT FAN MOTOR

0.5000 HP; 1725 RPM; 120 VAC; 1 PH; 60 HZ;

88WC-1	0453	COOLING WATER PUMP #1 MOTOR

75.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88WC-2	0453	COOLING WATR PUMP #2 MOTOR

75.00 HP; 3600 RPM; 460 VAC; 3 PH; 60 HZ;

88WN-1	0462	WATER INJECTION PUMP MOTOR

60.00HP; 3600 RPM; 480VAC; 3PH; 60HZ

PART OF PW1-1 PUMP ASSY

MANUAL DEVICE SETTINGS REQUIRED

88WS-1	0461	WATER WASH SKID SPACE HEATER BLOWER MOTOR

0.1000 HP; 1550 RPM; 208 VAC; 1 PH; 60 HZ;

(POWER FROM ON-SKID TRANSFORMER)

90SR-1	0422	STOP/SPEED RATIO VALVE SERVO VALVE

RATED FLOW: 10.00 GPM AT 1000 PSID

90TV-1	0469	INLET GUIDE VANE SERVO VALVE

RATED FLOW: 5.0 GPM AT 1000 PSIG

95FP-1	0440	GENERATOR AIR GAP FLUX PROBE

95SG-1	0415	IGNITION EXCITER FOR 95SP-1

115 V OR 230 V, 50/60 HZ, MAX 150 VA INPUT

DUTY: 1.5 MIN ON / 1.5 MIN OFF / 1.5 MIN ON / 25 MIN OFF

95SG-10	0415	IGNITION EXCIER FOR 95SP-10

115 V OR 230 V, 50/60 HZ, MAX 150 VA INPUT

DUTY: 1.5 MIN ON / 1.5 MIN OFF / 1.5 MIN ON / 25 MIN OFF

95SP-1	0415	COMBUSTION CHAMBEER SPARK PLUG

95SP-10	0415	COMBUSTION CHAMBER SPARK PLUG

96AP-1A 	0492	BAROMETRIC PRESSURE TRANSMITTER

4.000+-0.2000 MA=22.00 INHG OR 558.8 MMHG

20.00+-0.2000 MA=37.00 INHG OR 939.8 MMHG

96AP-1B	0492	BAROMETRIC PRESSURE TRANSMITTER

4.000+-0.2000 MA=22.00 INHG OR 558.8 MMHG

20.00+-0.2000 MA=37.00 INHG OR 939.8 MMHG

96AP-1C	0492	BAROMETRIC PRESSURE TRANSMITTER

4.000+-0.2000 MA=22.00 INHG OR 558.8 MMHG

20.00+-0.2000 MA=37.00 INHG OR 939.8 MMHG

96BD-1	0492	COMPRESSOR BELLMOUTH DIFFERENTIAL

PRESSURE TRANSMITTER

4.000 MA=0.0 INH2O OR 0.0 MMH2O

20.00 MA=138.5 INH2O OR 3518 MMH2O

96BH-1	0432	INLET HTG CV UPSTREAM PRESSURE TRANSMITTER

4.000+-0.2000 MA=0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 250.0 PSIG OR 17.58 KG/CM2G

96BH-2	0432	INLET HTG CV DOWNSTREAM PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 150.0 PSIG OR 10.55 KG/CM2G

96CD-1	0417`	COMPRESSOR DISCH PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 300.0 PSIG OR 21.09 KG/CM2G

96CD-1B	0417	COMPRESSOR DISCH PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 300.0 PSIG OR 21.09 KG/CM2G

96CD-1C	0417	COMPRESSOR DISCH PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 300.0 PSIG OR 21.09 KG/CM2G

96CS-1	0492	INLET AIR TOTAL PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 INH2O OR 0.0 MMH2O

20.00+-0.2000 MA= 11.10 INH2O OR 281.9 MH2O

96EP-1	0492	EXHAUST PRESSURE TRANSMITTER

4.000 MA= 0.0 INH2O OR 0.0 MMH2O

20.00 MA=27.70 INH2O OR 703.6 MMH2O

96FG-1 	0422 	GAS FUEL UPSTREAM PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 600.0 PSIG OR 42.18 KG/CM2G

96FG-2A	0422	INTERSTAGE FUEL GAS PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 400.0 PSIG OR 28.12 KG/CM2G

96FG-2B	0422	INTERSTAGE FUEL GAS PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 400.0 PSIG OR 28.12 KG/CM2G

96FG-2C	0422	INTERSTAGE FUEL GAS PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 400.0 PSIG OR 28.12 KG/CM2G

96FG-4	0422	FUEL GAS CONTROL VALVE OUTLET PRESSURE TRANSMITTER

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 400.0 PSIG OR 28.12 KG/CM2G

PRIMARY

96FG-5	0422	SECONDARY FUEL GAS CONTROL VALVE OUTLET PRESSURE XMTR

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA= 400.0 PSIG OR 28.12 KG/CM2G

96FG-6	0422	TRANSFER FUEL GAS CONTROL VALVE OUTLET PRESSURE XMTR

4.000+-0.2000 MA= 0.0 PSIG OR 0.0 KG/CM2G

20.00+-0.2000 MA=400.0 PSIG OR 28.12 KG/CM2G

96FM-1	0422	MULTIVARIABLE TRANSMITTER

4.000 MA= 0.0 PPS OR 0.0 KG/SEC

20.00 MA= 30.00 PPS OR 13.61 KG/SEC

MULTIVARIABLE FLOW TRANSMITTER – RTD REQUIRED BUT NOT

WIRED TO THE CONTROL SYSTEM DIRECTLY

96GC-1	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.8 VAC

96GC-2	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.8 VAC

96GC-3	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.1 VAC

96GC-4	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.1 VAC

96GC-5	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.8 VAC

96GC-6	0422	FUEL GAS CONTROL VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.8 VAC

96PLP-1 	0477 	PRIMARY LIQUID FUEL PURGE PRESSURE  TRANSMITTER                                         		4.000+-0.2000 MA= -20.00 PSID OR -1.406 KG/CM2D					20.00+-0.2000 MA= 120.0 PSID OR 8.437 KG/CM2D						 REPLACEMENT FOR 63PLP-I PRESS SW FORMERLY SET 					PSID ALARM, 2 PSID TRIP REFERENCED TO PCD.

96PLS-1 	0477 	SECONDARY LIQUID FUEL PURGE PRESSURE 	TRANSMITTER					4.000+-0.2000 MA= -20.00 PSID OR -1.406 KG/CM2D					20.00+-0.2000 MA= 120.0 PSID OR 8.437 KG/CM2D					        	REPLACEMENT FOR 63PLS-I PRESS SW FORMERL Y SET					5 PSID ALARM, 2 PSID TRIP REFERENCED TO PCD.

96PWP-1               	0477 	PRIMARY WATER PURGE PRESSURE TRANSMITTER

4.000+-0.2000 MA= -20.00 PSID OR -1.406 KG/CM2D				20.00+-0.2000 MA= 120.0 PSID OR 8.437 KG/CM2D 					REPLACEMENT FOR 63PWP-I PRESS SW FORMERLY SET				5 PSID ALARM, 2 PSID TRIP 	REFERENCED TO PCD.

NOTE: SER YES THE PRI+SEC       COMBINED CIRCUIT					PRIMARY AS WELL AS SECONDARY

96SR-1	0422	STOP/SPEED RATIO VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.1 VAC

96SR-2	0422	STOP/SPEED RATIO VALVE LVDT

0% STROKE = 0.7 VAC

100% STROKE = 2.1 VAC

96TD-1	0471	DEWPOINT SENSOR

4.000+-0.5000 MA= -49.00 F OR -45.00 C

20.00+-0.5000 MA= 167.0 F OR 75.00 C

96 TH-1	0432	INLET HEATING CONTROL VALVE POSITION TRANSMITTER

4.000+-0.2000 MA= 0.0 % OR 0.0 %

20.00+-0.2000 MA= 100.0 % OR 100.0 %

96TV-1	0469	INLET GUIDE VANE LVDT

96TV-2	0469	INLET GUIDE VANE LVDT

96WF-1	0462	WATER INJECTION FLOW

4-20ma   0.1 – 18.06 lbs/sec

96WF-2	0462	WATER INJECTION FLOW

4-20ma   0.1 – 18.06 lbs/sec

96WF-3	0462	Water Injection Flow

4-20ma   0.1 – 18.06 lbs/sec

96WN-4	0462	WATER INJECTION MOTOR SPEED

(+-)10vdc  0 – 3600 RPM

96WP-1	0462	WATER INJECTION SKID PRESSURE TRANSMITTER

4-20ma   0 – 800 psi

97WN-1	0462	WATER INJECTION SKID VARIABLE FREQUENCY CONTROLLER

4-20ma    0 – 100%

96VC-11	0415	SHAFT AXIAL POSN TRANSMITTER BEARING #1

96VC-12	0415	SHAFT AXIAL POSN TRANSMITTER BEARING #1

ACV1-1	0469	IGV HYDRAULIC CYLINDER ACTUATOR

AATI-1A      	0425   	ATOMIZING AIR COMPRESSOR INLET TEMP

AATI-1B     	0425  	ATOMIZING AIR COMPRESSOR INLET TEMP

AH1-1	0434	HYDRAULIC OIL ACCUMULATOR

PRECHARGE: 750 PSIG DRY NITROGEN

AL-15	0440	AC LIGHT-GENERATOR COMPARTMENT

120 VAC, 60 HZ

AL-26	0471	120 VA,C 60 HZ

AL-33	0440	AC LIGHT-GENERATOR COMPARTMENT

AL-59	0462	AC LIGHT SWITCH- WATER INJECTION SKID

AL-62	0461	AC LIGHT-WATER WASH SKID

AL-63	0461	AC LIGHT-WATER WASH SKID

AL-81	0461	AC LIGHT-WATER WASH SKID

AL-82	0462	AC LIGHT SWITCH- WATER INJECTION SKID

AL-87	0422	AC LIGHT-GAS FUEL MODULE

AL-88	0422	AC LIGHT-GAS FUEL MODULE

AR-17	0440	AC RECEPTACLE-GENERATOR COMPARTMENT

AR20	0471	AC RECEPTACLE- INLET FILTER COMPARTMENT

120 VAC

AR-41	0462	AC RECEPTACLE- WATER INJECTION SKID

AR-42	0462	AC RECEPTACLE- WATER INJECTION SKID

AR-50	0461	AC RECEPTACLE-WATER WASH SKID

ASW-10	0471	AC LIGHT SWITCH-INLET AIR COMPARTMENT

120VAC, 60 HZ

ASW-31	0461	AC LIGHT SWITCH-WATER WASH SKID

ASW-43	0422	AC LIGHT SWITCH-GAS FUEL MODULE

ASW-44	0422	AC LIGHT SWITCH-GAS FUEL MODULE

AT-ID-1	0471	AMBIENT TEMPERATURE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

AT-ID-2	0471	AMBIENT TEMPERATURE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

AT-ID-3	0471	AMBIENT TEMPERATURE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-GJ1-1A	0440	BEARING METAL TEMP-GENERATOR BEARING #1

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ1-1B	0440	BEARING METAL TEMP-GENERATOR BEARING #1

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ1-2A	0440	BEARING METAL TEMP-GENERATOR BEARING #1

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ1-2B	0440	BEARING METAL TEMP-GENERATOR BEARING #1

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ2-1A	0440	BEARING METAL TEMP-GENERATOR BEARING #2

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ2-1B 	0440 	BEARING METAL TEMP-GENERATOR BEARING #2

TYPE K – CHROMEL/ALUMEL THERMOCOUPE

BT-GJ2-2A	0440	BEARING METAL TEMP-GENERATOR BEARING #2

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-GJ2-2B	0440	BEARING METAL TEMP-GENERATOR BEARING #2

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

BT-J1-1A	0415	BEARLING METAL TEMP-TURBINE BEARING #1

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J1-1B	0415	BEARLING METAL TEMP-TURBINE BEARING #1

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J1-2A	0415	BEARLING METAL TEMP-TURBINE BEARING #1

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J1-2B	0415	BEARLING METAL TEMP-TURBINE BEARING #1

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J2-1A	0415	BEARLING METAL TEMP-TURBINE BEARING #2

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J2-1B	0415	BEARLING METAL TEMP-TURBINE BEARING #2

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J2-2A	0415	BEARLING METAL TEMP-TURBINE BEARING #2

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J2-2B	0415	BEARLING METAL TEMP-TURBINE BEARING #2

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J3-1A	0415	BEARLING METAL TEMP-TURBINE BEARING #3

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J3-1B	0415	BEARLING METAL TEMP-TURBINE BEARING #3

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J3-2A	0415	BEARLING METAL TEMP-TURBINE BEARING #3

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-J3-2B	0415	BEARLING METAL TEMP-TURBINE BEARING #3

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TA1-1A	0415	BEARLING METAL TEMP-THRUST ACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TA1-1B	0415	BEARLING METAL TEMP-THRUST ACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TA1-2A	0415	BEARLING METAL TEMP-THRUST ACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TA1-2B	0415	BEARLING METAL TEMP-THRUST ACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TI1-1A	0415	BEARING METAL TEMP-THRUST INACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TI1-1B	0415	BEARING METAL TEMP-THRUST INACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TI1-2A	0415	BEARING METAL TEMP-THRUST INACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

BT-TI1-2B	0415	BEARING METAL TEMP-THRUST INACTIVE

TYPE K THERMOCOUPLE

2 ELEMENTS; UNGROUNDED;

CA1-1  	0425   	MAIN ATOMIZING AIR COMPRESSOR

CA2-1   	0425  	BOOSTER ATOMIZING AIR COMPRESSOR

CT-DA-1	0415	COMPRESSOR DISCHARGE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-DA-2	0415	COMPRESSOR DISCHARGE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-DA-3	0415	COMPRESSOR TEMP-DISCHARGE ANNULUS

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-IF-1A	0415	COMPRESSOR TEMPERATURE-INLET FLANGE (DTC)

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-IF-1B	0415	COMPRESSOR TEMPERATURE-INLET FLANGE (DTC)

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-IF-2A	0415	COMPRESSOR TEMPERATURE-INLET FLANGE (DTC)

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-IF-2B	0415	COMPRESSOR TEMPERATURE-INLET FLANGE (DTC)

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED

CT-IF-3/R	0415	COMPRESSOR TEMP-INLET FLANGE-RTD

DCL-15	0440	GENERAATOR LIGHTING-125VDC

DCL-33	0440	GENERATOR LIGHTING-125VDC

DL-51	0422	DC LIGHT-GAS FUEL MODULE

DT-GGC-10	0440	GENERATOR TEMP-COLD GAS COUPLING END

100 OHM PLATINUM RTD

DT-GGC-11	0440	GENERATOR TEMP-COLD GAS COLLECTOR END

100 OHM PLATINUM RTD

DT-GGH-18	0440	GENERATOR TEMP-HOT GAS COUPLILNG END

100 OHM PLATINUM RTD

DT-GGH-19	0440	GENERATOR TEMP-HOT GAS COLLECTOR END

100 OHM PLATINUM RTD

DT-GSA-4 	0440 	GENERATOR TEMP-STATOR COLLECTOR END

100 OHM PLATINUM RTD

SLOT RTD

DT-GSA-5 	0440 	GENERATOR TEMP-STATOR COLLECTOR END

100 OHM PLATINUM RTD

SLOT RTD

DT-GSA-6 	0440 	GENERATOR TEMP-STATOR COLLECTOR END

100 OHM PLATINUM RTD

SLOT RTD

DT-GSF-I 	0440 	GENERATOR TEMP-STATOR COUPLING END

100 OHM PLATINUM RTD

SLOT RTD

DT-GSF-2 	0440 	GENERATOR TEMP-STATOR COUPLING END

100 OHM PLATINUM RTD

SLOT RTD

DT-GSF-3 	0440 	GENERATOR TEMP-STATOR COUPLING END

100 OHM PLATINUM RTD

SLOT RTD

ET-CRS-1/R 	0421	STARTING MOTOR STATOR TEMP

PART OF ELECTRIC START MOTOR

PLATINUM RTD: 100 OHM

ET-CRS-2/R 	0421	STARTING MOTOR STATOR TEMP

PART OF ELECTRIC START MOTOR

PLATINUM RTD: 100 OHM

ET-CRS-3/R	0421	STARTING MOTOR STATOR TEMP

PART OF ELECTRIC START MOTOR

100 OHM PLATINUM RTD

ET-CRS-4/R	0421	STARTING MOTOR STATOR TEMP

PART OF ELECTRIC START MOTOR

COPPER: 10 OHM

ET-CRS-5/R	0421	STARTING MOTOR STATOR TEMP

PART OF ELECTRIC START MOTOR

COPPER: 10 OHM

ET-CRS-6/R	0421	STARTING MOTOR STATOR TEMP

10 OHM COPPER RTD

PART OF ELECTRIC START MOTOR

FA4-1 	0425 	ATOMIZING AIR CONTROL FILTER

FA5-1 	0425 	MAIN ATOMIZING AIR FILTER

FA6-1	0417	COMPRESSOR BLEED FILTER

FDl-1 	0424 	FLOW DIVIDER

FF1-1	0424 	PRIMARY(LOW PRESS) FUEL FILTER

FILTRATION: I MICRON NOMINAL

FF1-2	0424 	PRIMARY(LOW PRESS) FUEL FILTER

FILTRATION: I MICRON NOMINAL

FH2-1	0434	HYDRAULIC OIL SUPPLY FILTER

FILTRATION: 0.5 MICRON

3 MICRON ABSOLUTE

FH2-2	0434	HYDRAULIC OIL SUPPLY FILTER

FILTRATION: 0.5 MICRON

3 MICRON ABSOLUTE

FH3-1 	0424 	HYDRAULIC OIL SUPPLY FILTER-LIQUID FUEL SERVO

FILTRATION: 40 MICRON

FH4-2 	0424 		HYDRAULIC OIL SUPPLY FILTER-NOZZLE ISOLATION 								VALVE FILTRATION: 0.5 MICRON

FH6-1	0469	IGV SERVO HYDRAULIC OIL SUPPLY FILTER

FILTRATION: 15 MICRON

FH7-1	0422	FUEL GAS SERVO HYDRAULIC OIL SUPPLY FILTER

FILTRATION: 15 MICRON ABSOLUTE

FH8-1	0422	GAS FUEL SERVO HYDRAULIC SUPPLY FILTER

FILTRATION: 15 MICRON ABSOLUTE

FH8-2	0422	GAS FUEL SERVO HYDRAULIC SUPPLY FILTER

FILTRATION: 15 MICRON ABSOLUTE

FH8-3	0422	GAS FUEL SERVO HYDRAULIC SUPPLY FILTER

FILTRATION: 15 MICRON ABSOLUTE

FM1-1	0462	WATER INJECTION FLOW METER

FM4-1	0427	LIQUID FUEL FLOW 50-550 GPM

FT-GC-1	0422	FUEL GAS TEMPERATURE SENSOR

TYPE K THERMOCOUPLE

FT-GC-2	0422	FUEL GAS TEMPERATURE SENSOR

TYPE K THERMOCOUPLE

FT-GC-3	0422	FUEL GAS TEMPERATURE SENSOR

TYPE K THERMOCOUPLE

FT-GI-1C	0485	FUEL GAS TEMPERATURE SENSOR

TYPE K THERMOCOUPLE

UNGROUNDED;

ISA DEVICE NAME: TE-2

FT-GI-1D	0485	HEATER-INLET THERMOCOUPLE

TYPE K THERMOCOUPLE

UNGROUNDED;

INPUT TO DIFF TEMP CONTROLLER

ISA DEVICE NAME: TE-1

FT-MG-1/R	0422	RTD FOR GAS FUEL MULTIVARIABLE FLOW TRANSMITTER

100 OHM PLATINUM (DIN 43760) RTD

1 ELEMENT; GROUNDED;

DEVICE IS NOT WIRED TO THE SPEED TRONIC CONTROL PANEL, BUT IS

WIRED DIRECTLY TO 96FM-1

FW1-1 /FW2-2	0462	DUPLEX FILTER W/TRANSFER VALVE

WATER INJECTION SYSTEM

HM1-1	0421	TORQUE CONVERTER

HM2-1	0421	HYDRAULIC RATCHET MECHANISM

MOUNTED ON TORQUE CONVERTER

HX1-1  	0425 	ATOMIZING AIR PRE-COOLER

HX4-1	0477 	PURGE AIR HEAT EXCHANGER

LIQUID FUEL PURGE COOLER. 275F (NOM) AIR

LC-GS	0484	LEVEL CONTROLLER GAS SCRUBBER

NO ELECTRICAL CONTACTS

ACTUATED BY GAS PRESSURE IN SCRUBBER

AUTOMATIC DUMP TO DRAINS TANK

LT-B1D-A	0416	LUBE OIL THERMOCOUPLE #1 BEARING DRAIN

LT-B1D-B	0416	LUBE OIL THERMOCOUPLE #1 BEARING DRAIN

LT-B2D-A	0416	LUBE OIL THERMOCOUPLE #2 BEARING DRAIN

LT-B2D-B	0416	LUBE OIL THERMOCOUPLE #2 BEARING DRAIN

LT-B3D-A	0416	LUBE OIL THERMOCOUPLE #3 BEARING DRAIN

LT-B3D-B	0416	LUBE OIL THERMOCOUPLE #3 BEARING DRAIN

LT-G1D-1A	0440	LUBE SYSTEM TEMP-GENERATOR #1 BEARING DRAIN

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

LT-G1D-1B	0440	LUBE SYSTEM TEMP-GENERATOR #1 BEARING DRAIN

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

LT-G2D-1A	0440	LUBE SYSTEM TEMP-GENERATOR #2 BEARING DRAIN

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

LT-G2D-1B	0440	LUBE SYSTEM TEMP-GENERATOR #2 BEARING DRAIN

TYPE K – CHROMEL/ALUMEL THERMOCOUPLE

LT-TH-1A	0416	LUBE OIL THERMOCOUPLE TURBINE HEADER

LT-TH-1B	0416	LUBE OIL THERMOCOUPLE TURBINE HEADER

MG1-1	042	GAS FUEL NOZZLE - PM1

MG1-2	0422	GAS FUEL NOZZLE – PM2

MG1-3	0422	GAS FUEL NOZZLE - TRANSFER

MG2-1	0422	GAS FUEL METER TUBE/ORIFICE

PF1-1 	0424 	MAIN LIQUID FUEL PUMP

PH1-1	0434	MAIN HYDDRAULIC OIL SUPPLY PUMP

RATED FLOW: 13.2 GPM AT 1500 PSIG (1422 RPM)

PH2-1	0434 	AUXILIARY HYDRAULIC OIL SUPPLY PUMP

RATED FLOW: 16.5 GPM AT 1500 PSIG (1750 RPM)

PW1-1	0462	WATER INJECTION PUMP

SLA-1A	0426	FIRE ALARM STROBE & HORN (ACCESSORY COMPT)

100DB @ 10FT./300 CANDELA/24 VDC

INTERIOR- ACCESSORY COMPT. (ZONE 1)

CLASS 1, GROUP D, DIV 2 APPROVED

SLA-1B	0426	FIRE ALARM STROBE & HORN (ACCESSORY COMPT)

100 DB @ 10FT./300 CANDELA/24 VDC

INTERIOR- ACCESSORY COMPT. (ZONE 1)

CLASS 1, GROUP D, DIV 2 APPROVED

SLA-1C	0426	FIRE ALARM STROBE & HORN (ACCESSORY COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 1

WEATHERPROOF DEVICE

SLA-1D	0426	FIRE ALARM STROBE & HORN (ACCESSORY COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 1

WEATHERPROOF DEVICE

SLGC-3A	0426	FIRE ALARM STROBE 7 HORN (GEN COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 3

WEATHERPROOF DEVICE

SLGC-3B	0426	FIRE ALARM STROBE & HORN (GEN COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 3

WEATHERPROOF DEVICE

SLLC-2A	0426	FIRE ALARM STROBE 7 HORN (LOAD COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 2

WEATHERPROOF DEVICE

SLLC-2B	0426	FIRE ALARM STROBE & HORN (LOAD COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 2

WEATHERPROOF DEVICE

SLT-1A	0426	FIRE ALARM STROBE & HORN (TURBINE COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 1

WEATHERPROOF DEVICE

SLT-1B	0426	FIRE ALARM STROBE & HORN (TURBINE COMPT)

96 DB @ 10FT./15 MINUMUM CANDELA/24 VDC

EXTERIOR-ZONE 1

WEATHERPROOF DEVICE

TT-IB-1	0415	TURBINE TEMP-INNER BARREL

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-IB-2	0415	TURBINE TEMP-INNER BARREL

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-IB-3	0415	TURBINE TEMP-INNER BARREL

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS1AO-1	0415	TURBINE TEMPERATURE-WHEELSPACE 1ST STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS1AO-2	0415	TURBINE TEMPERATURE-WHEELSPACE 1ST STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS1FI-1	0415	TURBINE TEMPERATURE-WHEELSPACE 1ST STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS1FI-2	0415	TURBINE TEMPERATURE-WHEELSPACE 1ST STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS2AO-1	0415	TURBINE TEMPERATURE-WHEELSPACE 2ND STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS2AO-2	0415	TURBINE TEMPERATURE-WHEELSPACE 2ND STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS2FO-1	0415	TURBINE TEMPERATURE-WHEELSPACE 2ND STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS2FO-2	0415	TURBINE TEMPERATURE-WHEELSPACE 2ND STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS3AO-1	0415	TURBINE TEMPERATURE-WHEELSPACE 3RD STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS3AO-2	0415	TURBINE TEMPERATURE-WHEELSPACE 3RD STG AFT OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS3FO-1	0415	TURBINE TEMPERATURE-WHEELSPACE 3RD STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-WS3FO-2	0415	TURBINE TEMPERATURE-WHEELSPACE 3RD STGFWD OUTER

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-1	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-10	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-11	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-12	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-13	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-14	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-15	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-16	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-17	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-18	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-2	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-3	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-4	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-5	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-6	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-7	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-8	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

TT-XD-9	0415	EXHAUST TEMPERATURE THERMOCOUPLE

TYPE K THERMOCOUPLE

1 ELEMENT; UNGROUNDED;

VA13-1 	0477	FUEL GAS SYSTEM PURGE VALVE

PRIMARY GAS FUEL SYSTEM PURGE NORMALLY CLOSED

VA13-2 	0477   	FUEL GAS SYSTEM PURGE VALVE PRIMARY GAS 						FUEL SYSTEM PURGE-NORMALLY CLOSED

VA13-3	0477	FUEL GAS SYSTEM PURGE VALVE

TRANSFER GAS FUEL SYSTEM PURGE-NORMALLY OPEN

VA13-4	047	FUEL GAS SYSTEM PURGE VALVE

TRANSFER GAS FUEL PURGE VALVE NORMALLY OPEN

VA13-8 	0477 	FUEL GAS SYSTEM PURGE VENT VALVE

AIR ACTUATED PRIMARY GAS PURGE, NORM=OPEN

VA13-16	0477	FUEL GAS SYSTEM PURGE VENT VALVE

NORM=CLOSED

VA14-1	0417	BEARING SEALING AIR VALVE

NORM=BOTTOM (11TH STAGE) TO COMMON BEARINGS

OPEN: TOP (5TH STAGE) CLOSED

VA17-1 		0424 		FALSE START DRAIN VALVE-COMBUSTION WRAPPER

VA1 7-2 	0424  	FALSE START DRAIN VALVE-EXHAUST FRAME

VA17-5 	0424 	DRAIN VALVE EXHAUST PLENUM NORM=OPEN;

VA18-1 	0425  	ATOMIZING AIR COMPRESSOR BYPASS AIR OPERATED VALVE				NORM=OPEN

VA19-1 	0477 	LIQUID FUEL NOZZLE PURGE VALVE

PRIMARY LIQ  FUEL SYSTEM PURGE-NORMALLY CLOSED

NORM=C TO A OPEN TO DRAIN; B CLOSED; PRESSURE AT B 					ACTUATES=B TO C OPEN; A CLOSED

VA1 9-2 	0477  	LIQUID FUEL NOZZLE PURGE VALVE

SECONDARY FUEL SYSTEM PURGE-NORMALL Y CLOSED

NORM=C TO A OPEN TO DRAIN; B CLOSED; PRESSURE AT B

ACTUATES=B TO C OPEN; A CLOSED

VA19-3-1T1O 	0477  	LIQUID FUEL PURGE ISOLATION VALVES

SET 0.5000+-0.5000 PSID OR 0.0352+-0.0352 KG/CM2D

PRIMARY LIQUID FUEL 3 WAY VALVE

VAI9-4-1T1O    	0477    	LIQUID FUEL PURGE ISOLATION VALVES

SET 0.5000+-0.5000 PSID OR 0.0352+-0.0352 KG/CM2D 					SECONDARY LIQUID FUEL 3 WAY VALVE

VA22-1    	0425 	STARTING ATOMIZING AIR COMPRESSOR 							ISOLATION VALVE NORM=OPEN

VA23-1   	0477 	LIQUID PURGE PRESSURE RATIO CONTROL VALVE

PNEUMATIC; NORMALLY= OPEN

SYSTEM BY-PASS ORIFICE CONTROL (WHEN ACTUATED)

FOR OIL AND WATER PURGE

VA23-2    	0477 	LIQUID PURGE PRESSURE RATIO CONTROL GLOBE VALVE BYPASS				PNEUMATIC; NORMALL Y= OPEN

SYSTEM BY-PASS ORIFICE CONTROL (WHEN ACTUATED)					FOR OIL AND WATER PURGE

VA33-1                     	0477 	WATER INJECTION PURGE VALVE WATER

INJECTION (PRI + SEC) PURGE-NORMALLY CLOSED

NORM=C TO A OPEN TO DRAIN; B CLOSED; PRESSURE AT B

ACTUATES=B TO C OPEN; A CLOSED

VA36-1      	0477 	FUEL GAS SYSTEM PURGE VALVE ACTUATOR QUICK EXH VALVE

PRIMARY VALVE EXHAUST. ORIFICE NEEDLE

CONTROL VALVE IN SUPPLY PORT

VA36-2    	0477 	FUEL GAS SYSTEM PURGE VALVE ACTUATOR QUICK EXH VALVE

PRIMARY VALVE EXHAUST. ORIFICE NEEDLE

CONTROL VALVE IN SUPPLY PORT

VA42-1  	0432 	INLET BLEED HEAT QUICK EXHAUSTER VALVE

VA2-1	0417	COMPRESSOR BLEED VALVE

NORM=OPEN;

VA2-2	0417	COMPRESSOR BLEED VALVE

NORM=OPEN;

VA20-1	0432	INLET HEATING CONTROL VALVE

8.00 INCH ANSI FLANGE CONNECTION

LINEAR TRIM CHARACTERISTIC

2.00 INCH STROKE

VA36-3	0477	FUEL GAS SYSTEM PURGE VALVE ACTUATOR QUICK EXH VALVE

TRANSFER VALVE EXHAUST ORIFICE NEEDLE

CONTROL IN VENT PORT

VA36-4	0477	FUEL GAS SYSTEM PURGE VALVE ACTUATOR QUICK EXH VALVE

TRANSFER VALVE EXHAUST ORIFICE NEEDLE

CONTROL IN VENT PORT

VA40-1	0432	INLET HEATING CONTROL VALVE VOLUME BOOSTER

VAB1-1	0434	HYDRAULIC OIL SYSTEM AIR BLEED VALVE (MAIN)

VAB2-1	0434	HYDRAULIC OIL SYSTEM AIR BLEED VALVE (AUX)

VAD-2	0419	AIR PROCESSING UNIT DRAIN VALVE

PNUEMATICALLY OPERATED DRAIN VALVE.

CONTROLLED BY A FLOAT SWITCH

VC2-1	0421	HYDRAULIC RATCHET INLET FLOW CONTROL VALVE

4.0 GPM AT 1500 PSIG

VCK3-1	0434	HYDRAULIC OIL PUMP CHECK VALVE

VC3-1 	0424 	LIQUID FUEL PUMP BYPASS CONTROL VALVE

STROKE= 1.25" (PLUG TRAVEL)

SLEW = 2.7 SECONDS (0,5 GPM SERVO)

VCK2-11T20 	0477 	LIQUID FUEL NOZZLE PURGE CHECK VALVE SET 						0.5000+-0.5000 PSID OR 0.0352+-0.0352 KG/CM2D 						WATER INJECTION PURGE, TO PRIMARY

VCK2-1TIO 	0477 	LIQUID FUEL NOZZLE PURGE CHECK VALVE

SET 0.5000+-0.5000 PSID OR 0.0352+-0.0352 KG/CM2D					WATER INJECTION PURGE, TO SECONDARY

VCK2-21T30	0477		Water Injection Purge Check Valves

Set 0.50+-0.50 PSID OR 0.50 +-0.50 PSID

Water Injection Purge TO PRIMARY

VCK2-31T40	0477		Water Injection Purge Check Valves

Set 0.50+-0.500 PSID OR 0.50 +-0.50 PSID

Water Injection Purge TO SECONDARY

VCK3-2	0434	HYDRAULIC OIL PUMP CHECK VALVE

VCK7-1	0417	TURBINE SHELL & EXHAUST FRAME BLOWER CHECK VALVE

VCK7-2	0417	TURBINE SHELL & EXHAUST FRAME BLOWER CHECK VALVE

VCK80-1	0477 	PURGE CONTROL AIR CHECK VALVE

SET 10.00+-2.500 PSIG OR 0.7031 +-0.1758 KG/CM2G					CONTROL AIR FROM PA1 CONNECTION

VCK80-2 	0477 	PURGE CONTROL AIR CHECK VALVE

SET 10,00+-2.500 PSIG OR 0,7031 +-0.1758 KG/CM2G					ALTERNATE CONTROL AIR FROM PG35

VCK8-1T20	0462	WATER INJECTION CHECK VALVE

15 PSID (1.035 BARD) CRACKING PRESSURE

50 PSID (3.448 BARD) AT 16 GPM (1.000LPS)

VGC-1	0422	FUEL GAS CONTROL VALVE

1.125 IN. MAXIMUM STROKE

VGC-2	0422	FUEL GAS CONTROL VALVE

0.75 IN. MAXIMUM STROKE

VGC-3	0422	FUEL GAS CONTROL VALVE

1.125 IN. MAXIMUM STROKE

VH3-1	0469	INLET GUIDE VANE DUMP VALVE

VH4-1 	0424 	LIQUID FUEL STOP VALVE HYDRAULIC TRIP VALVE

VH5-1	0422	GAS FUEL DUMP VALVE-STOP/SPEED RATIO VALVE

VH5-2	0422	GAS FUEL DUMP VALVE-CONTROL VALVE

VH5-3	0422	GAS FUEL DUMP VALVE-CONTROL VALVE

VH5-4	0422	GAS FUEL DUMP VALVE-CONTROL VALVE

VH9-2 	0424 	LIQIUD FUEL SYSTEM NOZZLE ISOLENOID VALVE, SECONDARY

VM15-1	0432	INLET HEATING ISOLATION VALVE

8.00 INCH ANSI FLANGE CONNECTION

MANUAL BUTTERFLY VALVE

VM4-1	0434	HYDRAULIC OIL FILTER TRANSFER VALVE

VM5-1 	0424 	FUEL FILTER TRANSFER VALVE

VPR2-1	0416	LUBE OIL HEADER PRESSURE REGULATOR VALVE

SET 26.00+-1.000 PSIG OR 1.828+-0.0703 KG/CM2G

VPR3-1	0434	COMPENSATOR-HYDRAULIC OIL SUPPLY PUMP (IN PUMP)

SET 1510+-10.00 PSIG OR 106.2+-0.7031 KG/CM2G

VPR3-2	0434	COMPENSATOR-HYDRAULIC OIL SUPPLY AUX PUMP

SET 1510+-10.00 PSIG OR 106.2+-0.7031 KG/CM2G

VPR41-1	0432	TURBINE IAH CONTROL VALVE I/P INST AIR PRESSURE REG

SET 45.00+-2.000 PSIG OR 3.164+-0.1406 KG/CM2G

VPR41-2 	0432 	INLET HEATING ISOLATION VALVE PRESSURE REG

SET 80.00+-2.000 PSIG OR 5.625+-0.1406 KG/CM2G

VPR53-1	0427	LIQUID FUEL SUPPLY PRESSURE REGULATOR  VALVE

SET 65.00+-2.0 PSIG OR 4.83+-0.14 BARG

VPR53-2 	0424 	ISOLATION VALVE HYDRAULIC OIL PRESSURE REG VALVE 						SET 100.0+-5.000 PSIG OR 7.031 +-0.3515 KG/CM2G							INLET 1200 TO 1500 PSIG

OUTLET ADJUSTABLE SET: 75 TO 150 PSIG

VPR54-1 	0477 	PURGE CONTROL VALVE AIR PRESSURE REGULATOR

SET 90.00+-5.000 PSIG OR 6.328+-0.3515 KG/CM2G

REGULATOR FOR LIQUID PURGE VALVES AND ORIFICE BY

PASS VALVES

VPR54-2	0477	PURGE CONTROL VALVE AIR PRESSURE REGULATOR

SET 90.00+-5.000 PSIG OR 6.328+-0.3515 KG/CM2G

PRESSURE REGULATOR FOR VA13 GAS PURGE (2) AND

20VG PURGE VENT (1) VALVES

VPR67-1	0419	AIR FILTER BLOWDOWN REGULATOR VALVE

SET 100.0+-4.000 PSIG OR 7.031+-0.2812 KG/CM2G

VPR68-1 	0425 	PRESSURE REGULATOR-STARTING AA CPRSR ISOLATION VALVE

SET 65.00+-5.000 PSIG OR 4.570+-0.3515 KG/CM2G

VQE1-1	0462		QUICK EXHAUST VALVE, WATER INJ STOP VALVE

PART OF VS2-1 STOP VALVE ASSEMBLY

VR1-1	0416	MAIN LUBE OIL PUMP PRESSURE RELIEF VALVE

SET 101.0+-1.000 PSIG OR 7.101+-0.0703 KG/CM2G

VR14	0484	GAS SCRUBBER RELIEF VALVE

SET 600.0+-15.00 PSIG OR 42.18+-1.055 KG/CM2G

THERMAL RELIEF VALVE

VR14-1	0419	APU PRESSURE RELIEF VALVE

SET 150.0+-1.000 PSIG OR 10.55+-0.0703 KG/CM2G

DRYER TOWER RELIEF VALVE

VR14-2 	0419 	APU PRESSURE RELIEF VALVE

SET 150.0+-1.000 PSIG OR 10.55+-0.0703 KG/CM2G

DRYER TOWER RELIEF VALVE

VR14-7	0485	RELIEF VALVE-FUEL GAS

SET 600.0+-18.00 PSIG OR 42.18+-1.266 KG/CM2G

THERMAL RELIEF VALVE

VR21-1	0434	MAIN HYDRAULIC OIL SUPPLY PUMP PRESSURE RELIEF VALVE

SET 1700+-20.00 PSIG OR 119.5+-1.406 KG/CM2G

VR22-1	0434	AUXILIARY HYDRAULIC OIL SUPPLY PUMP PRESSURE RELIEF VALVE

SET 1700+-20.00 PSIG OR 119.5+-1.406 KG/CM2G

VR4-1 	0424 	MAIN FUEL PUMP PRESSURE RELIEF VALVE

SET 1200+-25.00 PSIG OR 84.37+-1.758 KG/CM2G

VR64-6 	0420 	HEAT EXCHANGER - ATOMIZING AIR

SET 150.0+-5.000 PSIG OR 10.55+-0.3515 KG/CM2G

VR70-1		0462	H2O INJECTION STOP VALVE ACTUATION PRESS RELIEF VALVE

SET 120.0 +- 5.00 PSIG

VR70-3		0462	H2O INJECTION FILTER PRESSURE RELIEF VALVE

INCREASING: 750.0 +- 25.0 PSIG

VSI-I	 0424 	LIQUID FUEL STOP VALVE

VS2-1	0462		WATER INJECTION STOP VALVE

OPEN WHEN 20WN-1 ENERGIZED

VSR-1	0422	STOP/SPEED RATIO VALVE

90 DEGREES ROTATION MAX STROKE

VTR1-1	0420	LUBE OIL HEADER TEMP REGULATOR VALVE

SET 130.0+-8.000 F OR 54.44+-4.444 C

VTR2-1 	0420 	ATOMIZING AIR PRECOOLER AIR DISCH TEMP RGLTR VALVE

SET 225.0+-8.000 F OR 107.2+-4.444C