Questions from GTG and Auxiliary Specifications for Conversion to Dual Fuel System of GE 7EA’s

Section 1.1- General

Replacement of 17th stage compressor blades:

- EDC - Need clarification of scope; supply of new stator blades, labor, equipment (crane), tools, technical direction.

Technical Services for Installation and Commissioning:

- EDC - Need clarification of scope;  complete turbine installation and commissioning or only for the modification scope of work

Section 1.3.1- Liquid Fuel System

Scope of Fuel System:

- EDC – Need to clarify scope:

  - Design, supply, and erection  of fuel treatment systems

  - Design, supply, and erection of fuel tanks

  - Clarification – Main fuel pump will be driven by the accessory gear

  - Liquid fuel system to be designed for a maximum flow rate of 150 gpm.

Section 1.5 – Fuels and Auxiliaries

- EDC - Need technical details on original cooling water system associated with each unit to evaluate the additional heat rejection.

Section 1.5.1 – Water Injection (NOx Control)

- EDC – Is there existing demineralized water available on site or adjacent to the site? If not a demineralized water system will be required including storage tank(s).

- See attached demineralized water specifications

- Clarification: demineralized system to be designed for a maximum flow rate of 85 gpm

Section 1.8 – Spare Parts

- Clarification - a complete list of spare parts will be provided based on equipment supplied.

Section 1.10 – Control System Functions

- Clarification – Plan to modify existing GE control system for dual fuel capabilities. Will need documentation from existing equipment to confirm scope and cost.

- Clarification – transferring from liquid to gas fuel has some restrictions based on load, DLN mode, and other control parameters.

Other Information Requests:

- Need technical documentation and drawings for all turbine generators and auxiliary equipment.

- The fuel gas system was mentioned briefly. Is there any need to supply fuel gas handling or treatment systems?

- What is the expected date to begin construction for installation of the units and the anticipated COD date?