April 5, 2010

COPOELEC

Electricidad de Caracas

Project: Dual Fuel Conversion for Margarita Island

Attention:

Below are some clarifications and recommendations based on the meeting between ProEnergy / Derwick and EDC on March 26th.

Clarifications:

ProEnergy confirmed their proposed scope of work includes modification to the turbine and turbine accessories to provide the unit with the capability to operate on dual fuel (natural gas and No 2 diesel). This scope of work includes all “on base” components, piping, wiring, conduit, and labor to install. The piping and interconnecting conduit and wiring between the turbine and accessory base is also included in ProEnergy’s work scope. The “off base” skids associated with the modification that are provided by ProEnergy, include one skid per unit for the following: water injection, liquid fuel forwarding, and demineralized water forwarding skids. The piping, conduit, and cable to and from these skids and electrical breakers to energize this equipment will not be provided by ProEnergy. However some of the technical details required to specify this equipment will be provided by ProEnergy.

ProEnergy will also require some technical details from EDC in order to properly size and specify some equipment associated with this modification.  However, the Turbine Operations and Maintenance, and Parts Manuals are required prior to the start of any detailed work on the modification.

The ProEnergy Workscope does not include any equipment to process, store, treat, or transfer water or fuel.

This work scope will be provided and performed on the gas turbine generators to be installed at Plant Juan Bautista Arismedndi, Issla de Margarita. The turbine serial numbers for this plant are 298034 and 298035.

Discussions:

- Primary and Secondary Fuel Nozzles

ProEnergy prefer to remove the primary and secondary fuel nozzles from the units in storage. This will allow modifications of the fuel nozzles to begin quickly and will help to shorten the cycle for the unit modification.

ProEnergy can mobilize to the equipment storage location on May 3rd to remove fuel nozzles from the two 7EA gas turbines. It is expected to take approximately 3 days per unit. The flexible piping to the fuel nozzles will be removed and boxed to be shipped separately with the unit, the primary and secondary nozzles will be removed and boxed for shipment to

ProEnergy, and blind flanges / covers will be attached to the open flanges and combustion cans.

ProEnergy will utilize a fork truck with a boom extension to remove and pack the fuel nozzles. The flexible hoses will be removed by hand and packed in plywood boxes.

ProEnergy will require access to the turbine compartment on both sides of the

unit.  Approximately twenty feet around each side of the turbine compartment

will be required to gain access with the fork truck.

ProEnergy will provide all tools to remove and pack the fuel nozzles.

- Equipment Spare Parts for Operations and Maintenance

ProEnergy will develop and supply a list of spare parts for the two units at Margarita Island and the two units at La Risa. In order to provide unit specific parts, the turbine parts manuals will need to be transmitted to ProEnergy for review.

- Water Injection System

The volume of piping between the water injection skid and the turbine should not exceed the equivalent of 100 feet of 3” schedule 40 pipe.

General specifications for the water injection skid:

- Inlet pressure: 65 psi

- Inlet and outlet flow: 0-115 GPM

- Outlet pressure: 0-500 PSIG

Water Injection Flow Control: Variable Frequency Drive with flow meter feedback on the water injection skid.

The gas turbine can be operated on liquid fuel without water injection. However the control system software will need to be modified to some degree for the unit to operate properly and not cause damage to the unit.

There are no documented cases for units not operating on liquid fuel without water injection, therefore there is no operational data for NOX output without water injection.

The flow rate for water injection for NOx control varies per load. The water injection for NOx control is initiated at approximately 30 Megawatt load (actual set point is based on parameters and calculations from the control system) and increased with load. The flow rate at base load varies and is dependent on many factors. The water injection rate at base load is expected to be between 80-90 gallons per minute with the system maximum flow rate of 115 GPM.

- Technical Services for Installation and Commissioning

Technical direction for assembly of the dual fuel modification will be supplied with the equipment. Technical direction for commissioning and start-up of the equipment will be supplied at time and material rates.

- Points of Contact

The following are points of contact for ProEnergy Services

- Technical and Project Execution:  Tom Koontz

  - E-mail: tkoontz@proenergyservices.com

  - Phone: 660-829-5100 (in USA) or 0424-173-0470

- Commercial:  Joaquin Mavares

  - E-mail: jmavares@proenergyservices.com

  - Phone: 71-392-1790

- Country Manager:  Brett Bettinger

  - Email: bbettinger@proenergyservices.com

  - Phone:  58-212-793-8172

- Lead Time for Dual Fuel Modification

The lead time to procure equipment and manufacture components for the dual fuel system is approximately 15 weeks.

Recommendations and Follow up:

- Turbine Control System

The existing Mark V Control System associated with the 7EA units is obsolete; not supported by the original manufacturer. This means that the availability of new control boards and the ability to burn EE Proms is a major concern. It is recommended that the Mark V Control System be upgraded to a Mark VI or equivalent Control System.

A Mark VI Control System or equivalent will take approximately 4 months to procure. The cost of this system would be $ 2,700,000.  This cost includes control systems for two units, 4 HMI’s (one in each turbine PECC and one in the control room), shipping, installation, and documentation. The new control systems can be implemented during the normal installation and commissioning schedule.

- Compressor Work Scope and Technical Information Letters

ProEnergy can perform inspection and repair work scopes on the turbine compressor. The technical details and scope of work associated with the compressor will be derived from unit specific TIL’s (Technical Information Letters) from the Original Equipment Manufacturer. ProEnergy can also provide any other technical interpretation and execution of work associated with other TIL’s applicable to each specific unit.

References:

- Specification:  Gas Turbine Generator and Accessories Specification for Conversion to Dual Fuel System of GE 7EA Rev 0, issued by CORPOELEC for Project C-599 on 11/09/09.

- ProEnergy Proposal No. 409-2956, 7EA Dual Fuel Modification, issued on 7-Dec-09.