GE Frame 7EA DLN1.0 Fuel Nozzle Conversion

Secondary Nozzles

Gas Only – Duel Fuel

Prepared by

ProEnergy Turbine Services

10/19/2010

Table of Content

- Process Outline

- Current Status

- Conversion Photos

1)Process Outline:

- Disassemble outer sheath from nozzle body

- Disassemble Gas Tube from nozzle body

- Disassemble Blank liquid core from nozzle body

- Mechanically clean all details

- Caustic clean all details

- Aqueous clean all details

- Perform visual and dimensional inspection of all details

- FPI all details

- Remove flame scanner port form housing

- Machine nozzle housing to remove passage plugs

- Machine housing to install passage sleeve port

- Aqueous clean housing

- Weld install Liquid and Water inlet pipes

- Final machine passage sleeve port

- Aqueous clean housing

- Braze install passage sleeve

- Pressure test housing

- FPI housing

- Assemble Liquid nozzle to housing

- Flow test and calibrate liquid circuit

- Assemble gas tube to housing

- Flow test and calibrate water circuit

- Assemble outer sheath to housing

- Flow test and calibrate secondary gas and tertiary gas circuits

- Tablock retaining bolts

- Weld tablocks to retaining bolts

- FPI tablock welds

- Perform final Gas circuit flow tests

- Perform final liquid and water flow tests

- Perform final visual and dimensional inspection

2) Current Status:

All nozzles have been processed through step 30.

3) Conversion Photos:

Final Assembly