June 17, 2010

Change order cost.

The following is the scope for all the changes occurred in the Guarenas Power Plant.

EDC - Guarenas

CO #1

Scope Changes Narrative

Status Date: 17 June 2010

General

The major scope change components are:

- Additional LM 6000 GTG installation.

- Additional liquid fuel treatment, storage, and containment facilities.

- Additional water treatment and storage facilities.

- Space allocation only for 2 additional gas compressors.

The plant arrangement included in the TSD for the original 3 GTGs scope is dimensioned as being 232 ft by 555 ft = 128,760 sq ft.  The developed property areas, including roads, to allow for the additional facilities included in CO #1 result in an increase in the total developed property area of approximately 75% to 80%!

Additional LM6000 GTG Installation

The major components of this change are:

- A 2nd LM6000 and all ancillary facilities were added.

- A 3rd GSU of the same capacity of the previous 2 GSUs was added.

- The substation and tie-in was extensively expanded.

Additional Liquid Fuel Treatment, Storage, and Containment Facilities

The major components of this change are:

- Extensive liquid fuel unloading facilities were added.

- Liquid fuel treatment facilities were expanded.

- A liquid fuel unloading shed was added.

- The liquid fuel treatment shed was expanded.

- The raw liquid fuel storage tank increased in capacity from 500,000 gallons to 750,000 gallons.

- The treated liquid fuel storage tank increased in capacity from 200,000 gallons to 300,000 gallons.

- The liquid fuel containment facilities total capacity increased from 700,000 gallons to 1,050,000 gallons – an increase of 50%!

Additional Water Treatment and Storage Facilities

The major components of this change are:

- Water treatment facilities were expanded.

- The water treatment building was expanded.

- The raw/fire water storage tank capacity increased from 250,000 gallons to 1,000,000 gallons – an increase of 300%!

- The demineralized water storage tank increased from a single 21,000 gallons fiberglass tank to a 250,000 gallons stainless steel field erected tank – an increase of 1100%!

Price

Cost Estimate for Adding a LM6000PC			$ 6,771,900	BsF 24,577,909

Cost Estimate for additional Liquid Fuel Treatment 		$ 3,493,890 	BsF 9,617,907

Cost Estimate for Add'l Water Treatment 			$ 1,796,780	BsF 5,790,000

Cost Estimate for adding gas compressors e installation	$ 8,319,600	BsF 22,577,909

Cost Estimate for add'l HV					$ 2,660,000	 BsF 2,560,700

TOTAL					$23,042,170	BsF 65,124,425

This Price includes the Freight of the extra unit as well as the BOP.

The nationalization and custom cost are not included.