Section 4.0	Design Basis and Interconnect Points

- 4.1      Design Conditions

Design Conditions

Site Elevation (Meters above Mean Sea Level) 1500 ft Design Temperature 74 F Design relative humidity: 75% Predominant wind direction: Northwest Maximum average multiannual wind velocity: 80 mph Seismic Zone 4 Liquid Fuel Supply by Owner’s Pipeline Liquid Fuel Consumption Rate (2) LM6000 96.6 gpm Liquid Fuel Consumption Rate (2) Fr. 7FA’s 419.4 gpm High Voltage Interconnect @ GSU Bushings 13.8 KV /230KV & 18KV/230KV Instrument Air System 600 scfm by Contractor Demin Water required 548 gpm Demin Water Storage 1,320,000 gallons s.s. Raw Water Storage (Includes Fire water) existing 1,000,000 gallons Evap Water Storage 300,000 Gallons R.O. Water Storage 76,000 gallons Raw Diesel Fuel Storage 2,000,000 gallons Clean Diesel Fuel Storage 1,000,000 gallons

4.2	Interconnect Points

Interconnect Points

Liquid Fuel Pipeline At Plant Boundary by Owner Plant Waste Water At waste water tank discharge pump Plant Waste Oil At waste oil tank discharge pump 230 KV Connection to 230KV Dead end towers by owner Raw Water Supply Contractor to build 500 meter water line to Ceauta Creek and install pumps for 1000 gpm

THIS DOCUMENT IS CONFIDENTIAL. IT IS DESIGNED AND INTENDED FOR PDVSA’S USE. THIS DOCUMENT IS FOR THE SOLE PURPOSE OF EVALUATING DERWICK EPC SERVICES’ PROPOSAL FOR THE GE LM6000 / Fr. 7FA POWER PROJECT.

4.3   Project Design Codes and Standards

The following organization’s standards and codes are applicable to design and construction practices for the project.

ANSI B31.3	Plant Piping

ASME IX	Welder Qualifications

AWS A3/0	Definitions of Welding Terminology

AWS B2.1-84	Standard for Welding Procedure and Performance Qualification

AWS D1.1	AWS Code for Structural Welding

AISC	American Institute of Steel Construction – Various sections

ASTM	American Society for Testing Materials – Various Sections

ASME	American Society for Mechanical Engineers – Various Sections

ISA S5.1	Instrumentation Symbols and Identification

NACE RP018890	Standard Recommended Practice: Discontinuity (Holiday) Testing of Protective Coatings

NEMA AB1	Molded Case Circuit Breakers

NEMA ICS1	General Standards for Industrial Control and Systems

NEMA ICS2	Industrial Control Devices, Control and Systems

NEMA ICS4	Terminal Blocks for Industrial Use

NEMA ICS6	Enclosures for Industrial Controls and Systems

MG1	Motors and Generators

PE5	Constant-Potential-Type Electric Utility (Semi-Conductor Static Converter) Battery Chargers

SG2	High Voltage Fuses

WC2	Rubber Insulated Wire and Cable for the Transmission and Distribution of Electrical Energy

NFPA70	National Electric Code

NFPA No. 1	Carbon Dioxide Extinguishing Systems

NFPA No. 37	Stationary Combustion Engines and Gas Turbines

NFPA 850	Fire Protection for Electric Generation

OSHA CFR Title 29	Occupational Safety and Health Administration