Section 6.0	Project QA/QC Plan

TABLE OF CONTENTS

I.	SCOPE

II.	TESTS / INSPECTIONS-CIVIL

Iii.	TESTS / INSPECTIONS GROUND GRID

IV.	TESTS / INSPECTIONS-MECHANICAL

- Structural Steel

- Welding Inspections/Tests

- Natural Gas Piping

- Lube Oil System

- Hydraulic System

- Raw Water System

- Fire Water System

- Pump Testing

V.	WELDER QUALIFICATIONS

VI.	AREA DESIGNATION

VII.	MATERIAL TEST REPORTS

VIII.	SUB-SYSTEMS MECHANICAL TESTS

- Fuel System Tests

- Lube Oil System Tests

- Hydraulic Starter System Tests

- Instrument Air System Leak Tests

IX.	SPECIFIC TESTS-ELECTRICAL

- Ground Grid Integrity Test

- Cable Insulation Testing-Megger

- Cable Insulation Testing-Hi Potential Testing

D.	Cable and Conduit Installation-Inspections

E.	Point to Point Testing

F.	Switchgear, Motor Control Centers, Breakers and other Electrical Components, Instrumentation

X.FACTORY ACCEPANCE TESTS / INSPECTION

XI.	START-UP TESTING AND COMMISSIONING

XII.	REPORTS

PART 2	PROJECT SPECIFIC TEST AND INSPECTION PROCEDURES

I.	SCOPE

The following civil, mechanical and electrical test and inspection requirements have been developed for the project.

The civil, mechanical and electrical tasks on this project shall comply with the standards set forth in this document to ensure both the safety and quality of the installation.  This document stipulates the inspections and tests that will be performed on the project.

II.	TESTS / INSPECTIONS - CIVIL

Inspections will be undertaken throughout the civil portion of the project.  The site dimensions will be confirmed.  Topographical elevations will be confirmed following grading.  All concrete slab and wall dimensions will be confirmed prior to concrete pouring.  All concrete will be confirmed to be compliant with design specifications.  A qualified third party inspection agency will be retained to conduct slump tests prior to and during concrete pours.  All concrete will be strength-tested intervals per ASTM standards.  Grouting of mechanical equipment skids will be performed per the developed specifications.

Iii.	TESTS / INSPECTIONS - GROUND GRID

The ground grid will be inspected throughout installation to ensure that materials used are per design specifications and that installation splices, junctions, and taps are made properly.  Depth and dimensional boundaries will be measured and recorded.  At the conclusion of installation, the grounding grid will be tested using a test instrument specifically for the task to confirm acceptable impedance levels.

IV.	TESTS / INSPECTIONS - MECHANICAL

Several elements of the project will require welding during fabrication and installation.  These elements include:

- Structural Steel

- Fuel System - Natural Gas Fuel System Piping

- Fuel System -  Liquid Fuel System Storage Tank and Piping

- Process Water Systems

- Raw Water System Storage Tank and Piping

- Waste Water System Piping

- Firewater System Piping (HDPE piping Thermal Welding Inspections)

- Oily Waste System

- Lube Oil System

The welding inspection criteria for each of these tasks will be based upon the applicable codes and standards.  The following paragraphs briefly describe each task and stipulate the specific code and/or standard(s) that apply.

- Structural Steel

The structural steel aspects of the project will consist of the building related structural steel and various supports of racks.  Design and erection of these assemblies shall be in accordance with the latest edition of the AISC.  All welding will be visually inspected per AWS applicable codes and standards.

- Welding Inspections/Tests

All welders are required to have current certification of their qualifications.  Current certifications should indicate the welder has been tested to the project welding procedures within one year prior to welding on project piping.

All visual-welding inspections will be performed by persons who have current certification from AWS or ASNT-TC-1A.  All NDE will be performed and approved by persons holding current ASNT-TC-1A Level II certification for the specific test processes implemented.  All visual welding inspections will be performed based on the criteria established in ANSI B31.1 and AWS D1.1.

Radiographic Testing (RT) where necessary will be performed in accordance with standards established by ASME Boiler and Pressure Vessel Code, Article 2, Section V, except as stipulated in the applicable code, ANSI B31.3 (Pipe welding inside Plant Battery Limits).

All radiographs of full penetration welds must be accepted by a certified Level II inspector with current certification under ASNT-TC-1A.  Accept/Reject criteria for all welds shall be in accordance with criteria established as well as applicable codes.  Any rejections will require two (2) weld penalty shots on that welder.  If in the judgment of the Site QA/QC Manager that a welder or welders have excessive rejections; may demand the welder be removed from the project or certified to weld on only non critical piping.

- Natural Gas Piping

Piping from the supply source to the Fuel Filter/Separators will be Carbon Steel.  The piping on the downstream side of the filter/separators to the will change to Stainless Steel piping.  All Natural Gas piping will be designed and constructed to ANSI B31.3.

A total of 100% of the pipeline welds (100% of each weld) will be subjected to Radiographic Testing (RT).

All radiographs of full penetration welds must be approved and accepted per criteria established in Section B above.

- Liquid Fuel System

All piping systems will be visually inspected by Craft Inspectors qualified to visually inspect these systems.  10% carbon steel piping welds will undergo RT, 100% of the weld.  RTs will be examined and approved by a Level II or III ANSTC-1A qualified technician.

PE or RTR lines will unde4rgo hydro or pneumatic testing. If Hydrotest is used, water as the test medium hydro will be 1.5 times design pressure up to a maximum of 150 PSI.  If a pneumatic test is decided upon, the test pressure will be 1.2 times design pressure.

- Lube Oil System

The Lube Oil system consists of a skid and interconnecting stainless steel piping to the Gas Turbine Package.  All interconnecting pipe welds shall be in accordance with ANSI B31.3.  All Lube Oil system welds will undergo visual inspection or testing in accordance with ANSI B31.3.  Ten percent (10%) of these welds will undergo RT testing (100% of the weld)

- Hydraulic System

The Hydraulic System consists of a skid and interconnecting stainless steel piping to the Gas Turbine Package.  All interconnecting pipe welds shall be in accordance with ANSI B31.3.  All Hydraulic system welds will undergo visual inspection or testing in accordance with ANSI B31.3. Ten percent (10%) of these welds will undergo RT testing (100% of the weld)

All radiographs of full penetration welds must be approved and accepted per criteria established in Section B above.

G.	Raw Water System

The Raw Water System consists of Carbon Steel Piping.

Raw Water System piping welds will be visually inspected.

H.	Process Water Systems

All welded steel piping will be visually inspected as welds are completed.  All PVC piping joints will be inspected as they are made up. The Process water systems will be inspected prior to startup.  All pumps will be balanced.  Remaining components will be inspected and confirmed that they are supplied and installed per specifications.

J.	Pump Testing

All pumps supplied will be balanced and confirmed as fully operational prior to startup.

V.	WELDER QUALIFICATIONS

Welders qualified according to the appropriate codes shall make all welds on the project:

- Structural Steel			AWS CODE D1.1

- Fuel System Piping		ANSI B31.3

- Lube Oil System Piping		ANSI B31.3

- Hydraulic Startup System Piping	ANSI B31.3

All welders will be required to provide certification of their qualification to the appropriate standard.  Each welder's certified qualifications will be reviewed and approved by the welding inspector prior to the welder’s beginning work on the project.  Applicable welding procedure specifications (WPS) and Procedure Qualification Reports (PQRs) will be required.  All reports and certifications will be in accordance with ASME Section IX Article II.

VI.	AREA DESIGNATION

Areas where combustible fluids, gases or vapors might be present shall be classified as hazardous areas or hot areas.  Guidelines for welding in these areas will be drawn from ANSI Z49.1.  Areas designated as safe areas will be those areas on site remote from hazardous areas and where no contact with combustible fluids, gases and vapors are present.  Welding in these safe areas, as well as on-site welding fabrication, will be subject to the same standards and codes listed in the previous paragraphs.  The welding inspector shall designate an area classification for the project.

VII.	SUB-SYSTEMS MECHANICAL TESTS

The test requirements for the various tasks on the project are defined in the following paragraphs.  Tests are defined in this case to be "system" centered, i.e., hydrostatic tests, vacuum tests, etc., versus inspections which are "component" centered.  All tests shall be performed in the presence of a QA/QC inspector or his designate.  All tests shall be documented with a written test report.  The test report shall include a description of the test, the item or items tested, the procedure used, the date and time of the test and the test results.  All test documentation shall be signed by the inspector.

A.	Fuel System Tests

All fuel system piping shall be subjected to hydrostatic leak testing to 1.5 times the design pressure.  Non-pipe components of the system shall be isolated from the test.  The hydrostatic leak test pressure shall be held for a minimum of 1 Hour and then reduced in accordance with ANSI B31.3 to conduct examination for leakage.  Pneumatic tests on the PE or RTR may be substituted at 1.2 times design pressure.

- Lube Oil System Tests

All Lube Oil System piping shall be subjected to hydrostatic leak testing to 1.5 times the design pressure.  Non-pipe components of the system shall be isolated from the test.  The hydrostatic leak test pressure shall be held for a minimum of 1 Hour and then reduced in accordance with ANSI B31.3.

- Hydraulic Starter System Tests

All Hydraulic Starter System piping will be subjected to hydrostatic leak testing to 1.5 time the design pressure.  Non-Pipe components of the system shall be isolated from the test.  The hydrostatic leak test pressure shall be held for a minimum of 1 Hour and then reduced in accordance with ANSI B31.3.

D.	Process Water System Tests

All metallic process water system piping will be leak service tested prior to commissioning. The piping systems under test will be brought up to Normal Operating Pressure and this pressure will be held for 10 minutes or as long as it takes to check each joint or fitting on the line under test. Test shall be conducted in accordance with ANSI B31.3 to conduct examination for leakage.  Piping Systems which will be tested in this manner are the following:

- Cooling Water Systems (New Piping)

- Oily Water Piping

E.	Instrument Air System Leak Tests

Instrument air piping systems will be subjected to a Pneumatic leak test following installation.  Pressures will be raised to Normal Operating Pressures levels for each system and held for a minimum of 10 minutes.

VIII.	SPECIFIC TESTS – ELECTRICAL

A.	Ground Grid Integrity Test

The new installed grounding cables/rods will be attached to the existing system.  Installed Ground Grid will be tested using a suitable multimeter to measure integrity prior to startup.  Continuity and resistance will be confirmed for the new installed cables/rods.  The readings will be recorded for record.

B.	Cable Insulation Testing - Megger

All 600 Volt and above wire and cable to be used on this project will undergo an insulation test or tests to ensure cable is suitable for intended usage and has structural integrity for installation.  All low voltage cables, below 600 volts, will be tested for continuity prior to being energized.

All medium and high voltage cable and wire will undergo Megger testing.  Cables will be tested to levels established not to exceed the rated voltage of the cables.  Megger testing will be performed with a calibrated test instrument certified to national standards.

The results will be recorded and maintained for record.  A cable failing a Megger test will be tagged, segregated and removed from the job site.

C.	Cable Insulation Testing - Hi Potential Test

Medium and high voltage cables will undergo Hi-Potential testing to detect any insulation breakdown in these cables.

Testing will be accomplished with a calibrated instrument certified to national standards.  Results will be recorded and maintained for record.

D.	Cable and Conduit Installation - Inspections

All cable, conduit and associated fittings will be checked to ensure compliance to specifications developed for this project.  Conduit, fittings and cable installation will be monitored during construction to ensure compliance to NEC codes.

E.	Point to Point Testing

All installed cables shall be point-to-point tested prior to being energized.  The point-to-point test shall confirm cables are installed as designed and phased properly.

F.	Switchgear, Motor Control Centers, Breakers, and other Electrical Components, Instrumentation

All switchgear, motor control centers, breakers and other electrical components, will be inspected and tested prior to and following installation.  Specific test procedures will be developed for each major piece of equipment to be installed.  Electrical components will be inspected prior to installation and, in most cases, will be tested as part of a larger sub-system.  Instrumentation will be inspected prior to installation and calibrated following installation.  Instrumentation will be tested as part of a larger sub-system.

IX.	FACTORY ACCEPTANCE TESTS / INSPECTIONS

The Client has the right to request the contractor an inspection of the equipment and witness all factory tests prior to shipment to the Project site if schedule allows. Tests will be undertaken at the manufacturer or fabricator's facility prior to being shipped to site.

X. 	STARTUP TESTING AND COMMISSIONING

Startup testing and commissioning will involve integration of all sub-systems into a complete system-wide test of operation.  Testing will involve operation of all sub-systems listed below:

- Process Water Systems – Raw Water Supply System and Firewater System

- Fuel Gas Delivery System

- Gas Turbine Startup

- Gas Turbine Electrical Transmission

- Breaker Operation

- Protective Relays, Breaker Testing

XI.	REPORTS

A copy of all inspection and test reports shall be maintained in a file at the project site.  These reports shall be made available for review and reference as may be required throughout the project.  The original copies of all inspection and test reports shall be forwarded periodically to the Quality Assurance Manager for review and safekeeping.  Quality related problems that cannot be readily corrected at the project site will be immediately referred to the Quality Assurance Manager for resolution.