Section 2.0	Equipment List - Detailed Division of Responsibility between Owner and Contractor:

Note: The Owner has purchased two (2) Liquid fueled GE Frame 7FA GTG’s with associated facilities and two (2) Liquid fueled LM 6000 PC Sprint GTG’s for this project.  These units and associated equipment are identified in the Table Below:

| Material/Responsibility | Qty | Description |  |
| --- | --- | --- | --- |
| OWNER Provide /CONTRACTOR Install | 2 | Liquid Fueled GE Model Frame 7FA (60Hz) DLN Gas Turbine Generator including Water Injection for NOX for liquid fuel with Associated Equipment – See Details in Appendix |  |
|  | 2 | Inlet Air Filter Assembly with Evaporative Cooler |  |
|  | 2 | Water Injection Flow Center w/pumps |  |
|  | 2 | Liquid Fuel Injection Skids – Stainless Steel piping, duplex filters, fuel atomizing module w/air compressor, motor driven fuel pump |  |
|  | 2 | Lubricating and Hydraulic System w/pumps, filters and coolers |  |
|  | 2 | Exhaust System Diffuser, expansion joint – no stack |  |
|  | 2 | Fire Protection System |  |
|  | 2 | Water Wash Cleaning System Skids |  |
|  | 2 | GTG Cooling Water System excluding piping, pumps, motors, etc. |  |
|  | 2 | Generator Start with load commutated inverter and isolation transformer |  |
|  | 2 2 2 3 | Hydrogen Cooled Generator including Generator Gas Coolers, LO Systems 18KV/4160V 12/15 MVA Aux Transformers 4160 SWGR 4160/480V Aux Transformers |  |
|  | 2 | Generator Excitation Systems, Static Components, Current & Voltage Transformers |  |
|  | 2 | PEEC Modular Building with: |  |
|  | 2 | -Turbine Control Panels |  |
|  |  | - Local Operator Station |  |
|  | 2 | -Generator Protection Panel |  |
|  | 2 sets | - 24 VDC Batteries and Chargers |  |
|  | 2 sets | -125 VDC Batteries and Chargers |  |
|  | 2 | GTG Auxiliary Cooling System with fin-fans |  |
|  | 2 sets | Cooling Water Circulation Pumps |  |
|  | 2 sets | Fuel Gas Filters |  |
|  | 2 | Liquid Fueled GE LM 6000 PC Sprint Gas Turbine Generator packages Including Water Injection for NOx with Associated Equipment – See Details in Appendix |  |
|  | 2 | Inlet Air Assembly |  |
|  | 2 sets | Turbine and Generator Control Panels |  |
|  | 2 sets | 24 VDC Batteries and Chargers |  |
|  | 1 Lot | Gas Turbine Generator Technical Representatives |  |
| OWNER Will Provide |  |  |  |
|  | 1 Lot | Project Site free and clear of rock and ground water |  |
|  | 1 Lot | #2 Diesel Fuel delivered to site boundary by pipeline with measurement |  |
|  | 1 Lot | 230 KV Utility connection to Plant 230KV Dead-end Towers |  |
|  | 1 Lot | DFO and Water for commissioning and start up |  |
|  | 1 Lot | Waste Water Disposal |  |
|  | 1 Lot | Eight (8) Telephone Circuits to Project Site |  |
|  | 1 Lot | Permits for Environmental, Transportation, Building, Construction, Operations, etc. |  |
|  | 1 Lot | Construction & Commissioning Water and 480V three phase power |  |
|  | 1 Lot | Access Roads to site |  |
|  | 1 Lot | Import Duties and Taxes |  |
|  | I Lot | Construction lay down area (3 acres) within or adjacent to project site |  |
|  | 1 Lot | Transportation of Owner Equipment from the US to Site |  |
| Contractor – Derwick EPC Responsibility |  |  |  |
| Civil / Structural |  |  |  |
|  | 1 Lot | Site Preparation, Rough Grading, Excavation, and final grading |  |
|  | 1 Lot | Plant Concrete Foundations |  |
|  | 1 Lot | Plant Paving, Gravel and Pads for Turbine and Generator |  |
| Buildings |  |  |  |
|  | 1 | Climitized Control Room and Office Building (60’ x 70’) with attached Maintenance / Warehouse Building (75’ x 120’) |  |
|  | 1 | Water Treatment – pumps Building (100’ x 60’) |  |
|  | 1 | Fuel Treatment, pumps Shed (35’ x 30’) and MCC Room (10’ x 30’) |  |
|  | 1 | Guard House (15’ x 15’) |  |
| Contractor (continued) |  |  |  |
| Mechanical | 2 | Frame 7FA - 55 Ft. tall Exhaust Stack with Silencing |  |
|  | 2 | GE LM 6000 PC – 45 ft. tall Exhaust Stacks with silencing |  |
|  | 1 | Lube Oil Cooling water System for GTG’s including piping, pumps, etc. |  |
|  | 2 | 2 ea. 20 Hp Inlet Evap Pumps with 5 Hp sump |  |
|  | 1 | Raw Water pipeline 500 meters from Ceauta Creek to the site boundary with pumps for a reliable 1000 gpm supply |  |
|  | 1 | Evap water Storage Tank 300,000 gallons |  |
|  | 2 | Evap water Pumps 20 Hp |  |
|  | 1 | Raw water Storage Tank 1,000,000 gallon c.s. |  |
|  | 1 | Raw water 60HP duplex forwarding Pump 940 gpm skid |  |
|  | 1 lot | Demin/RO/EDI Water Treatment System – 802 gpm |  |
|  | 1 | Demin Water Forwarding Pumps Skid 650 gpm |  |
|  | 1 | Demin Water Forwarding Pumps Skid 130 gpm |  |
|  | 2 | Demineralized Water Storage Tank, 660,000 Gallons ea. s.s. |  |
|  | 2 | 100% Demineralized Water Forwarding Pumps for Turbine Wash |  |
|  | 2 2 | Duplex Demineralized Water Filters LM 6000’s Duplex Demineralized Watet Filters Fr. 7FA’s |  |
|  | 2 2 2 | Demineralized Water Injection Pumps NOx / Fogging DFO Injection Skid’s Fr 7FA’s DFO Fuel Filters - Fr. 7FA’s |  |
|  | 2 | DFO Injection Skid’s LM 6000 PC’s |  |
|  | 2 | DFO Fuel Filters – LM 6000 PC’s |  |
|  | 1 | Oily Water Separators |  |
|  | 1 | Waste Oil Tank, 10,000 Gallon. |  |
|  | 1 | Waste Oil Delivery Pump |  |
|  | 1 | Waste Water Tank, 10,000 Gallon |  |
|  | 1 | Waste Water Delivery Pump |  |
|  | 3 | Instrument Air Package with two compressors, receiver, filters and dryer |  |
|  | 1 | Raw Liquid fuel storage tank, (2,000,000 gallons) c.s. |  |
|  | 2 | 525 gpm Liquid Fuel Forwarding Pumps |  |
|  | 1 | Liquid Fuel Treatment System (4 centrifuges) 3ea 600,000 GPD capacity |  |
|  | 1 | 2,000,000 gallons Clean Fuel Storage Tank s.s. |  |
|  | 1 | 10,000 gallons sludge storage with forwarding pump for truck removal |  |
|  | 2 | Liquid Fuel Transfer Pumps LM 6000 PC’s |  |
|  | 2 | Liquid Fuel forwarding Pumps Fr. 7FA’s |  |
|  | 3 | Treated Liquid Fuel Forwarding Pumps LM 6000 PC’s – 65 gpm ea. |  |
|  | 3 | Treated Liquid Fuel Forwarding Pumps Fr. 7FA’s - 248 gpm ea. |  |
|  | 1 set | Liquid Fuel Filters LM 6000 PC’s |  |
|  | 1 Lot | Firewater System including pumps, GSU sprays, Plant Firewater Loop, Fuel tank foam systems, with controls, monitors & hydrants |  |
|  | 1set | Liquid Fuel Filters Frame 7FA’s |  |
| Electrical 230KV | 2 | 18KV/230KV GSU 220 MVA |  |
| Substation | 2 | 13.8KV/230KV GSU 83 MVA |  |
|  | 12 | 230KV GSU 83 MVA |  |
|  | 8 | 230 Disconnect Switches (2 future) |  |
|  | 7 | Dead End Towers |  |
|  | 3 | CVT’s |  |
|  | 1 Lot | Protective Relays |  |
| Balance of Plant | 2 | 18 KV 8000 amp GTG Generator Breaker NEMA 3R Frame 7FA’s |  |
| Electrical | 1 Lot 2 2 1 Lot 1 | 18 KV ISO Phase Bus – Fr 7FA’s Gen Breaker to GSU’s 18 KV / 4160V 12/15 MVA Aux Transformers 13.8KV 3000 amp GTG Generator Breaker NEMA 3R LM 6000 PC’s 13.8KV Cable Bus LM 6000 PC’s Gen Breakers to GSU’s 13.8KV/480V 2500 KVA Aux. Transformer |  |
|  | 1 | 4160V / 480 V 1500 KVA Station Service Transformer |  |
|  | 1 | 4160V / 480 V 1000 KVA Station Service Transformer |  |
|  | 2 | 4160 V Distribution Switchgear |  |
|  | 1 | Diesel Black Start / Emergency Generator – 480 V -1000 KW |  |
|  | 2 | 480 V BOP MCC |  |
|  | 2 | 480 V Distribution Board |  |
|  | 1 Lot | BOP 480 V / 120 V Transformers, Lights, Panels etc. |  |
|  | 1 | UPS System for Control Room |  |
|  | 8 | Welding Receptacles |  |
|  | 1 | Plant Grounding Grid |  |
|  | 1 Lot | Lightning Protection |  |
|  | 1 Lot | Cathodic Protection for underground steel piping |  |
|  | 1 Lot | Area Lighting |  |
| I&C |  |  |  |
|  | 1 Lot | Plant Instrumentation |  |
|  | 1 | Plant DCS System |  |
| Construction |  |  |  |
|  | 1 Lot | Construction Tools, Rental Equipment & Rental Cranes |  |
|  | 1 Lot | Relocation of Owner’s Electrical Transmission Lines presently crossing over the existing site |  |
|  | 1 Lot | Construction Site Temporary Power Distribution |  |
|  | 1 Lot | Local Subcontractor(s) Electrical & Mechanical Craft Labor |  |
|  | 1 Lot | Transportation of all Contractor supplied BOP equipment |  |
|  | 1 Lot | Construction Offices, Storage, Temporary Facilities and Utilities |  |
|  | 1 Lot | Lubricants, Chemicals, Filters, etc. for Plant Commissioning |  |
|  | 1 Lot | Balance of Plant Start up and Commissioning Spare Parts |  |
| Engineering |  |  |  |
|  | 1 Lot | Conceptual and Detail Design Engineering (Total Plant) |  |
| Project Management |  |  |  |
|  | 1 Lot | Project Management with Scheduling, QA/QC, safety, and training |  |
|  | 1 Lot | Plant Start-up, Commissioning and Testing |  |
|  | 1 Lot | Overall Plant Training |  |