Note: The Owner has purchased two (2) dual fueled GE LM 6000 PC Sprint Gas Turbine Generator packages with associated facilities and two (2) dual fueled GE LM 2500+ Gas Turbine Generator packages for this project.  The Natural Gas fuel delivery pressure to the site is 250 psig.  These Gas Turbines when fueled with natural gas will require Fuel Gas Compressors and associated equipment as identified below:

- Fuel Gas Compressor Sets Scope of Supply

2.1 	Fuel Gas Compressors for 2 x LM 2500+ Gas Turbine Generators

Contractor will supply two (2) Fuel Gas Compressor sets each capable of providing 7 mmscfd of fuel gas to each GE LM 2500+ GTG at a minimum of 500 psig.with a minimum suction pressure of 250 psig.

- The Fuel Gas Compressors with be electric motor driven at 4,160 KV, 3 phase

- Skid mounted motor with multi-stage compressor

- One Compressor with water/ lube oil exchanger and One with Fin Fan Cooler

- Control panel.  Note: These items will be installed in the contractor supplied modular pre-built fuel gas compressor control with MCC’s

  - Fuel Gas Compressors for 2 x LM 6000 PC Gas Turbine Generators

Contractor will supply Three (3) Fuel Gas Compressor sets each capable of providing 11 mmscfd of fuel gas to each GE LM 6000 PC Sprint gas turbine generator sets at a minimum of 700 psig with a minimum suction pressure of 250 psig  One compressor will act as standby for the 2ea LM 25000 Plus GTG’s and the 2ea LM 6000 GTG’s

- These Fuel Gas Compressors will be electric motor driven at 4.16 KV, 3 phase

- Skid mounted motor with multi-stage compressor

- Fin-fan Lube oil cooler

- Control Panel

- 4160 and 480 volt MCC’s installed in the Electrical Room of the Compressor Shed

Contractor will provide Turnkey EPC Services to purchase and install these Fuel Gas Compressors and required Balance of Plant described below:

2.3 Scope of Supply and Detailed Division of Responsibility

| Material/Responsibility | Qty | Description |  |
| --- | --- | --- | --- |
| Owner: |  |  |  |
|  | 1 Lot | Natural Gas Pipeline and supply metered at inter-tie point within 50’ of Plant Boundary at a quality that meets GE’s Aero-derivative gas turbine specifications. |  |
|  | 1 Lot | Permits for Environmental, Importation, Building, Operations, etc. to allow plant construction and commercial operations |  |
|  | 1 Lot | Construction & Commissioning Water and 480V three phase power |  |
|  | 1 Lot | Access Roads to site as required |  |
|  | 1 Lot | Import Duties and Taxes |  |
|  | 1 lot | Right of Way, easements, etc. to allow proposed interconnects as required |  |
|  | 1 Lot | Project Site free and clear of rock and ground water with sufficient space to install Fuel Gas Compression facilities |  |
|  | 1 Lot | Natural Gas Supply Delivered to the Plant Boundary by pipeline at a minimum of 250 psig pressure. |  |
|  | 1 Lot | Permits for Environmental, Transportation, Building, Construction, Operations, etc. |  |
|  | 1 Lot | Construction & Commissioning Auxiliary Power, 480V three phase power |  |
| Contractor will Provide and Install |  |  |  |
| Civil, Engineering & Construction: | 1 Lot | Design Engineering and Construction Management of Contracted Labor including Safety, QA/QC, Project Schedule Management, Technical management, start-up, commissioning, systems turnover and performance testing. |  |
| Contractor Mechanical Supply | 1 Lot | Plant Site civil earthwork, leveling, foundations, roadways, plant gravel, asphalt and paving |  |
|  | 2 | Fuel Gas Compressors for the 2 GE LM 2500 GTG’s |  |
|  | 3 | Fuel Gas Compressors for the 2 GE LM 6000 GTG’s with one compressor as a spare capable of serving as back up to either model of GTG |  |
|  | 1 Lot | Mechanical pipe, valves, and material including installation with contract labor |  |
| Electrical |  |  |  |
|  | 2 | 13.8KV 4.160 KV 3750 KVA Aux Transformer |  |
|  | 2 | 4.16 KV 1200 Amp Breakers |  |
|  | 1 Lot 1 | Electrical wire, conduit, and cable including installation with contract labor 4160 V MCC for Compressors w/ 5ea Starter |  |
|  | 1 | 480 V Distribution Panel Feeder Breaker |  |
|  | 1 | BOP 480V MCC |  |
|  | 1 Lot | Cathodic Protection System |  |
| Associated Instrumentation: |  |  |  |
|  | 1 Lot | Plant Instrumentation |  |
|  | 1 Lot | Interconnect to Plant DCS System |  |
| Buildings: |  |  |  |
|  | 1 | Fuel Gas Compressor Shed |  |