Note: The Owner has purchased two (2) dual fueled GE LM 6000 PC Sprint Gas Turbine Generator packages with associated facilities and two (2) dual fueled GE LM 2500+ Gas Turbine Generator packages for this project.  The additional LM 6000 PC requires an expansion of the Water Treatment Facility.

- Demin Water Treatment Expansion Scope of Supply

2.1 	Demin Water for 1 dual fueled x LM 6000 Gas Turbine Generator

Contractor will supply an expansion to the water treatment capacity to allow NOx and Sprint Demin Water to control the NOX to Air Permit levels when the LM 2500+ and LM 6000 PC Sprint are operating on natural gas or Liquid Fuel.

- The Natural Gas & Liquid Fuel Supply must meet the GE Aero-Derivative Gas Turbine Fuel Specifications for the LM 2500+ and LM 6000 PC.

- The Demin Water Treatment System will be installed in an expansion of the existing Water Treatment Building

- The expansion will produce up to the required 60 gpm or 86,000 gallons per day.

- The Demin Water Storage will be increased by 50,000 gallons

- The Raw Water Storage will be increased by 550,000 gallons

Contractor will provide Turnkey EPC Services to purchase and install the Demin Water Treatment expansion and required Balance of Plant described below:

2.2 Scope of Supply and Detailed Division of Responsibility

| Material/Responsibility | Qty | Description |  |
| --- | --- | --- | --- |
| Owner: |  |  |  |
|  | 1 Lot | Permits for Environmental, Building, Operations, etc. to allow plant construction and commercial operations |  |
|  | 1 Lot | Construction & Commissioning Water and 480V three phase power |  |
|  | 1 Lot | Access Roads to site as required |  |
|  | 1 Lot | Import Duties and Taxes |  |
|  | 1 lot | Right of Way, easements, etc. to allow proposed interconnects as required |  |
|  | 1 Lot | Project Site free and clear of rock and ground water with sufficient space to install the required facilities |  |
| Contractor will Provide and Install |  |  |  |
| Civil, Engineering & Construction: | 1 Lot | Design Engineering and Construction Management of Contracted Labor including Safety, QA/QC, Project Schedule Management, Technical management, start-up, commissioning, systems turnover and performance testing. |  |
| Contractor to Provide Mechanical as Outlined | 1 Lot 1ea 1ea 1ea 1ea 1ea | Plant Site civil earthwork, leveling, foundations, roadways, plant gravel, asphalt and concretes as mutually agreed. RO System Expansion of 60 GPM Water Softener Expansion of 60 GPM EDI Demin System Expansion of 60 GPM Increase in Raw Water Tank of 550,000 gal Increase in Demin Water Tank of 50,000 gal |  |
|  | 1 Lot | Mechanical pipe, valves, and material including installation with contract labor |  |
| Electrical |  |  |  |
|  | 1 | 480 V Supply for treatment and pumps |  |
|  | 1 Lot | Electrical wire, conduit, and cable including installation with contract labor |  |
|  | 1 | 480 V Distribution Panel |  |
|  | 1 | BOP 480V MCC |  |
| Associated Instrumentation: |  |  |  |
|  | 1 Lot | Plant Instrumentation |  |
|  | 1 Lot | Interconnect to plant DCS System |  |
| Buildings: |  |  |  |
|  | 1 | Water Treatment Building expansion |  |