Note: The Owner has purchased one (1) dual fueled GE LM 6000 PC Sprint Gas Turbine Generator package with associated facilities and two (2) dual fueled GE LM 2500+ Gas Turbine Generator packages for this project.  These units and associated equipment are identified in the Table Below:

- Gas Turbine Generator Sets Scope of Supply

2.1 	LM 2500+ Gas Turbine Generators

Owner will supply two (2) LM2500 + dual fuel gas turbine generator sets each includes the following scope of supply:

- LM2500+ dual fuel engine with water injection for NOx control

- Skid mounted engine drive module

- 2-pole 60 Hz Brush generator for pad mounting

- Multi-stage static high efficiency air filter

- Dual ventilation fans

- Electric hydraulic start skid

- Generator Lube Oil skid.

- Liquid fuel pressurization skid

- Water injection pressurization pump skid

- Fin-fan lube oil cooler skid

- Free standing turbine control panel.  Note: These items will be installed in the contractor supplied modular pre-built gas turbine control building with MCC’s and Batteries w/Charger.

  - LM 6000 PC Gas Turbine Generator

Owner will supply One (1) dual fueled GE LM 6000 PC Sprint gas turbine generator set including the following scope of supply:

- LM 6000 Duel fuel engine with water injection for NOx control

- Water injection for Sprint Performance

- Skid mounted engine drive module

- 2-pole 60 Hz generator

- Multi-stage static hight efficiency air filter

- Duel ventilation fans

- Electric hydraulic start skid

- Generator Lube Oil skid

- Liquid fuel pressurization skid

- Water injection pressurization pump skid

- Fin-fan lube oil cooler skid

- Free standing GTG Control Panel.  Note:  Contractor will supply modular control Building w/MCC, Batteries and Chargers.

Contractor will provide Turnkey EPC Services to purchase and install (1) the required Balance of Plant identified below and (2) to install Owner’s provided equipment described above.

2.3 Scope of Supply and Detailed Division of Responsibility

| Material/Responsibility | Qty | Description |  |
| --- | --- | --- | --- |
| Owner: |  |  |  |
|  | 1 Lot | Natural Gas Pipeline and supply metered at inter-tie point within 50’ of Plant Boundary - Future |  |
|  | 1 Lot | Liquid Fuel supply delivered to the site boundary via pipeline |  |
|  | 1 Lot | Liquid Fuel for Commissioning / Start-up that meets GE Fuel Specifications |  |
|  | 1 Lot | Raw Water Supply to Site Boundary |  |
|  | 1 Lot | Waste Water and Waste Oil Truck Removal |  |
|  | 1 | Provision for Telephone communications to site |  |
|  | 1 Lot | Permits for Environmental, Importation, Transportation, Building, Operations, etc. to allow plant construction and commercial operations |  |
|  | 1 Lot | Construction & Commissioning Water and 480V three phase power |  |
|  | 1 Lot | Access Roads to site |  |
|  | 1 Lot | Import Duties and Taxes |  |
|  | 1 lot | Right of Way, easements, etc. to allow proposed interconnects as required |  |
| Gas Turbine Generator Packages – Owner Provided |  |  |  |
|  | 2 | New GE LM2500 + (60Hz) Dual Fueled Gas Turbine Generator Packages |  |
|  | 2 | Brush Generators |  |
|  | 2 | Turbine Control Panels |  |
|  | 2 | Generator Control Panel and Protection Panel |  |
|  | 2 sets | 24 DC Batteries and Chargers |  |
| OWNER Provide /CONTRACTOR Install | 1 | New GE LM 6000 PC Sprint (60Hz) Gas Turbine Generator with Associated Equipment |  |
|  | 1 | -Turbine Control Panel |  |
|  | 1 | -Generator Control Panel and Protection Panel |  |
|  | 1 set | - 24 VDC Batteries and Chargers |  |
| OWNER Will Provide |  |  |  |
|  | 1 Lot | Project Site free and clear of rock and ground water |  |
|  | 1 Lot | #2 Diesel Fuel Supply Delivered to the Plant Boundary either by truck or pipeline. |  |
|  | 1 Lot | Industrial Water for Commissioning and Startup |  |
|  | 1 Lot | Diesel Fuel Supply for Commissioning and Startup |  |
|  | 1 Lot | Electrical Back Feed for Commissioning and Startup |  |
|  | 1 Lot | Waste Oil Disposal |  |
|  | 1 Lot | Waste Water Disposal |  |
|  | 1 Lot | Permits for Environmental, Transportation, Building, Construction, Operations, etc. |  |
|  | 1 Lot | Construction & Commissioning Auxiliary Power, 480V three phase power |  |
|  | 1 Lot | Access Roads to site |  |
|  | 1 Lot | Import Duties and Taxes |  |
| Contractor will Provide and Install |  |  |  |
| Civil, Engineering & Construction: | 1 Lot | Design Engineering and Construction Management of Contracted Labor including Safety, QA/QC, Project Schedule Management, Technical management, start-up, commissioning, systems turnover and performance testing. |  |
|  | 1 Lot | Civil earthwork, leveling, foundations, roadways, plant gravel, asphalt and concretes as mutually agreed. |  |
| Mechanical: | 1 set | GTG Tools |  |
|  | 2 | LM 2500+ GTG Exhaust Stacks with Silencer |  |
|  | 1 | LM 6000 GTG Exhaust Stack with Silencer |  |
|  | 1 Lot | Mechanical pipe, valves, and material including installation with contract labor |  |
|  | 1 | Duplex 185 scfm Plant Service and Instrument Air Compressor |  |
|  | 1 | 2000 gallon Underground Oily Water Separator System |  |
|  | 1 | 10,000 gallon Waster Oil Storage Tank for Truck removal |  |
|  | 1 | 10,000 gallon Waste Water Oil Storage Tank for Truck Removal |  |
|  | 1 | Waste Water Fwd. Pump |  |
|  | 1 | Waste Oil Fwd. Pump |  |
|  | 1 set | Firewater Pumps (Diesel, Electric & Jockey) with Controls |  |
|  | 1 | Firewater HDPE underground distribution system with hydrants, monitors, controls and foaming system. |  |
|  | 1 | 250,000 gallon Raw Water/Firewater Storage Tank |  |
|  | 2 | Raw Water supply pumps |  |
|  | 2 | Raw Water Forwarding pumps |  |
|  | 1 | Demin. Water Treatment Plant – 35,000 gpd |  |
|  | 2 | 21,000 gallon Fiberglass Demin Water Storage Tanks |  |
|  | 2 | Demin. Water Forwarding Pumps |  |
|  | 1 | 500,000 gallon raw fuel storage tank |  |
|  | 1 | DFO Metering Skid |  |
|  | 1 | DFO Forwarding Pump Skid |  |
|  | 1 | Liquid Fuel Treatment System (2 Centrifuges) |  |
|  | 1 | 200,000 gallon treated fuel storage tank |  |
|  | 3 | DFO Filter Skids |  |
|  | 1 | Sanitary Sewer System |  |
| Electrical |  |  |  |
|  | 2 | 13.8KV 2000 Amp Generator Breakers NEMA 3R |  |
|  | 1 | 13.8KV 3000 Amp Generator Breaker NEMA 3R |  |
|  | 1 Lot | Electrical wire, conduit, and cable including installation with contract labor |  |
|  | 5 | 13.8 KV Fused Disconnects |  |
|  | 1 | 480 V Distribution Panel |  |
|  | 1 | LM 6000 Modular Control Building with 480V MCC, Batteries and Chargers |  |
|  | 1 | BOP 480V MCC |  |
|  | 4 | 480V 750 KVA Aux. Transformers |  |
|  | 2 | 480V/120V/208V Aux Transformers |  |
|  | 6 | Area Lighting Poles each with (2) lights |  |
|  | 1 Lot | Cathodic Protection System |  |
|  | 1 Lot | Lightning Protection |  |
|  | 1 | Plant UPS System |  |
| Instrumentation: |  |  |  |
|  | 1 Lot | Plant Instrumentation |  |
|  | 1 Lot | Plant DCS System Hardware/Software interconnecting cables, documentation |  |
|  | 1 | PBX Communications System |  |
|  | 1 | Loud Speaker System |  |
|  | 2 | Fiber Optic Cables, Fittings & Terminators |  |
| Buildings: | 1 | Guard House (12’ x 15’) |  |
|  | 1 | Local GTG Control / MCC Building |  |
|  | 1 | Office/Control/Restrooms, Warehouse Building (90’ x 60’) |  |
|  | 1 | Water Treatment/Pumps, Instrument Air Compressor, DFO Treatment shed (40’ x 30’) |  |
|  | 1 | Firewater Skid / Foam System Shed |  |
| 69KV Substation: |  |  |  |
|  | 2 ea. | 13.8KV / 69KV Generator Step Up Transformers (2 x LM 2500 on 1 GSU) & (1 LM 6000 on 1 GSU) |  |
|  | 2 ea. | Plant 69KV Overhead Transmission lines to Owners existing 69KV Substation (2) empty bays. |  |
|  | 1 Lot | GSU Dress Out and Test |  |