Section 4.0	Design Basis and Interconnection Points

4.1      Design Conditions

| Design Conditions |  |
| --- | --- |
| Site Elevation (Meters above Mean Sea Level) | 283.6 |
| Multi-year median temperature: | 27.5°C (81.5°F) |
| Maximum dry bulb temperature: | 35°C (95°F) |
| Maximum wet bulb temperature: | 28.3°C (82.94°F) |
| Multi-year median relative humidity: | 85% |
| Median annual precipitation: | 813mm (32 in) |
| (Majority during the months of October and November) |  |
| Predominant wind direction: | Northeast |
| Maximum average multiannual wind velocity: | 80.3km/h (48 mph) |
| Seismic Zone | 4 |
| Fuel Gas Supply Pressure | 250 psig minimum |
| Plant Gas Fuel Consumption Rate (3) FT8 SwiftPac | 42.66 mmscfd * |
| Liquid Fuel Consumption Rate(3) FT* SwiftPac | 219 gpm |
| High Voltage Interconnect @ GSU Bushings | 230KV Substation (By Owner) |
| Instrument Air System | 185 scfm by Contractor |
| Demin Water required | 211 gpm |
| Demin Water Storage | 1,000 m³ (275,000 gal) |
| Raw Water Storage (Includes Fire water) | 2,400 m³ (675,000 gal) |
| Raw Diesel Fuel Storage | 5,000 m³ (2 x 675,000 gal) |
| Clean Diesel Fuel Storage (2) | 3,000 m³ (2 x 275,000 gal) |
| * assumes 900 - 1050 Btu/SCF natural gas quality |  |

4.2	Interconnect Points

| Interconnect Points |  |
| --- | --- |
| Fuel Gas | 250 psig at PDVSA Metering & Regulating Station within Site |
| Liquid Fuel | Diesel Fuel Offloading Station (By Contractor) |
| Plant Waste Water | At waste water tank discharge pump |
| Plant Waste Oil | At waste oil tank discharge pump |
| 230 KV | At GSU High Side Bushings |
| Raw Water Supply | At Plant battery limits from Water Utility (Not purified for drinking) |