Site visit to Planta Luisa Carceres

July 7, 2009

ATTENDEES:

PES- Brett Bettinger, Al Rivera, John Lopez

INELMECA- Freddy Power

LAEDC- Wolfgang Freites, Rafael Narvaez, Diego Izarra

Scope; removal of numerous transformer sections to another area of the site where customer requests we pour a pad with containment to hold the “junk”. Removal of various and numerous sections of concrete – above grade. Customer requests we do not hammer down too far with the concrete as the vibration would likely cause their primary fuel line supply to rupture – very old and deteriorating. They have plans for a new ring main for their fuel line but it will not be complete prior to our efforts on site. Removal of blast walls. Removal of existing backup generator. Addition of fuel pumps and piping to allow feed to the TM2500s. Power supply for the pumps is currently 220v.

- Removal of some concrete required.

- Availability of concrete: need to move on this as there is a substantial amount of development in the area –Concrete companies are : ROFERCA, AMBRIOSO and CEMEX

Liquid fuel quality is poor-need to send sample bottle to plant manager, then have him ship back and we send to lab for analysis. thoughts are to move forward on centrifuge—possible filters could help for first runs of TM’s – along with this will be the amount of filters we might need. (Existing fuel line running parallel to the site, at the entrance side, is fragile, CS) AR-- Fuel lines for units are to be included in our bid price along with forwarding  pumps. These lines are going to be temporary according to customer. We should take into consideration that they would like to place the third TM2500 in same area we should plan to size the piping and pumps as such andmake it optional. No demin avail., will need to add demin and centrifuge for fuel in phase 2 (after this 90 day ordeal). Site will draw a fuel sample for us once we provide the container etc.

- Transportation route from port to the point where loads come off the highway is clear, however several power/telephone/cable tv lines need to be addressed once loads turn off of the highway onto the road to the site, once at the site road and route are clear. Plant road to site approximately 35ft wide. At the entrance to the site there is an elevation difference of about 5 feet. From edge of site to edge of road is about 15 feet. Approximately 40 kilometers from port to site.

- Raw water supply is available from water tower across the road from the site, about 250 feet away from entrance to site, no above ground obstructions.

Electrical – GSU’s – need to look at relocating existing transformers and replacing with a 60 kva or 2 30’s-- Addition of adequately sized transformers; need to input existing transformer rating v.s. TM2500 requirement. We have a clear opportunity for sale of transformers here.

- Liquid fuel supply- run new piping from fuel tanks and add new pumps

- Fire water, per say, is not available.

- Temporary electrical power for both the office area and construction is available. 2 separate points.

- Plant access- available 24/7

- We need to provide guard/s

- We need to provide safety person/s.

- Vehicle parking exists both on plant road and a small area at the entrance to the plant.

Notes:

1)Prevailing wind direction is towards the SE

2 ) Look at 3- TMs in the same location- concern—current proposed configuration of TM’s has the exhausts close to inlets.

3 ) Sleepers are acceptable and desirable as site has multi level concrete sections 6” to 1’.

4) Give price for removing all equipment, loose concrete, junk etc from site to in plant location. (one area is approximately 1/8 mile from site, has a 1300 volt line running near it, the other is approximately ¾ mile away (use of skytrak or Lull desirable to remove materials, junk, equipment etc. from site, will save time as compared to using crane)

5) Fuel Oil is delivered by tanker. About 30 tankers/day, we were told, they have 3 day capacity for existing units.

6) Include price to remove existing fuel oil building on west side of site. Approximately L 50ft x W 30 ft x ht 14 feet concrete building.

7) Proposed Dump site #1 is about 60 ft x 200 ft

8) Proposed Dump site #2 is about 50 square meters, will need to dump equipment etc close to existing wall as future gas line will be installed near this area.

9) Concrete trenches exist on southwest side and one runs through the middle of site. About 2’ wide by 2’ 6” deep. The trench through the middle is full of concrete debris.

10) Security is to be provided by us, there is no problem to run a 24/7 shift if needed

11) Need to run remote control lines to main control room

12) Optional items to be priced as such are: demolition of concrete walls, the Demi system along with tank, move diesel generator and tear down building for additional space.

TM Site looking from North to south. (taken july 7 2009)