From Derwick – Iker e-mail on August 10th, 2010.

We have reviewed the information given by Derwick about the proposal of the liquid fuel and demineralized water supply pumps for the turbo generators GE MS7001EA of PJBA. Hereby we present the following comments:

Clean fuel bombs for turbo generators I and II

First and for most, and based on the Preliminary General Flow Diagram (DWG N° 409-2956-GFL Rev. 0),  the clean fuel pumps for the turbo generators are the so called Liquid Fuel Forwarding Skid #1 and #2 (named in our engineering as  pumps P-1004 A/S y P-1005 A/S).  Then, in the Preliminary Liquid Fuel Forwarding Pump Skid-7EA General Arrangement (DWG N° SLFFPD7EA-900 Rev. B) document you can observe the skid built by two parallel pumps, from which we assume 1 should be 1 in operation and the other on standby. The skid shown would apply for the Skids #1 and #2 pointed in the General Flow Diagram. This is correct. Conduit and cable to a pressure switch on the skid should be provided and installed by the customer. This cable will provide a signal to the DCS or turbine control system that will notify the when the pressure of the header is low so a start signal can be sent to the stand-by pump.

1. According to the Dual Fuel System – Scope of Work document, the pumps are capable of dealing with a power source of 150gpm each, and according to our calculations it requires a 142 gpm. Therefore, the pumps that Derwick suggested are able to manage the fuel required by each turbo generator. The comment is correct. The power supply will need to be specified and provided by the customer.

2. Based on the document mentioned before, and regarding the pump discharge pressure, it can be observed that the proposed pumps would discharge a Max. pressure of 75 psi, and the required pressure according our hydraulic is 106 psi. It would be favorable to consult to Derwick which would be the discharge of their pumps to be able to defeat several pressure losses along a pipe of 4” and 512mts long, in order to give the turbo generators the fuel at the right pressure in the combustion chamber. The pump and motor will be sized to the meet the requirements of the turbine generator and to overcome any pressure losses. At this time the specification for the pump & motor have not been finalized as we needed the pressure loss data that you supplied. The pressure regulation will occur just upstream of the turbine at the liquid fuel management spool which will contain a regulating valve, a flow meter, and a stop valve. The flow control of this system is a back pressure regulating valve at the discharge of the pump.

3. Need the minimum suction head on forwarding pumps.

Water Pumps to turbo generators I and II

In the same matter, and based in the Preliminary General Flow Diagram given (DWG N° 409-2956-GFL Rev. 0) the proposed pumps are called Demin Water Forwarding Skid #1 and #2 (called in our engineering as the pumps P-0403 A/B/C/S, having C for the future for the Combined Cycle). Then, in the document Preliminary Demin Water Forwarding Pump Skid-7A General Arrangement (DWG N° SDWFPD7EA-900 Rev. 0)  we can appreciate the skid built by two parallel pumps, assuming  1 in operation and the other on standby, which would will apply on the skid shown on the General Flow Diagram in the Skid #1 and #2. This is correct. Conduit and cable to a pressure switch on the skid should be provided and installed by the customer. This cable will provide a signal to the DCS or turbine control system that will notify when the pressure of the header is low and to send a start signal to the stand-by pump.

1. According to the Dual Fuel System – Scope of Work document, the pumps are capable of dealing with a source of power of 115 gpm each, and according to our calculations only 42.6 gpm are required. Therefore, the pumps offered by Derwick are oversized for the requirements of the project, so we presume that these pumps are designed for the NOx emission control of 42 ppm and not the 150 ppm established in our design. It is important to remark that the design made for the Project, by VEPICA for the intake, pre-treatment, desalinization, demineralization, post-treatment and discharge of water is based for the control of NOx emissions of 150ppm. ProEnergy has designed the forwarding pumps to meet specifications of a typical water injection system for a 7EA DLN 1.0 system. The flow rate provided should not be a problem since the flow is controlled by a back pressure relief valve on the forwarding skid.

2. Regarding the discharge pressures, these ones differ from the ones calculated for the Project. The pressure control is critical at the suction of the high pressure pump in the water injection skid. The forwarding skid is designed to control the pressure to the water injection skid.

3. In addition, they also suggest the Water Injection Skid #1 and #2 units (one booster for each turbo generator) shown in the General Flow Diagram. These units are also designed by Derwick to manage 115 gpm each, which is 3 times more than the required. The high pressure water injection pump is a variable speed drive pump. It has a minimum set point (minimum flow 18 gpm) and a maximum set point. The maximum set point can be adjusted at the site to meet site specific needs.

4. Need minimum suction head on the forwarding pumps and the friction losses expected on piping between the forwarding skid and water injection skid so the pumps and motors can be sized.

Based on the comments previously exposed, we suggest:

1. To consult Derwick the possibility to evaluate their proposal in order to adapt it to the design established for the Project (attached you will find the information of each one of the mentioned pumps).

In case the suggested is not feasible then:

2. Request Derwick the working curves and data sheets of the pumps suggested, and also the booster unit to evaluate if they can operate under the parameters established for the Project. Customer to provide pressure losses for piping designed for each system. ProEnergy will propose pump and motor specification and pump curves for review.

3. Consult to Derwick which would be the discharge pressure of their fuel pumps to defeat pressure losses along the pipe of 4” and 512mts long to deliver the fuel to the turbo generators at the required pressure in the combustion chamber. Same as above.

4. Request Derwick to evaluate the impact that a water decrease would have on the combustion chamber. See attached document.

5. Evaluate the impact that the use of the suggested pumps by Derwick would have over both systems (fuel supplier and demineralized water to the turbo generators).