PROPOSAL

Presented To:

Derwick Associates

for

3 x LM6000 Gas Turbine Equipment

Prepared By

Proposal No. 709-2485

June 15, 2009

This document is privileged and contains confidential information intended for use only by

Derwick Associates.

Table of Contents

1.0	INTRODUCTION	3

2.0	SCOPE OF SUPPLY	3

2.1	Basic Scope Description	3

2.2	Optional Equipment and Services Checklist and Descriptions	7

3.0	LIMITS OF SELLER SCOPE & EXCLUSIONS	10

3.1	Limits of Seller Scope	10

3.2	Exclusions	11

4.0	SCHEDULED DATE(S)	12

5.0	FUEL SPECIFICATIONS	13

6.0	DESIGN CRITERIA	14

7.0	COMMERCIAL TERMS	15

7.1	Validity	15

7.2	Taxes	15

7.3	Price	15

7.4	Payment Schedule	15

7.5	Warranty	16

7.6	Terms & Conditions	16

8.0	SITE SERVICES	16

9.0	FOLLOW UP	16

ATTACHMENT A	GENERAL ARRANGEMENT

ATTACHMENT B	FUEL GAS SPECIFICATION

ATTACHMENT C	NOx WATER PURITY

ATTACHMENT D	LUBE OIL SPECIFICATION

ATTACHMENT E	COMPRESSOR WASH DETERGENT SPECIFICATION

ATTACHMENT F	COMPRESSOR WASH WATER PURITY SPECIFICATION

- INTRODUCTION

ProEnergy Services (“ProEnergy”) is pleased to provide this proposal to Derwick Associates (“Derwick”) for three (3) GE LM6000 PC Gas Turbines.  (1) One Refurbished and (2) Two Never Used.

The GE LM6000 PC is a highly reliable, mid-sized packaged power plant developed for either 50 or 60 hertz applications with design emphasis placed on energy efficiency, availability, performance and maintainability.

- SCOPE OF SUPPLY

  - Basic Scope Description

    - Gas Turbine

General Electric gas turbine model LM6000 is a two-shaft/two-spool engine consisting of a five-stage low pressure compressor, a fourteen-stage high pressure compressor, a two-stage high pressure turbine, and a five-stage low pressure turbine. The engine is equipped with a stainless steel mesh screen in the inlet air stream for "last chance" protection against foreign object damage. The engine is shock mounted and shipped in position, with the exception of the coupling spacer, which is removed and shipped in a separate container.

    - Generator

Air cooled, 2-pole generator operating at 13.8 kV, 60 Hz. Generator is capable of handling Purchaser power requirement throughout a wide ambient temperature range. A cooling water loop and its associated fans and pumps are not required. The generator includes a brushless excitation system with permanent magnet generator. Neutral and line side cubicles are included.

    - Unit Enclosure

The basic equipment package is supplied with weatherproof acoustic enclosures with sound attenuation to an average of 85 dB(A) at 3ft 3 in (1 m) from the face of the equipment at 4 ft 11 in (1.5 m) above ground. The enclosures are completely assembled and mounted over the equipment prior to testing and shipment. The turbine and generator compartment is fully ventilated with belt driven fans. Explosion-proof lighting is provided in both compartments.

    - Gas Turbine / Generator Baseplate

The basic equipment package is supplied with the support structures for the gas turbine generator set consisting of a two-piece skid assembly, which is sectioned between the gas turbine and the generator. The full depth, bolted section is designed to provide the full structural properties of the wide flange I-beams. Full depth crossmembers are utilized to provide for a rigid design that is suitable for installation in earthquake areas (U.S. Seismic Zone 4) as well as providing a convenient structure for transportation. The baseplate support system is enhanced by the installation of a heavy-duty, welded superstructure, which utilize structural tubing for wall columnsand roof beams.

    - Air Inlet System

The basic equipment package is supplied with a modular, multi-stage filtration system consisting of inlet screens, a prefilter and a final barrier filter. All air for ventilation systems is filtered to the same level as turbine combustion air. An evaporative cooling system is included in the basic equipment package scope. Filtered air is silenced before entering the turbine plenum. This design results in a compact arrangement and eliminates the need for Purchaser supplied inlet ducting when the standard design is utilized. Internal lighting of the filter house is provided to facilitate inspection and service.

Package is also supplied with platforms and ladders to service the inlet filter. These items are packaged separately for shipment. Ladders, platforms and stairways to service other portions of the gas turbine generator enclosure are not included. Special or customized filter arrangements can be supplied, and they are quoted on an individual basis.

    - Turbine Exhaust

The basic equipment package is supplied with a circular, axial exhaust outlet with connection flange to facilitate in-line mounting of an HRSG or simple cycle exhaust stack.

    - Fuel System

The basic equipment package is supplied with a natural gas fuel system using an electronically controlled fuel-metering valve. All necessary shutoff valves, piping and instruments between the auxiliary skid connection and the turbine are included. For full-load operation, the gaseous fuel must be supplied to the baseplate at 675 psig±20 (4,658 ±138 kPag). All necessary shutoff valves, piping and instruments between the baseplate connection and the turbine are included. Gas fuel must meet General Electric specification MID-TD-0000-1.

    - Lube Oil Systems

The basic equipment package is supplied with two separate lube oil systems: one for the gas turbine (synthetic oil) and one for the generator (mineral oil). The oil reservoirs and piping are all stainless steel, and the lube oil system valves have stainless steel trim. Each lube oil system has duplex filters, duplex shell and tube coolers, and thermostatically-controlled electric heaters. The coolers, oil reservoir, and filters for each system are mounted on an auxiliary equipment module located next to the gas turbine baseplate.    The auxiliary equipment module provides simplified piping connections and reduces Purchaser's installation time and costs. Purchaser must supply cooling water to the shell and tube coolers. Turbine lube oil must meet MID-TD-0000-6.

    - Electro-Hydraulic Start System

The basic equipment package is supplied with an electric motor driven hydraulic pump assembly, filters, cooler and controls, mounted on the auxiliary equipment module. A hydraulic motor is also mounted on the gas turbine accessory gearbox. Hydraulic hoses are furnished to connect the auxiliary equipment module and the main baseplate.

    - Fire Protection System

The basic equipment package is supplied with a factory installed fire protection system complete with optical flame detection, hydrocarbon sensing and thermal detectors, piping and nozzles in both generator and engine compartments. The fire protection system includes cylinders containing CO2 mounted on a separate skid. A 24 V DC battery and charger to power the fire protection system is also included. All alarms and shutdowns are annunciated at the turbine control panel (TCP). An alarm sounds at the turbine if the gas detectors detect high gas levels, or if the system is preparing to release the CO2. When the system is activated, the package shuts down, and the primary CO2 cylinders are discharged into the turbine and generator compartments via multiple nozzles, and the ventilation dampers automatically close. After a time delay and if required, the reserve supply of CO2 is discharged.

    - Digital Control System

The basic equipment package is supplied with a free-standing control panel suitable for mounting in an indoor, non-hazardous area. The control system features an integrated Woodward MicroNet Plus turbine control system, vibration monitor, digital meter, digital generator protective relay module and an HMI (human machine interface) display of key discrete and analog data. The operator selects HMI displays with convenient touch screen control. Alarm and shutdown events are displayed on the HMI automatically. An Ethernet TCP/IP EGD or RS485 Modbus Port is provided to transmit unit conditions (status, pressures, temperature, etc.) to the Purchaser's distributed control system. Power for the control panel is provided by a dedicated 24V DC battery system with dual 100% capacity chargers, which are shipped separately for installation by others.

    - Generator Protective Relays

The basic equipment package is supplied with a microprocessor-based generator protective relay module, mounted in the TCP. The protective relay system includes functions necessary for protection of the generator.

    - Soak Wash System

The basic equipment package is supplied with a turbine cleaning system, which allows Purchasers to clean the compressor section of the turbine during full power operation. The same system reservoir and piping are utilized for off-line soak washing. Auxiliary skid connections are provided for Purchaser supplied purified water at a maximum of 50 psig (345 kPag) and air at 100 – 120 psig (689 – 827 kPag). Purchaser is required to provide purified water meeting MID-TD-0000-4, detergent meeting MID-TD-0000-5 (See Attachment 16), and air filtered to ISA S7.3 standards.

    - Component Testing and Package Full Load Test

Every new gas turbine is performance tested under load in a GE Test Cell, using procedures developed for flight turbine reliability. The generator is tested to ANSI C50.14 or IEC 34.3 standards at its factory of manufacture.

All gas turbine generator sets receive a rigorous 400-point static test including:

- Switch State (N.O. or N.C., actuation, wiring, and setpoint)

- Temperature element output, and wiring

- Transmitter range, output, and wiring

- Solenoid operation

- Control valve torque motor, excitation, and return signal

- Fire system continuity, and device actuation

- System flushing verification

- Tubing integrity

    - Drawings, Data and Manuals

The basic equipment package is supplied with a Purchaser drawing package that includes general arrangement drawings, flow and instrument diagrams, electrical one-line drawings and interconnection plan drawings. Additional electrical schematic diagrams and logic drawings are provided for record.

Maintenance manuals are provided and are printed in English. The manuals cover operating concepts for power generating equipment, guides to troubleshooting, basic information on components, and equipment within the turbine generator set.

    - Training (Optional)

The base scope of supply includes hands-on training for up to 10 operators and supervisors, where students are assumed to have at least a journeyman's knowledge of electrical generating plant operation and to be proficient in reading piping flow and instrument drawings, mechanical drawings, and have a working knowledge of electrical generators, and gas turbines. The course is designed around an eight-hour day, five consecutive day schedule with an hour lunch break and fifteen-minute breaks every one and one half hours. Experienced instructors, using specially developed training materials, provide a firm groundwork of basic theory, plus advanced concepts with classroom and hands-on training. Training includes Gas Turbine Familiarization plus System Design & Operations and Maintenance.

    - Improvements and Changes

It is understood that the Seller has the right to make changes in product design and add improvements to products or services at any time without incurring any obligations to install the same on or in connection with the Equipment or Services provided hereunder.

  - Optional Equipment and Services Checklist and Descriptions

(I) included in base offer at prices indicated in Article 3

    - Factory Options

| I | Option A | SPRINT® Power Augmentation |
| --- | --- | --- |
| I | Option B | NOx Control - Water Injection System |
| I | Option C | Inlet Air Cooling – Evaporative Cooling |
| I | Option D | Lube Oil Cooler - Fin/Fan |
| I | Option E | Left-handed Piping Connections |
| I | Option F | Left-handed Lineside Cubicle |
| I | Option G | Lineside Cubicle Entry Configuration Options |
| I | Option H | DC Backup Lighting |
| I | N/A | Auxiliary Skid Enclosure |

    - Factory Options Descriptions

Option A        SPRINT® Power Augmentation

SPRINT® boosts engine performance using a demineralized water spray intercooling design that significantly increases the mass flow by cooling the air during the compression process. The system is based on an atomized water spray injected through spray nozzles placed at two locations, one between the high pressure and low-pressure compressors, and the second at inlet bellmouth. Water is atomized using high-pressure air taken off of the eighth stage bleed. The water flow rate is metered, using the appropriate engine control schedules and at the inlet bellmouth. Bellmouth and inter-stage portions on SPRINT® alternate operation based on turbine inlet temperature. Purchaser supplies 30 gpm (114 lpm) of demineralized water to the connection on the unit. Water must meet GE specification MID-TD-0000-3 (See Attachment 16)

Option B        NOx Control - Water Injection System

A water injection system for control of NOx emissions shall be provided. The demineralized water injection system consists of inlet strainer, pump, valves, piping and controls for use with a gaseous fuel, liquid fuel or dual fuel system. Water injection shall reduce NOx emissions to 25 ppm (51 mg/N m3) (Ref. 15% O2) on gaseous fuel. For gaseous fuel applications, Purchaser must provide a demineralized water supply of up to 55 gpm (208 lpm) and at 20-40 psig (138-276 kPag). Water must meet GE specification MID-TD-0000-3 (See Attachment 16). The minimum Purchaser supplied pressure and temperature is determined by the water injection rate required and the type of fuel nozzle utilized.

Option C        Inlet Air Cooling – Evaporative Cooling

Evaporative cooling shall be utilized in the inlet air cooling system to lower the dry bulb temperature of the inlet ambient air, thus increasing power output of the LM6000 equipment.

This system is designed for recirculation of evaporative cooling water from a sump in the bottom of the inlet air filter. A recirculation pump, a conductivity probe, blowdown and make-up valves, piping and wiring shall be provided. Purchaser must supply filtered, potable water to a flanged connection on the filter house and must dispose of wastewater from the blowdown valve. Flow rates will vary based on blow down. Water must meet GE specification GEK 107158.

Option D       Lube Oil Cooler - Fin/Fan

This replaces the standard simplex shell and tube coolers for the lube oil systems. A simplex core fin-fan cooler complete with changeover valve mounted on a separate base plate with dual fans is installed on a separate foundation.

Option E        Left-handed Piping Connections

The Seller shall furnish one (1) right hand (standard) configuration and one (1) left hand configuration LM6000 Unit. The left hand Unit shall be built with the Purchaser's piping connections on the left side, as viewed from the exciter. The turbine removal door is placed on the side opposite the piping connections.

Option F        Left-handed Lineside Cubicle

For the left hand Unit, the generator line-side cubicle shall be located on the left-hand side and the neutral cubicle shall be located on the right-hand side. However, the termination box for generator instrument and control wiring box, (MGTB) must remain on the right-hand side, and the turbine main terminal box (MTTB) must remain on the left.

Option G       Lineside Cubicle Entry Configuration Options

Top Bus Duct Entry

The standard lineside cubicle is configured for bottom cable entry. With this option, the lineside cubicle is configured for top bus duct entry.

Top Cable Entry

The standard lineside cubicle is configured for bottom cable entry. With this option, the lineside cubicle is configured for top cable entry.

NOTE for Option E, Option F, Option G:

Purchaser has elected to choose quantity one (1) Unit to be “Left-hand” configuration and one (1) Unit to be “Right-hand” configuration as described above. Configurations and delivery sequence to be finalized at the Order Definition Meeting. If the configuration or delivery sequence is changed after the Order Definition Meeting, Seller reserves the right to adjust Contract price and schedule accordingly.

Option H       DC Backup Lighting

Seller shall furnish DC backup lighting in the turbine and generator enclosures as an option. The DC lights turn on anytime the normal AC power fails.

Option I	Combustion Air Cooling – Chiller Coil

Lowering the combustion air inlet temperature can increase the power output of the LM6000 generator set. When specified, GE Energy can furnish high performance inlet air chilling coils as an integral part of the air inlet system. Purchaser provides adequate quantities of chilled water and interconnecting piping to GE Energy furnished chilling coils at the filter house. The same coils can be used for anti-icing.

(Option)    Transportation Services

Seller arranges for shipment on behalf of the Buyer. The Buyer pays the Seller for all fees and expenses including, but not limited to, those covering preparation of consular documents, freight, loading fees at storage, storage, transit insurance and warehouse-to-warehouse insurance.

- LIMITS OF SELLER SCOPE & EXCLUSIONS

  - Limits of Seller Scope

Listed below are the limits/exclusions to the Seller standard Scope of Supply. All piping, wiring, cables, ducts, etc. connecting to these points is furnished by Purchaser (others) unless modified by specification agreement.

| Equipment System | Limits of Seller Scope |
| --- | --- |
| All piping, including Fuel Gas, Fuel Oil, Steam, Cooling Water, Heating Water, Demineralized Water, Lube Oil, Compressed Air, Instrument Air, Hydraulic Start Oil | Flanged or threaded connection on Seller baseplate. |
| Inlet Air-to-Filter | Atmosphere (non-standard duct by others) |
| Turbine Package Ventilation/Cooling Air | Atmosphere (non-standard duct by others) |
| Turbine Exhaust | Exhaust flange on main baseplate |
| Instruments on Seller’s Baseplate | Terminal box on baseplate |
| Instrument wiring in Turbine Control Panel | Wiring Terminal block in Turbine Control Panel |
| High Voltage Connections | Bus bar in Seller Lineside cubicle |
| Generator Ground Connections | Seller Neutral cubicle |
| Electric Motors | Terminal box on individual motor |
| Ladders and Platforms for Air Filter | Ladders and Platforms for Inlet Air Filter maintenance only |
| 24 V DC Batteries and Chargers for Control System and Fire and Gas Systems | Battery terminals to baseplate (if supplied loose) |

  - Exclusions

- Civil engineering design of any kind

- Building and civil works

- Site facilities

- Drains and/or vent piping from the gas turbine package to a remote point

- Fuel storage, treatment and forwarding system

- Site grounding

- Lightning protection

- Power system studies

- Sensing and metering voltage transformers

- Machine power transformers, and associated protection

- Grid failure detection equipment

- Off-loading, transportation and storage

- Off-skid cabling, and design of off-skid cable routing

- Balance of plant and energy optimization controls

- Anchor bolts, embedments, and grouting (quoted separately)

- Distributed plant control

- Purchaser's remote control

- Field supervision (quoted separately)

- High voltage transformer(s), cables, and associated equipment

- Interconnecting piping, conduit, and wiring between equipment modules

- Plant utilities, including compressed air supply and off-skid piping

- Battery containment

- Lube oil measurement other than that defined in the scope of supply

- Additional lube oil breather ducting other than that defined in the scope of supply

- Fuel transfer pump

- Off-skid fuel block and vent valves

- Fuel supply pipework beyond the scope of supply

- Generator controls other than that defined in the scope of supply

- Load sharing control

- Balance of plant controls

- Field Performance Testing

- Site Labor

- Ladders, Stairs, and Platforms for equipment beyond the gas turbine

- SCHEDULED DATE(S)

| Reference | Equipment Description | Scheduled Date |
| --- | --- | --- |
| Unit 1&2 | LM6000PC Generating Set (Never Used) | 90 Days From Contract |
| Unit 3 | LM6000PC Generating Set (Refurbished) | 120 Days From Contract |

- FUEL SPECIFICATIONS

GE Aero Derivative gas turbines have the ability to burn a wide range of gaseous fuels as shown in Table 1. These gases present a broad spectrum of properties due to both active and inert components. This specification is designed to define guidelines that must be followed in order to burn these fuels in an efficient, trouble-free manner, while protecting the gas turbine and supporting hardware.

| Table 1 Fuel Gas Usability |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Fuel Type | LHV Btu/SCF (kJ/NM3) | Wobbe Number | Major Components | Operational Comments | Applicability SAC DLE |  |
| Pipeline Natural Gas | 850-1200 (33383-47128) | 45-60 | Methane | No Restrictions | Yes | Yes |
| Medium BTU Natural Gas | 400 - 850 (15709-33838) | 20-45 | Methane, Hydrocarbons (HC), carbon dioxide, Nitrogen | Requires > 700 BTU/scf (27492 kJ/NM3) for starting. May require modified fuel nozzles. Contact GE | Yes | No, See Note 8. |
| Liquefied Petroleum Gas (LPG) | 2300- 3200 (90330- 125676) | 70-75 | Propane, Butane | May require specific fuel nozzles. Contact GE | Yes | No |
| Gasification Gases - Air Blown - Oxygen Blown | 150-200 (5891- 7855) 200- 400 (7855-15709) | 6-8 8-20 | Carbon monoxide, Hydrogen, HC, Nitrogen, Water Vapor Carbon monoxide, Hydrogen, HC, Water Vapor | Contact GE Contact GE | Yes Yes | No No |
| Process Gases | 300-1000 (11782-39274) | 15-50 | Methane, Hydrogen, Carbon monoxide, Carbon dioxide | Requires >700 BTU/scf (27492 kJ/NM3) for starting. Restricted transient operation. | Yes | See Note 8 |
| Refinery Gases | 1000- 1300 (39274- 51056 | 45-60 | Methane, Hydrogen, Carbon monoxide, Ethylene, Propylene, Butylene | No restrictions. Hydrogen content should be reviewed by GE. | Yes | See Note 8 |

Notes:

- When considering the use of alternate fuels, provide details of the fuel constituents, fuel temperature, and expected engine usage conditions and operating characteristics to GE for evaluation and recommendations.

- Values and limits apply at the inlet of the gas fuel control module.

- DESIGN CRITERIA

The following table outlines the criteria conditions at the proposed jobsite for the design of the equipment:

| Location | TBD |
| --- | --- |
| Elevation | TBD |
| Design Point Ambient Temperature / Relative Humidity | TBD |
| Primary Fuel Source | TBD |
| Secondary Fuel Source | TBD |
| Seismic Design Criteria (BOP Equipment) | TBD |
| Maximum Wind Speed (Wind Load), MPH | TBD |
| Near Field Noise at 3 ft horizontal and 5 ft vertical, dBA NOTE 1 | TBD |
| Far Field Noise, dBA NOTE 1 | TBD at 400 ft / TBD at 700 ft |

NOTE:

- Far field noise is based on single-unit only operation.  Multiple units operating at the same time will have an impact on both near and far field noise levels.

- COMMERCIAL TERMS

  - Validity

This proposal is valid until July 15, 2009. Subject to prior Sale.

  - Taxes

No sales or use taxes have been included in this quotation.  These prices quoted exclude any federal, state or local taxes or fees which may be associated with the export, import or purchase of equipment and/or services.

  - Price

Three (3) GE LM6000 Gas Turbine Generator Set including optional equipment specified as included (I) as described in the scope of supply.  All pricing is based on ex-works factory delivery unless otherwise stated.

GTG UNIT

Generators set price (Three Units)……………….US$50,500,000

  - Payment Schedule

This proposal is based upon receipt of the following progress payments and a Contract Agreement by both Parties by the Validity date Seller may request at any time, Purchaser will demonstrate its financial capability to continue to carry out its obligations under this Contract.  This demonstration may require that Purchaser furnish adequate payment security.

|  | Payment Event | % of Equipment Price |
| --- | --- | --- |
| 1 | Within five days of signature of the Contract Agreement by both Parties, paid against Seller’s invoice. | 20% |
| 2 | In equal monthly installments, commencing thirty days following signature of the Contract Agreement until thirty days before the first scheduled Shipment Date, paid against Seller’s invoices. | 70% |
| 3 | Upon notice of Ready to Ship, pro-rata by shipment (See terms below) | 10% |

Name:  ProEnergy Services LLC

Bank:  US Bank

Routing # 081000210

Account # 152305958703

Swift Code:  USBKUS 44IMT (that is an “i” not a 1)

On the Notice of Readiness to Ship Milestone, payment must be received at least 5 days before shipment, but no later than 15 or 30 days [depending on terms] from notification of Readiness to Ship.

  - Warranty

ProEnergy will provide a one (1) year warranty on the entire gas turbine generator package and any other balance of plant equipment provided.

  - Terms & Conditions

This proposal shall be valid for thirty (30) days; provided, however, the obligation to treat this proposal as confidential, and that it cannot be shared with any third party without the prior written consent of ProEnergy shall survive.

ProEnergy and Derwick will negotiate in good faith to establish general terms and conditions that are usual and customary of the sale of used equipment.

- SITE SERVICES

ProEnergy would be pleased to also provide a proposal for the installation, startup and commissioning of the facility.  This would include providing construction supervision as well as startup engineers for all equipment provided.

ProEnergy can also provide an experienced service representative to assist the operating personnel during the first two (2) months after the equipment goes online.

- FOLLOW UP

Please contact the following person at ProEnergy for information regarding this proposal:

Joaquin Mavares, Director of International Sales

jmavares@proenergyservices.com

Office:  660.829.5100

Cell:  	 713.992.1790

- ATTACHMENT A

- GENERAL ARRANGEMENT

- ATTACHMENT B

- FUEL GAS SPECIFICATION

- ATTACHMENT C

- NOx WATER PURITY

- ATTACHMENT D

- LUBE OIL SPECIFICATION

- ATTACHMENT E

- COMPRESSOR WASH DETERGENT SPECIFICATION

- ATTACHMENT F

- COMPRESSOR WASH WATER PURITY SPECIFICATION