Package Inspection Report

Client: EDC - LM6000 PD

ProEnergy Field Services has been retained by EDC (Owner) to provide an inspection of a GE LM6000 PD Gas Turbine Generator package. The LM6000 package was recently purchased by the owner from Wood Group and delivered to the Port in Houston, Texas. The following information included in this report is based upon ProEnergy’s vast experience and familiarity of the LM6000 equipment.

General Information

The GE LM6000 Gas Turbine Generator package was built in 2002 by GE under the following package identification numbers:

Work Order number 312415

Gas Turbine Serial number _192-222__

A complete inventory list of the components is included as Attachment A. We have identified those parts which are missing from a standard GE LM6000 package inventory list and will need to be replaced in order to have a complete operational unit.

The unit has two primary enclosures, which house the gas turbine and generator, and are the most critical for proper operation of the unit. We have broken this report into 4 sections to address the concerns or issues of those critical areas:

- Generator Enclosure

- Gas Turbine Enclosure

- Package Inventory – Attachment “A”

  - Missing Parts

- Pricing

Generator Enclosure

The Generator enclosure was visually inspected both externally and internally. Based on this inspection we could not locate any areas of concern. The package was dry and clean internally and all pipes and cables were sealed properly. The package has not been damaged during shipping and appears in good condition.  Generator Enclosure pictures are below:

Generator Internal – MGTB location

Gas Turbine Enclosure

The Gas Turbine Enclosure was visually inspected both externally and internally. Based on this inspection there were numerous areas of damage to report.

It appears the package was hit externally in numerous locations causing roof panels to separate and allow water in enter the package. This is a real concern since many of the cables were under water and pipes uncovered and exposed to allow water to enter. This will require a complete package cleaning and all cables and pipes tested and cleaned. Some Cables may require replacement if water has migrated into the cable. This is further indicated in the External pictures.

Is was also note some of the primary damage occurred because the internal bridge crane was not properly lock down and secured prior to transportation. During the transport the bridge crane appeared to move in both front and back and side to side causing damage to numerous items in internal to the package. This further indicated in the internal pictures.

External:

- One wall panel has 3” diameter, 2” deep indention where it was hit by something. Repair or replace.

- One corner angle flashing damaged on right front corner - Replace

One wall panel has 3” diameter, 2” deep indention where it was hit by something. Repair or replace.

One corner angle flashing damaged on right front corner - Replace

Internal:

- Light broke off and mounting bracket damaged – Replace both

- Side walls need repaired or replaced

- Overhead hoist/crane;

  - Trolley is off end of beam but not damaged. Repair

  - Chain wheel on hoist trolley damaged – replace

  - Chain guide for crane trolley broke – replace

- Emergency Stop mounting bracket bent – Straighten

- Skid pan has 3” of water in it – remove water and clean

- Pan area and enclosure piping will need lot of cleaning and some touch painting.

- Front Turbine Pedestals base plates are rusted bad – Cleaned and polished

- Engine Cable cannon plug were laying in the water – Cleaned, checked or possibly replaced.

- Two 4 ft. wide wall panels perf. Damaged slightly by hoist.

- VBV duct needs touch of painting and has one corner bent slightly – Repair

- Inside enclosure needs lots of cleaning and touch up painting.

Light broke off and mounting bracket damaged – Replace both

Light broke off and mounting bracket damaged – Replace both

Chain guide for crane trolley broke – replace

Chain wheel on hoist trolley damaged – replace

Trolley is off end of beam but not damaged. Repair

Water inside inlet bell mouth - clean

Front Turbine Pedestals base plates are rusted bad – Cleaned and polished

Front Turbine Pedestals base plates are rusted bad – Cleaned and polished

Valves need to be cleaned and tested – possibly replace due to water damage

Valves need to be cleaned and tested – possibly replace due to water damage

Pan area and enclosure piping will need lot of cleaning and some touch painting.

Pan area and enclosure piping will need lot of cleaning and some touch painting.

Emergency Stop mounting bracket bent – Straighten

Engine Cable cannon plug were laying in the water – Cleaned, checked or possibly replaced. Pan area and enclosure piping will need lot of cleaning and some touch painting.

Engine Cable cannon plug were laying in the water – Cleaned, checked or possibly replaced.

Package Inventory

ProEnergy performed a complete inventory of all enclosures, skids and boxes associated with the LM6000 PD Gas Turbine Generator package. Based on the inspection the following are reported missing from the overall package inventory needed to have a complete unit:

Missing parts:

- Box # 3  H-Frame

- Box 8     VBV Expansion Joint

- Box 11   Alignment Tool

- Box 12   Engine Lift fixture

- Box 15   Gen Lube Oil piping

- Box 43   Paint

- Box 59   Transformer(no description on p/l on what type/size)

- Box 60   Batteries are present but probably need to be replaced-shelf life

- Box 61   Battery Chargers (3) 1 ea  H221N Switch, safety, SGL Throw, 30 amp. 1 ea H224N Disconnect, Safety. 2 ea TR125R Fuses, 125 amp, 125 VDC rated. 2ea TR30R, 30 amp, 125 VDC rated

- Box 62   Acid

- Box 66   CO2 Bottles

- Box 90   Calorimeter

- Box 88   DLE Pipe Missing the following from p/l:

- 1 ea Pipe 3” 600# one end, and 6” 600# one end.

- 1 ea Hanger rods, all thd ½-13NC, SS-P/N Fig. 122 ½”SS Item 0122

- Box 16 Generator run down tanks, missing the following items:

- 2 ea 4-3/4” SS Tube for Run down tanks

- 1 ea 1”Tubex3/4” MNPT 90 Deg (16LM12)

- 2  ea ¾”Tubesx3/4” MNPT 90 Deg (12LM12)

- 1 ea ¾” Tubex3/4” Tube 90 deg (12LU)

- 2 ea ¾” MJICxMNPT x FNPT (2611-12-12-12)

- 2 ea ¾” Tube x ¾” MNPT straight (12CM12)

- 1 ea 1” tube x ¾” MNPT (16CM12)

- 2 ea ¾” MJIC x MNPT (2404-12-12 316)

- 1 ea 1” Union 90 deg (16LU)

- 4 ea Havit Flanges Gasket Kit (SKV-100-SS)

- 4 ea 3/8” Tube x ½” MNPT 90 deg (6LM8)

- 4 ea Havit Flanges (7308-12-12-08)

Pricing

Due to the unknown condition of some items we can not provide a fixed price for material cost or replacement of missing inventory items at this time. Based on the inspection report and items identified for repair or replace we provide the following cost estimate:

- Labor for package clean-up, testing and repairs – 1068 hours (estimated) at $125.00  per hour plus T&L –  $165,000 (estimated)

- Equipment rental - $35,000 (estimated)

- Material – Cost plus 25% fee/mark-up

- Warehouse / Shop area rental - $55,000 (estimated)

- Shipping Equipment/Package from Port to Warehouse/Storage Area - $70,000 one way (estimated) The removal of equipment from the port will be necessary to facilitate any repairs process; as this cannot be performed in the port terminal efficiently and economically.

Should you have any questions please do not hesitate to contact Joaquin Mavares or myself.

Sincere Regards,

Michael Pollock
Manager of Aero Turbine Services
ProEnergy Services
2031 Adams Rd
Sedalia, Missouri 65301
660-829-5100 office
660-829-1160 fax
660-287-7678 cell

email mpollock@proenergyservices.com