## Recap
Pro Energy EPC
Job Description: |  | "Two LM 2500 Simple Cycle"
US & Local Split
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
[9 empty] | US | Local
I. Balance of Plant
1.0 Civil - Structual
|  | 1.1 Site Preparation |  |  |  | 71.3148
|  | 1.2 Excavation - Fill |  |  |  | 17.7778
|  | 1.3 Concrete Foundations |  |  |  | 954.3685
|  | 1.4 Concrete Pilings |  |  |  | 141.6667
|  | 1.5 Paving Asphalt - Concrete |  |  |  | 352.9333
|  | 1.6 Gravel - Sand |  |  |  | 41.377
|  | 1.7 Structual Steel |  |  |  | 86
|  | 1.8 Fencing |  |  |  | 47.7
|  | 1.9 Architectual Treatment |  |  |  | 0
|  | 1.9 Evaporation Pond |  |  |  | 0
[6 empty] | 1713.1381 |  | 1713.1381 |  | 1713.1381
2.0 Buildings
|  | 2.1 Various Bldgs |  |  |  | 142
0
[6 empty] | 142 |  | 142 | 90 | 126
3.0 Mechanical
|  | 3.1 Major Mechanical Equipment |  |  |  | 1760
|  | 3.2 Pipelines |  |  |  | 0
|  | 3.3 Mechanical Subcontractor |  |  |  | 1054.8765
[6 empty] | 2814.8765 |  | 2814.8765 | 1760 | 1054.8765
4.0 Electrical
|  | 4.1 Major Electrical Equipment |  |  |  | 1780.1
|  | 4.2 Substation Equipment |  |  |  | 356.2
|  | 4.3 Plant Electrical Subcontractor |  |  |  | 1250.3988
|  | 4.4 Substation Subcontractor |  |  |  | 29.904
[6 empty] | 3416.6028 |  | 3416.6028 | 2136.3 | 1280.3028
5.0 Instrumentation
|  | 5.1 Cems |  |  |  | 0
|  | 5.2 Plant Instrumentation |  |  |  | 125
|  | 5.3 Instrumentation Subcontractor |  |  |  | 0
[6 empty] | 125 |  | 125 | 125
6.0 DCS System
|  | 6.1 Hardware |  |  |  | 85
|  | 6.2 Software |  |  |  | 60.02
[6 empty] | 145.02 |  | 145.02 | 145.02
7.0 Plant Erection
|  | 7.1 Plant Erection |  |  |  | 194.4
[6 empty] | 194.4 |  | 194.4 |  | 194.4
8.0 Equipment Rental
|  | 8.2 Plant Equipment Rental |  |  |  | 464.7
[6 empty] | 464.7 |  | 464.7 |  | 464.7
| 9.0 Painting |  |  |  |  | 140 |  | 140 |  | 140
10.0 Transportation
|  | 10.1 Plant US Transport w/ crating |  |  |  | 0
|  | 10.1 Ocean Frt BOP |  |  |  | 0
[6 empty] | 0 |  | 0 | 0
| 11.0 Site Costs |  |  |  |  | 270.5 |  | 270.5 |  | 270.5
12.0 Engineering
|  | 12.1 EPC Eng Labor |  |  |  | 610
|  | 12.2 Local Eng |  |  |  | 70
|  | 12.3 Eng Travel & Per Diem |  |  |  | 89
[6 empty] | 769 |  | 769 | 699 | 70
13.0 Project Management
|  | 13.1 Project - Inspectors - Commissioning Lab |  |  |  | 1120
|  | 13.2 Travel & Per Diem |  |  |  | 284.5
[6 empty] | 1404.5 |  | 1404.5 | 1404.5
14.0 Technical Reps
|  | 14.1 GTG Tech Rep |  | 90 | 2200 | 198000
|  | 14.2 Fire Water |  | 0 | 2200 | 0
|  | 14.3 Gas Compressor |  | 20 | 2000 | 40000
|  | 14.4 Evap Cooler Pkg |  | 0 | 2000 | 0
|  | 14.5 Water Treatment |  | 15 | 2000 | 30000
|  | 14.6 Centrifuge |  | 15 | 2000 | 30000
|  | 14.7 Controls Rep |  | 90 | 2000 | 180000
|  | 14.8 Commissioning Start |  | 60 | 2200 | 132000
[6 empty] | 610 |  | 610 | 610
15.0 Project Tests
|  | 15.1 Soils Compaction |  |  |  | 15
|  | 15.2 Concrete Testing |  |  |  | 40
|  | 15.3 X Ray |  |  |  | 40
|  | 15.4 Plant Performance and Reliability |  |  |  | 75
|  | 15.5 Noise Emission Tests |  |  |  | 0
|  | 15.6 Protective Relays |  |  |  | 15
[6 empty] | 185 |  | 185 | 90 | 95
| 16.0 Legal |  |  |  |  | 50 |  | 50 | 50
17.0 Insurance
|  | 17.1 Project Insurance |  |  |  | 250 |  | 250 | 250
| 18.0 Performance Bond |  |  |  |  | 0 |  | 0
| 19.0 Project Contingency/Risk |  |  | 2.5% |  | 12694.7374 |  | 317.3684 | 317.3684
| 20.0 Sales Tax |  |  |  |  | 0 |  | 0
21.0 Commissions
|  |  |  | BOP Cost |  |  |  | 13012.1058 | 7677.1884 | 5408.9174
|  |  |  | % Markup |  |  |  | 4200 | 4200
|  |  |  | BOP Sales Price |  |  |  | 17212.1058 | 11877.1884 | 5408.9174
|  |  |  | 2% | Commission |  |  | 344.2421 | 344.2421
[6 empty] | 16100 |  | 17556.3479 | 12221.4306 | 5408.9174
|  |  |  | Actual Sales Price |  |  |  |  | 12536000
|  |  |  | Bolivar Conversion |  |  |  |  | 26952400 | 10218950
|  |  |  | Social Welfare Tax |  | 2.5% |  | 929283.75 | 673810 | 255473.75

## 1.1 Site Prep
|  |  | SITE PREP | [6 empty] | 1.1
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [5 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [5 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [5 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | "L" | "W" | "D" | Square | Square | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Site No. 1 |  |  | 80 | 200 | 1.5 | 24000 | 888.8889 | 15 | 13333.3333
2 | Site No. 2 |  |  | 0 | 150 | 1.5 | 0 | 0 | 15 | 0
3 | [9 empty] | 0
4 | Demolition Site No. 1
5 | Remove exist asphalt |  |  | 50 | 90 | 0.3 | 1350 | 50 | 50 | 2500
6 | Demolish exist wall |  |  | 50 | 10 | 1 | 500 | 18.5185 | 80 | 1481.4815
7 | Demolish Control barrier oil |  |  | 0 | 40 | 1 | 0 | 0 | 100 | 0
8 | Demolish Oil Piping | [5 empty] | 0 | 0 |  | 5000
9 | Relocate exist elect discs | [5 empty] | 0 | 0 |  | 4000
10 | Relocate exist Fire H2O Pump | [5 empty] | 0 | 0 |  | 10000
11
12 | Demolition Site No 2
13 | Remove exist asphalt |  |  | 0 | 150 | 0.3 | 0 | 0 | 50 | 0
14 | Demolish exist wall |  |  | 0 | 10 | 1 | 0 | 0 | 80 | 0
15 | Demolish exist concrete tank |  |  | 0 | 40 | 2 | 0 | 0 | 100 | 0
16 | Demolish exist elect structure | [5 empty] | 0 | 0 |  | 5000
17 | Relocate 69 KV Duct Bank |  |  | 0 | 6 | 6 | 0 | 0 | 300 | 0
18 | New 69 KV Cabling |  |  | 0 | 0 |  | 0 | 0 | 0 | 30000
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
71.3148

## 1.2 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 1.2
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [6 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [6 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [6 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
| Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Control/Office/Maint |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Water Treatment Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Pwr Blk Utility Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Liquid Fuel Unloading Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
12
2 | Site No. 1 |  |  |  | 80 | 200 | 2 | 32000 | 1185.1852 | 15 | 17777.7778
3 | Site No. 2 |  |  |  | 0 | 150 | 2 | 0 | 0 | 15 | 0
4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Excavation and Fill | [7 empty] | 17.7778
Evaporation Pond - Option 1 - RO w/EDI Water Treatment w/pond
[5 empty] | 675 | 200 | 5 | 135000 | 25000 | 2.5 | 62500 | 0 | 0 | 62500
Evaporation Pond - Option 2 - Deionizing trailers w/pond
[5 empty] | 475 | 200 | 5 | 95000 | 17592.5926 | 2.5 | 43981.4815 | 0 | 0 | 43981.4815

## 1.3 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 1.3
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [7 empty] | Date: | 2009-04-23
Customer: |  | EDC | [7 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total | 5
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price | mhr/cy
1 | POWER ISLAND
| GT Generators |  |  | 2 | 80 | 20 | 4 | 12800 | 474.0741 | 650 | 308148.1481 | 2370.3704
| Exhaust Stack |  |  | 2 | 25 | 25 | 4 | 5000 | 185.1852 | 650 | 120370.3704 | 925.9259
| HRSG |  |  | 0 | 75 | 16 | 4 | 0 | 0 | 650 | 0 | 0
| SCR |  |  | 0 | 52 | 16 | 4 | 0 | 0 | 650 | 0 | 0
| STG |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| STG Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| STG Inlet Chillers |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| GTG Fin Fan Coolers |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 650 | 10833.3333 | 83.3333
| Aux Skid(s) for GTG |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 650 | 10833.3333 | 83.3333
650
650
2 | BALANCE OF PLANT | [8 empty] | 650
| Chiller Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| Fuel Gas Regulator Skid |  |  | 2 | 15 | 8 | 1 | 240 | 8.8889 | 650 | 5777.7778 | 44.4444
| Fuel Gas GTG Meter Skid |  |  | 0 | 25 | 6 | 1 | 0 | 0 | 650 | 0 | 0
| Fin Fan L O Coolers |  |  | 0 | 15 | 15 | 2 | 0 | 0 | 650 | 0 | 0
| Gas Compressors |  |  | 3 | 45 | 15 | 3 | 6075 | 225 | 650 | 146250 | 1125
| Fuel Gas Plant Metering Skid |  |  | 1 | 20 | 8 | 1 | 160 | 5.9259 | 650 | 3851.8519 | 29.6296
| Comp Fin Fans |  |  | 3 | 15 | 15 | 1 | 675 | 25 | 650 | 16250 | 125
| Waste Oil/Water Storage Tank |  |  | 1 | 15 | 12 | 1 | 180 | 6.6667 | 650 | 4333.3333 | 33.3333
| Oily Water Separator |  |  | 1 | 30 | 20 | 0.5 | 300 | 11.1111 | 650 | 7222.2222 | 55.5556
| Lubricant Storage Area |  |  | 0 | 45 | 30 | 1 | 0 | 0 | 650 | 0 | 0
| Instrument Air Comp Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 650 | 1925.9259 | 14.8148
| Pipe Rack Stanchons |  |  | 12 | 2.5 | 2.5 | 6 | 450 | 16.6667 | 650 | 10833.3333 | 83.3333
| 15KV Cable Tray Stanchons |  |  | 0 | 2.5 | 2.5 | 6 | 0 | 0 | 650 | 0 | 0
| Fire Water Pump Skid |  |  | 0 | 15 | 30 | 1 | 0 | 0 | 650 | 0 | 0
| Area Light Poles |  |  | 4 | 2.5 | 3 | 5 | 150 | 5.5556 | 650 | 3611.1111 | 27.7778
| Aux Trans fndns |  |  | 3 | 10 | 15 | 1.5 | 675 | 25 | 650 | 16250 | 125
| Cable Trenches see est |  |  | 2 | 250 | 12 | 0.5 | 3000 | 111.1111 | 650 | 72222.2222 | 555.5556
| Water Treatment Plant |  |  | 1 | 60 | 40 | 0.7 | 1680 | 62.2222 | 650 | 40444.4444 | 311.1111
| Centrifuge Skid |  |  | 2 | 8 | 8 | 2 | 256 | 9.4815 | 650 | 6162.963 | 47.4074
| Liquid Fuel Day Tank |  |  | 3 | 15 | 15 | 1 | 675 | 25 | 650 | 16250 | 125
| Liquid Fuel forward pumps |  |  | 5 | 4 | 8 | 1 | 160 | 5.9259 | 650 | 3851.8519 | 29.6296
| Demin Water Pump skid |  |  | 4 | 8 | 6 | 1 | 192 | 7.1111 | 650 | 4622.2222 | 35.5556
| Demin Stg Tanks ____ Gal |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 650 | 10833.3333 | 83.3333
| Demin Forwarding Pumps |  |  | 1 | 8 | 5 | 1 | 40 | 1.4815 | 650 | 962.963 | 7.4074
| Chemical Injection Skid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| Raw Water Tank Base |  |  | 1 | 15 | 15 | 1 | 225 | 8.3333 | 650 | 5416.6667 | 41.6667
| Fire Water Tank base |  |  | 0 | 35 | 20 | 1 | 0 | 0 | 650 | 0 | 0
| Emer Generator Base |  |  | 1 | 25 | 12 | 2 | 600 | 22.2222 | 650 | 14444.4444 | 111.1111
650
3 | BUILDINGS | [8 empty] | 650
| Control Bldg/Office |  |  | 0 | 60 | 60 | 1 | 0 | 0 | 650 | 0 | 0
| Warehouse/Maintenance |  |  | 0 | 75 | 60 | 1 | 0 | 0 | 650 | 0 | 0
| Water Treatment Bldg |  |  | 1 | 25 | 40 | 1 | 1000 | 40 | 650 | 26000 | 200
| Compressor Shed |  |  | 1 | 55 | 35 | 1 | 1925 | 40 | 650 | 26000 | 200
| Electrical Bldg |  |  | 1 | 35 | 15 | 1 | 525 | 19.4444 | 650 | 12638.8889 | 97.2222
| Centrifuge shed |  |  | 1 | 30 | 15 | 1 | 450 | 30 | 650 | 19500 | 150
| Substation Bldg |  |  | 0 | 15 | 12 | 1 | 0 | 0 | 650 | 0 | 0
| Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| Pump Room(s) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
| Control Room |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
650
4 | SUBSTATION | [8 empty] | 650
| GSU Transformer |  |  | 0 | 25 | 25 | 3 | 0 | 0 | 650 | 0 | 0
| (___)KV SF6 Circuit Breaker |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 650 | 0 | 0
| (___)KV Disc Switch w/ Stand |  |  | 0 | 10 | 15 | 1 | 0 | 0 | 650 | 0 | 0
| Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 650 | 0 | 0
| Transmission Line Poles |  |  | 5 | 4 | 4 | 12 | 960 | 35.5556 | 650 | 23111.1111 | 177.7778
| Insulator Support Base |  |  | 6 | 2.5 | 2.5 | 3 | 112.5 | 4.1667 | 650 | 2708.3333 | 20.8333
| PT Support Base |  |  | 6 | 2.5 | 2.5 | 3 | 112.5 | 4.1667 | 650 | 2708.3333 | 20.8333
| Static Pole Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
|  |  | Total Cost of Foundations | [5 empty] | 1468.2593 |  | 954.3685 | 7341.2963

## 1.4 Pilings
PILINGS
|  |  |  | (1,000's) | [7 empty] | 1.4
Project Name: |  | Tacoa LM 2500 Power Plant | [7 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [7 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description | [7 empty] | Cu | Price | Total
Nol |  |  |  |  | Units | Qty | "L" | "D" | "W" | Yd | CuYd | Price
1 | Concrete Pilings
| Pilings GTG x _____ |  |  |  | 2 | 8 | 30 | 2.5 | 2.5 | 111.1111 | 600 | 66666.6667
| Pilings SCR x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilings GSU x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilings Gas Comp x _____ |  |  |  | 3 | 4 | 30 | 2.5 | 2.5 | 83.3333 | 600 | 50000
| Pilings H20/Diesel Treatment |  |  |  | 1 | 6 | 30 | 2.5 | 2.5 | 41.6667 | 600 | 25000
| Pilings STG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
0
0
0
0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
|  |  | Total Cost of Retaining Walls |  | Total Price: 141.6667

## 1.5 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 1.5
Project Name: |  | Tacoa LM 2500 Power Plant | [6 empty] | Date: | 2009-04-23
Customer: |  | EDC | [6 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
2 | Gen Removal Areas |  |  | 80 | 20 | 1 | 1600 | 59.2593 | 600 | 35555.5556
3 | Turbine Removal Areas |  |  | 60 | 15 | 0.8 | 720 | 26.6667 | 600 | 16000
4 | Entry Ways |  |  | 15 | 6 | 0.8 | 72 | 2.6667 | 600 | 1600
5 | Walk ways |  |  | 80 | 6 | 0.5 | 240 | 8.8889 | 600 | 5333.3333
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 600 | 0
7 | [6 empty] | 0 | 0 |  | 0
8 | [6 empty] | 0 | 0 |  | 0
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 400 | 20 | 0.7 | 5600 | 207.4074 | 500 | 103703.7037
12 | Parking Lot |  |  | 80 | 50 | 0.7 | 2800 | 103.7037 | 500 | 51851.8519
13 | [6 empty] | 0 | 0 |  | 0
14 | Retaining Wall upper site |  |  | 120 | 25 | 1 | 3000 | 111.1111 | 900 | 100000
15 | Retaining Wall lower site |  |  | 70 | 10 | 2 | 1400 | 51.8519 | 750 | 38888.8889
16 | [6 empty] | 0 | 0 |  | 0
17 | 69 KV Duct Bank |  |  | 0 | 6 | 2 | 0 | 0 | 650 | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
352.9333

## 1.6 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 1.6
Project Name: |  | Tacoa LM 2500 Power Plant | [7 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [7 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 120 | 130 | 0.5 | 7800 | 288.8889 | 479.5556 | 25 | 11988.8889
3
4 | Lower Compressor Area |  |  | 1 | 140 | 120 | 0.5 | 8400 | 311.1111 | 516.4444 | 25 | 12911.1111
5
6 | Transmission Line right away |  |  | 1 | 1200 | 8 | 0.7 | 6720 | 248.8889 | 413.1556 | 25 | 10328.8889
7
8 | Road ways |  |  | 1 | 400 | 20 | 0.5 | 4000 | 148.1481 | 245.9259 | 25 | 6148.1481
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Gravel | Total: 41.377

## 1.7 Structural
STRUCTUAL STEEL
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [5 empty] | Date: | 2009-04-23
Customer: |  | EDC | [5 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | # of | Qty | Price | Total
Nol | [5 empty] | Lbs / Tons |  |  | Price
1 | Misc Pipe Rack supports etc. | [5 empty] | 6 | 3500 | 21000
0
2 | 15 KV Cable Tray Stanchons | [5 empty] | 0 | 3000 | 0
0
3 | GTG walkways and stairs | [5 empty] | 2 | 15000 | 30000
0
4 | Structual Steel for equip supports | [5 empty] | 1 | 15000 | 15000
5 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 0 | 15000 | 0
6 | Steel Cover for Storm Water Catch Basin | [5 empty] | 0 | 0 | 0
7 | Steel Grating Walkways over pipe ways/ Comp Bldg | [5 empty] | 0 | 0 | 0
8 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 20000 | 20000
9
|  |  | Total Cost of Stuctual Steel | [5 empty] | 86 | 0

## 1.8 Fence
FENCING
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1200 | 12 | 14400
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 900 | 25 | 22500
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 0 | 3500 | 0
10 | Motor Operated Double Gate(s) |  |  |  |  | 1 | 10000 | 10000
11 | Personnel Gate(s) |  |  |  |  | 2 | 400 | 800
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 0 | 7000 | 0
15
|  |  | Total Cost of Fencing |  |  |  |  | 47.7

## 2.1 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 2.1
Project Name: |  | Tacoa LM 2500 Power Plant | [5 empty] | Date: | 2009-04-23
Customer: |  | EDC | [5 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
Nol |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 50 | 40 | 2000 | 45 | 90000
2 | Control/Office |  |  |  | 0 | 60 | 0 | 65 | 0
3 | Water Treatment |  |  |  | 20 | 30 | 600 | 45 | 27000
4 | Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0
5 | Warehouse/Maintenance |  |  |  | 0 | 60 | 0 | 45 | 0
6 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Unloading Shed |  |  |  | 0 | 25 | 0 | 40 | 0
9 | Centrifuge Shed |  |  |  | 20 | 20 | 400 | 40 | 16000
10 |  |  |  |  | 0 | 0 | 0 | 40 | 0
11 | Entry Guard House |  |  |  | 0 | 15 | 0 | 40 | 0
12 | Pump shed |  |  |  | 15 | 15 | 225 | 40 | 9000
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
|  |  | Total Cost of Other Buildings | [5 empty] | 142

## 3.1 & 3.3 Mech Equip & Labor
MECHANICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [9 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [9 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [9 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
GTG
1 | GTG Type LM 2500 |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 6 | 45 | 5400 | 21.851 | 117995.13
2 | Lube oils and Chemicals |  |  | 2 | 35000 | 70000 | 0 | 0 | 10 | 2 | 2 | 80 | 21.851 | 1748.076
3 | Exhaust Stack |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 160 | 21.851 | 3496.152
| Grout |  |  | Qty: 2; Unit: 50000; Total: 100000
4 | Anchor Bolts |  |  | Qty: 2; Unit: 50000; Total: 100000; Unit: 2000; Frt: 4000
5 | HRSG
6 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
7 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
8 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
9 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
10 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
11 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
12
13 | SCR
14 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
15 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
16
17 | STG
18 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
19 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
20 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
21 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
22 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
23 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
24
25 | Inlet Air Conditioning System
26 | Inlet Chilling Package |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
27 | Inlet Fogging System |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
28 | Inlet Evap Cooling System |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
29 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
30 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
31 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
32 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
33
34 | Fuel Gas Systems
35 | Fuel Gas compressor w/ Fin Fans |  |  | 3 | 0 | 0 | 0 | 0 | 10 | 4 | 8 | 960 | 21.851 | 20976.912
36 | Fuel Gas Check Metering/Regulator Skid |  |  | 1 | 120000 | 120000 | 3000 | 3000 | 10 | 4 | 4 | 160 | 21.851 | 3496.152
37 | Fuel Gas Turbine Metering Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
37 | Fuel Gas Filter Skid & Mnt (___) KW Htr(Htr in Elect) |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 3 | 4 | 240 | 21.851 | 5244.228
38 | ESD Valve, ___" ___# |  |  | 1 | 15000 | 15000 | 500 | 500 | 10 | 2 | 1 | 20 | 21.851 | 437.019
39 |  |  |  | Qty: 0; Unit: 0; Total: 0
40 | Liquid Fuel Systems
41 | Unloading Pump Skid |  |  | 1 | 20000 | 20000 | 600 | 600 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
42 | Metering Skid |  |  | 1 | 145000 | 145000 | 4350 | 4350 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
43 | Forwarding Pump Skid |  |  | 2 | 12000 | 24000 | 900 | 1800 | 10 | 3 | 3 | 180 | 21.851 | 3933.171
44 | Transfer Pump Skid |  |  | 1 | 25000 | 25000 | 750 | 750 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
45 | Fuel Heating |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
46 | Filters |  |  | 4 | 12000 | 48000 | 750 | 3000 | 10 | 2 | 3 | 240 | 21.851 | 5244.228
47 | Centrifuge |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 4 | 15 | 1200 | 21.851 | 26221.14
48 | Injection Pump Skid |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 4 | 3 | 120 | 21.851 | 2622.114
49 | Storage Tank |  |  | 2 | 30000 | 60000 | 20000 | 40000 | 10 | 4 | 8 | 640 | 21.851 | 13984.608
50 | Day Tank |  |  | 2 | 20000 | 40000 | 1500 | 3000 | 10 | 3 | 3 | 180 | 21.851 | 3933.171
51 | Water Supply System
52 | Raw Water Storage Tank 21 M gal |  |  | 1 | 25000 | 25000 | 15000 | 15000 | 10 | 3 | 4 | 120 | 21.851 | 2622.114
53 | Raw Water Supply Pumps |  |  | 2 | 15000 | 30000 | 900 | 1800 | 10 | 3 | 2 | 120 | 21.851 | 2622.114
54 | Raw Water Forwarding Pumps |  |  | 2 | 15000 | 30000 | 900 | 1800 | 10 | 3 | 2 | 120 | 21.851 | 2622.114
55 | Water Treatment System
56 | Multi Media Filter Package |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
57 | Water Injection Skid |  |  | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851
58 | Demin Treatment System |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 6 | 12 | 720 | 21.851 | 15732.684
59 | Demin Storage SS Tank gal |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
60 | Demin water fiberglass tank |  |  | 2 | 25000 | 50000 | 5000 | 10000 | 10 | 3 | 5 | 300 | 21.851 | 6555.285
61 | Demin forwarding pumps |  |  | 2 | 15000 | 30000 | 500 | 1000 | 10 | 3 | 2 | 120 | 21.851 | 2622.114
62 | Demin Filter Skid |  |  | 4 | 12000 | 48000 | 500 | 2000 | 10 | 3 | 2 | 240 | 21.851 | 5244.228
63 | Demin Water Tank, SS 300M gal |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
64
65 | Waste Water and Oil Storage and Transfer
66 | Oily Water Separator |  |  | 1 | 50000 | 50000 | 10000 | 10000 | 10 | 4 | 5 | 200 | 21.851 | 4370.19
67 | Oily Waste Tank 10000 gal |  |  | 1 | 10000 | 10000 | 2500 | 2500 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
68 | Waste Water Tank 10000 gal |  |  | 0 | 10000 | 0 | 2500 | 0 | 10 | 3 | 3 | 0 | 21.851 | 0
69 | Waste Oil and Water forwarding pumps w/ skid |  |  | 1 | 10000 | 10000 | 500 | 500 | 10 | 2 | 2 | 40 | 21.851 | 874.038
70
71 | Fire Control Systems
72 | Fire Water Pump Skids (Diesel / Electric) |  |  | 0 | 400000 | 0 | 15000 | 0 | 10 | 4 | 6 | 0 | 21.851 | 0
73 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 60000 | 60000 | 2000 | 2000 | 10 | 4 | 10 | 400 | 21.851 | 8740.38
74 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0
75 | Storm Water System
76 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
77 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
78 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
79
80 | Other Systems
81 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
82 | Potable Water System |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 3 | 3 | 90 | 21.851 | 1966.5855
83 | Emergency Generator |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 4 | 8 | 320 | 21.851 | 6992.304
84
85 | BOP Pipe, Valves and Fittings Labor |  |  | 1 | 650000 | 650000 | 20000 | 20000 | 10 | 10 | 140 | 14000 | 21.851 | 305.9133
86 |  |  | Total Cost | Total: 1760; Frt: 127.6; Hours: 10; Qty: 0; Qty: 0
[12 empty] | 26820 |  | 280.4351
[9 empty] | Total Manhours |  |  | 26820
[9 empty] | Times Prod Factor |  | 1.8 | 48276 | 21.851 | 1054.8765
Price per hour based with all labor burdens as follows:
[8 empty] | Local Hrly Cost |  | 9
[8 empty] | Labor Burden 35% |  | 3.15
[8 empty] | Small Tools |  | 1.5
[8 empty] | Fringes |  | 2.5
16.15
[8 empty] | Contrr G&A 8% |  | 1.292
[8 empty] | Contr Mark up 15% |  | 2.4225
19.8645
[7 empty] | 50 | Hour Work Week = |  | 21.851
Work Week Hours Multiplier
[7 empty] | 45 | 50 | 60
[7 empty] | 1.06 | 1.1 | 1.17

## 4.1 & 4.3 El Equip & Labor
ELECTRICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [11 empty] | Date: |  | 2009-04-23
Customer: |  | EDC | [11 empty] | Quote No: |  | T 9003 A - 5
Location: |  | Tacoa Venn | [11 empty] | Est By: |  | J DP
Bid Due Date: |  | 2009-04-16
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
Power Island Equipment
1 | Gas Turbine Generator |  |  |  |  | 2 |  |  |  |  | 10 | 4 | 30 | 2400 | 21.851 | 52442.28
2 | HRSG |  |  |  |  | 0 |  |  |  |  | 10 |  |  | 0 | 21.851 | 0
3 | SCR |  |  |  |  | 0 |  |  |  |  | 10 |  |  | 0 | 21.851 | 0
4 | STG |  |  |  |  | 0 |  |  |  |  | 10 |  |  | 0 | 21.851 | 0
5 | STG Cooling Tower |  |  |  |  | 0 |  |  |  |  | 10 |  |  | 0 | 21.851 | 0
6 | Liquid Fuel Treatment |  |  |  |  | 1 |  |  |  |  | 10 | 3 | 6 | 180 | 21.851 | 3933.171
7 | Water Treatment Package |  |  |  |  | 1 |  |  |  |  | 10 | 3 | 8 | 240 | 21.851 | 5244.228
8 | [10 empty] | 10 |  |  | 0 | 21.851 | 0
9 | 15KV
10 | Generator Breaker(s) |  |  |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 3 | 5 | 300 | 21.851 | 6555.285
11 | Distribution Breaker(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 4 | 0 | 21.851 | 0
12 | Fused Disconnect(s) |  |  |  |  | 2 | 20000 | 40000 | 1000 | 2000 | 10 | 3 | 4 | 240 | 21.851 | 5244.228
13 | Bus Duct |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 4 | 0 | 21.851 | 0
14 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 21.851 | 0
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 21.851 | 0
16 | 5KV
17 | Distribution Breaker(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 21.851 | 0
18 | Fused Disconnect(s) |  |  |  |  | 1 | 20000 | 20000 | 0 | 0 | 10 | 2 | 6 | 120 | 21.851 | 2622.114
10 | MCC's |  |  |  |  | 3 | 0 | 0 | 0 | 0 | 10 | 3 | 3 | 270 | 101 | 27270
11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 21.851 | 0
12 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 21.851 | 0
13 | 600V
14 | Distribution Panel(s) |  |  |  |  | 1 | 170000 | 170000 | 2500 | 2500 | 10 | 2 | 8 | 160 | 21.851 | 3496.152
15 | GTG MCC(s) |  |  |  |  | 0 | 48000 | 0 | 2500 | 0 | 10 | 2 | 5 | 0 | 21.851 | 0
16 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 21.851 | 0
17 | STG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 21.851 | 0
18 | BOP MCC(s) |  |  |  |  | 1 | 10000 | 10000 | 1500 | 1500 | 10 | 2 | 4 | 80 | 21.851 | 1748.076
19 | Water Treatment MCC(s) |  |  |  |  | 1 | 10000 | 10000 | 1000 | 1000 | 10 | 2 | 3 | 60 | 21.851 | 1311.057
20 | DC motor Starter |  |  |  |  | 0 | 18000 | 0 | 0 | 0 | 10 | 2 | 8 | 0 | 21.851 | 0
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
22 | Aux Transformer(s)
23 | 15/5KV ____1.5_______ MVA |  |  |  |  | 1 | 75000 | 75000 | 5000 | 5000 | 10 | 3 | 5 | 150 | 21.851 | 3277.6425
24 | 15/600V ___.75___ MVA |  |  |  |  | 2 | 45000 | 90000 | 5000 | 10000 | 10 | 2 | 4 | 160 | 21.851 | 3496.152
25 | 600/120/208V ________ KVA |  |  |  |  | 1 | 3500 | 3500 | 175 | 175 | 10 | 0 | 0 | 0 | 21.851 | 0
26 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
27 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
28 | Area Lighting
29 | Poles _______ High |  |  |  |  | 8 | 1500 | 12000 | 500 | 4000 | 10 | 2 | 1 | 160 | 21.851 | 3496.152
30 | Floodlights _______ Watts |  |  |  |  | 16 | 600 | 9600 | 100 | 1600 | 10 | 1 | 0.2 | 32 | 21.851 | 699.2304
31 | [5 empty] | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
32 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 60 | 0 | 21.851 | 0
33 | Other Systems
34 | UPS |  |  |  |  | 1 | 15000 | 15000 | 0 | 0 | 10 | 2 | 1 | 20 | 21.851 | 437.019
35 | DC 125 VDC Battery & Charger |  |  |  |  | 0 | 15000 | 0 |  | 0 | 10 | 2 | 2 | 0 | 21.851 | 0
36 | Cathodic Protection |  |  |  |  | 2 | 15000 | 30000 | 0 | 0 | 10 | 4 | 4 | 320 | 21.851 | 6992.304
37 | Lightning Protection |  |  |  |  | 2 | 15000 | 30000 | 0 | 0 | 10 | 4 | 4 | 320 | 21.851 | 6992.304
38 | 69 KV Underground Cable 1 conductor |  |  |  |  | 1800 | 125 | 225000 | 10000 | 10000 | 10 | 1 | 0.2 | 3600 | 21.851 | 78663.42
39
40 | Temporary Electric |  |  |  |  | 1 | 40000 | 40000 | 0 | 0 | 10 | 2 | 20 | 400 | 21.851 | 8740.38
41 | emergency Generator |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 10 | 4 | 5 | 200 | 21.851 | 4370.19
42 | Cable Tray, Conduit, & Cable |  |  |  |  | 2 | 500000 | 1000000 | 20000 | 40000 | 10 | 8 | 120 | 19200 | 21.851 | 419538.24
43 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
44 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
45 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 21.851 | 0
|  |  | Total Cost of Electrical Equipment |  |  |  |  | 1780.1 |  | 77.775 |  |  |  | 28612 |  | 646.5696
28612
[12 empty] | Productivity | 2 | 57224 | 21.851 | 1250.3988
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 9
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35 % |  | 3.15
16.15
[13 empty] | G&A 8% |  | 1.292
[13 empty] | Contr Markup 15% |  | 2.4225
19.8645
[12 empty] | 50 | Hour Work Week = |  | 21.851
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17

## 4.2 & 4.4 Substa Eq & Labor
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [11 empty] | Date: | 2009-04-23
Customer: |  | EDC | [11 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [11 empty] | Est By: | JDP
Bid Due Date: |  | 2009-04-16
Item |  | Description | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [5 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Main Power Transformer __69__ KV, _18/24/30MVA |  |  |  | 0 | 0 | 0 | 75000 | 0 | 10 | 4 | 8 | 0 | 21.851 | 0
2 | SF6 Circuit Switchers(s) _69___ KV |  |  |  | 2 | 70000 | 140000 | 5000 | 10000 | 10 | 2 | 3 | 120 | 21.851 | 2622.114
3 | Disconnect Switches __69____ KV |  |  |  | 2 | 12000 | 24000 | 1000 | 2000 | 10 | 2 | 2 | 80 | 19 | 1520
4 | Station Post Insulators __69__ KV |  |  |  | 6 | 500 | 3000 | 100 | 600 | 10 | 2 | 0.05 | 6 | 19 | 114
5 | Insulator Stanchons __15____ High |  |  |  | 6 | 700 | 4200 | 50 | 300 | 10 | 1 | 0.5 | 30 | 19 | 570
6 | Insulator Stanchons ______ High |  |  |  | 0 | 700 | 0 | 50 | 0 | 10 | 1 | 0.4 | 0 | 19 | 0
7 | Dead End Tower(s) |  |  |  | 0 | 35000 | 0 | 10000 | 0 | 10 | 3 | 1 | 0 | 19 | 0
8 | Alum Bus ______ Dia |  |  |  | 0 | 15 | 0 | 1.5 | 0 | 10 | 1 | 0.09 | 0 | 19 | 0
9 | Alum Bus Conn's |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 19 | 0
10 | Alum Bus End Plugs _____ Dia |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.05 | 0 | 19 | 0
11 | Alum Bus Support Clamps |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 19 | 0
12 | Alum Bus "V" Conn's |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.08 | 0 | 19 | 0
13 | Static Wire Poles, ____ High |  |  |  | 0 | 1500 | 0 | 500 | 0 | 10 | 4 | 1 | 0 | 19 | 0
14 | Area Lighting Poles, ____ High |  |  |  | 0 | 2500 | 0 | 0 | 0 | 10 | 2 | 1 | 0 | 19 | 0
15 | Flood Lights, ______ Watts |  |  |  | 0 | 400 | 0 | 0 | 0 | 10 | 0.5 | 1 | 0 | 19 | 0
16 | #4/0 Grounding Conductor |  |  |  | 0 | 1200 | 0 | 0 | 0 | 10 | 2 | 0.03 | 0 | 19 | 0
17 | 3/4"x10'-0" Ground Rods & Clamps |  |  |  | 0 | 50 | 0 | 0 | 0 | 10 | 1 | 0.04 | 0 | 19 | 0
18 | #90 Cadweld Shots |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0.3 | 0 | 19 | 0
19 | Metering CT's & CPT's |  |  |  | 3 | 15000 | 45000 | 0 | 0 | 10 | 2 | 1 | 60 | 19 | 1140 | 0
20 | Station Metering w/ In & Out Capabilities |  |  |  | 1 | 50000 | 50000 | 0 | 0 | 10 | 2 | 1 | 20 | 19 | 380
21 | Station Protective Relay(s) |  |  |  | 2 | 45000 | 90000 | 0 | 0 | 10 | 2 | 1 | 40 | 19 | 760
22 | Station RTU |  |  |  | 0 | 35000 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 19 | 0
23 | 125V DC System |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 19 | 0
24 | Transmission Line Poles |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 2 | 0 | 19 | 0
25 | Transmission Line Strain Insulators |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 19 | 0 | 0
26 | Cable Bus, Type _____, Size _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 6 | 0 | 19 | 0
27 | Main Power Transformer Oil, ______ Gal |  |  |  | 0 | 40000 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 19 | 0
28 | Main Power Transformer Dress Out & Test |  |  |  | 0 | 50000 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 19 | 0
29 | Lightning Arrestors |  |  |  | 0 | 5000 | 0 | 0 | 0 | 10 | 2 | 0.5 | 0 | 19 | 0 | 0
30 | Fiber Optic Cable Fittings & Terminations |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 |  | 19 | 0
31 |  |  | Rate: 0
32 |  |  | Rate: 0; Total: 0
34 |  |  | Rate: 0; Total: 0
35 |  |  | Rate: 0; Total: 0
36 |  |  | Rate: 0; Total: 0
37 |  |  | Rate: 0; Total: 0
38 |  |  | Rate: 0; Total: 0
39 |  |  | Rate: 0
40 |  |  | Rate: 0
41 |  |  | Rate: 0
42 |  |  | Rate: 0
43 |  |  | Rate: 0
44 |  |  | Total: 0
[7 empty] | 356.2 |  | 12.9 |  |  |  | 356 |  | 7.1061
[11 empty] | Total Hours |  | 356
[11 empty] | Prod Factor | 2 | 712 | 42 | 29.904
Price per hour based with all labor burdens as follows:
[6 empty] | Local Hrly Cost |  | 9
[6 empty] | Fringes |  | 2.5
[6 empty] | Small Tools |  | 1.5
[6 empty] | Labor Burden 35 % |  | 3.15
16.15
[6 empty] | G&A 8% |  | 1.292
[6 empty] | Contr Markup 15% |  | 2.4225
19.8645
[5 empty] | 50 | Hour Work Week = |  | 21.851
Work Week Hours Multiplier
[5 empty] | 45 | 50 | 60
[5 empty] | 1.06 | 1.1 | 1.17

## 5.1 CEMS
CEM's
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Cems | Cost | Cost
1 | Rosemont CEM's Unit Most States for 1 ea GTG |  |  |  |  | 0 | 120 | 0
2 | Rosemont CEM's Unit for Califormia for 1 ea GTG |  |  |  |  | 1 | 130 | 130
3 | Installation Support |  |  |  |  | 0 | 18 | 0
|  |  | Total Cost of CEM's |  |  |  |  | 0

## 5.2 Instrument
PLANT INSTRUMENTATION
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [9 empty] | Date: | 2009-04-23
Customer: |  | EDC | [9 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [9 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Instrumentation for GTG |  |  |  | 2 | 25000 | 50000 | 10 | 2 | 8 | 320 | 21.851 | 6992.304
0
2 | Instrumentation for SCR |  |  |  | 0 | 0 | 0 | 10 | 4 | 15 | 0 | 21.851 | 0
3 | Instrumentation for Gas Compression |  |  |  | 3 | 15000 | 45000 | 10 | 3 | 5 | 450 | 21.851 | 9832.9275
4 | Instrumentation for Injection Water Treatment |  |  |  | 1 | 15000 | 15000 | 10 | 2 | 20 | 400 | 21.851 | 8740.38
5 | Instrumentation for Waste Water Treatment |  |  |  | 0 | 0 | 0 | 10 | 2 | 10 | 0 | 21.851 | 0
6 | Instrumentation for Liquid Fuel |  |  |  | 1 | 15000 | 15000 | 10 | 4 | 5 | 200 | 21.851 | 4370.19
7 | Labor to Install CEMS |  |  |  | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 21.851 | 0
| Price per hour based with all labor burdens as follows: |  |  |  | Total: 125; Qty: 1370; Total: 29.9358
[9 empty] | Total Hours |  | 1370
|  | Local Hrly Cost |  | 9 | Qty: Prod Factor; Qty: 2; Qty: 2740; Rate: 0; Total: 0
|  | Fringes |  | 2.5
|  | Small Tools |  | 1.5
|  | Labor Burden 35 % |  | 3.15
16.15
|  | G&A 8% |  | 1.292
|  | Contr Markup 15% |  | 2.4225
19.8645
| 50 | Hour Work Week = |  | 21.851
Work Week Hours Multiplier
| 45 | 50 | 60
| 1.06 | 1.1 | 1.17

## 6.1 DCS Hard
DCS HARDWARE
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [6 empty] | Cost | Cost
1 | DCS Hardware |  |  |  |  | 1 | 60000 | 60000
0
0
2 | Lot of Misc interconnecting cables etc. |  |  |  |  | 1 | 5000 | 5000
3 | PBX Communications System |  |  |  |  | 1 | 10000 | 10000
0
4 | Loud Speaker System |  |  |  |  | 1 | 10000 | 10000
5 | Documentation |  |  |  |  | 0 | 40000 | 0
|  |  | Total Cost of DCS Hardware |  |  |  |  | 85

## 6.2 DCS Soft
DCS SOFTWARE
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Hrs | Cost | Cost
1 | Software for DCS |  |  |  |  | 1 | 60000 | 60000
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
2 | Software for O & M Package |  |  |  |  | 1 | 20 | 20 | 0 | 0 | 20
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
|  |  | Total Cost of DCS Software |  |  |  |  | 60.02 |  |  | 20

## 7.1 Erection
PLANT ERECTION
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [7 empty] | Date: | 2009-04-23 | *.2
Customer: |  | EDC | [7 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  | No | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | GTG Erection |  |  |  | 2 | 10 | 12 | 35 | 8400 | 21.851 | 183547.98
2 | HRSG Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 21.851 | 0
3 | SCR Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 21.851 | 0
4 | Water Treatment and FW Systems |  |  |  | 1 | 10 | 6 | 15 | 900 | 21.851 | 19665.855
5 | Liquid Fuel |  |  |  | 1 | 10 | 4 | 5 | 200 | 21.851 | 4370.19
6 | BOP Equip Erection |  |  |  | 1 | 10 | 4 | 10 | 400 | 21.851 | 8740.38
7 | Gas Compressor Erection |  |  |  | 3 | 10 | 6 | 5 | 900 | 21.851 | 19665.855
8 | Evap Cooling Erection |  |  |  | 0 | 10 | 4 | 4 | 0 | 21.851 | 0
9 | Fire Water Pump Skid |  |  |  | 0 | 10 | 4 | 3 | 0 | 21.851 | 0
10 | STG Erection |  |  |  | 0 | 10 | 12 | 36 | 0 | 21.851 | 0
11 | STG Cooling Tower |  |  |  | 0 | 10 | 8 | 8 | 0 | 21.851 | 0
Price per hour based with all labor burdens as follows:
|  | Local Hrly Cost |  | 9
|  | Fringes |  | 2.5
|  | Small Tools |  | 1.5
|  | Labor Burden 35 % |  | 3.15
16.15
|  | G&A 8% |  | 1.292
|  | Contr Markup 15% |  | 2.4225 |  |  |  |  | 10800 |  | 235.9903
|  |  |  | 19.8645 |  |  | Total Hours |  | 10800
| 50 | Hour Work Week = |  | 21.851 |  |  | Prod Factor | 2 | 21600 | 9 | 194.4
Work Week Hours Multiplier
| 45 | 50 | 60
| 1.06 | 1.1 | 1.17

## 8.2 Equip rent
EQUIPMENT RENTAL
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [6 empty] | Date: | 2009-04-23
Customer: |  | EDC | [6 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
Nol | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 2 | 10 | 20 | 3000 | 60000
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 30 | 60 | 2000 | 120000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 2 | 10 | 20 | 1500 | 30000
| 2 ea Sky Tracs |  |  |  |  | 2 | 30 | 60 | 70 | 4200
| 2 ea Fork Lifts |  |  |  |  | 2 | 30 | 60 | 70 | 4200
| 1 ea Man Lift |  |  |  |  | 2 | 0 | 0 | 80 | 0
| 2 ea Welders |  |  |  |  | 4 | 30 | 120 | 60 | 7200
2 | HRSG Erection
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
3 | SCR/CO
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
4 | STG
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
5 | STG Cooling Tower
| 150 Ton Crane |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 40 Ton Crane |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
6 | Fuel Gas Compressor Rental per Compr Skid
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 1 | 5 | 5 | 3000 | 15000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
7 | BOP Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 120 | 120 | 1500 | 180000
| 2 ea Fork Lifts |  |  |  |  | 1 | 90 | 90 | 70 | 6300
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 2 ea Pick ups |  |  |  |  | 0 | 0 | 0 | 30 | 0
| 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 90 | 90 | 70 | 6300
8 | Substation Equip Rental
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 2 | 3 | 6 | 4000 | 24000
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 5 | 5 | 1500 | 7500
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
|  |  | Total Cost of Plant Equip Rental |  |  |  |  | 656 |  | 464.7

## 9.0 Paint
PLANT PAINTING
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Paint for GTG |  |  |  |  | 2 | 15000 | 30000
2 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
3 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 25000 | 0
4 | Paint for Pipe Rack etc. |  |  |  |  | 2 | 10000 | 20000
5 | Paint for BOP Equipment |  |  |  |  | 1 | 30000 | 30000
6 | Paint for Gas Compressor |  |  |  |  | 3 | 10000 | 30000
7 | Paint for Water Treatment |  |  |  |  | 1 | 15000 | 15000
8 | Paint for Liquid Fuel Treatment |  |  |  |  | 1 | 15000 | 15000
9 | Paint for HRSG |  |  |  |  | 0 | 95000 | 0
|  |  | Total Cost of Plant Painting |  |  |  |  | 140
0

## 10.0 Transportation
PLANT TRANSPORTATION
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 127.6 | 127.6
2 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 77.775 | 77.775
3 | Transportation Substation Equip |  |  |  |  | 1 | 12.9 | 12.9
4 | Transportation of GTG
5 | Transportation of SCR
6 | Transportation of HRSG
7 | Transportation of STG
|  |  | Total Cost of Plant Transportation |  |  |  |  | 218.275

## 11.0 Site Costs
SITE COSTS
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant | [6 empty] | Date: | 2009-04-23
Customer: |  | EDC | [6 empty] | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
Nol | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
| Office Trailers |  |  |  |  | 4 | 7 | 900 | 25200
| Porta Potties |  |  |  |  | 4 | 7 | 150 | 4200
| Water and Ice |  |  |  |  | 2 | 7 | 500 | 7000
| Fed X |  |  |  |  | 1 | 7 | 300 | 2100
| Telephone |  |  |  |  | 1 | 7 | 1500 | 10500
| Office Supplies |  |  |  |  | 1 | 7 | 1000 | 7000
0
| Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 6 | 3000 | 18000
| Misc Items |  |  |  |  | 1 | 7 | 1500 | 10500
|  |  | Total Monthly Cost | [5 empty] | 84500
2 | Total Project Cost = Cost per Month Times Number of Mos
Plus the Project One Time Costs.
| Monthly Site Costs | [5 empty] | 1 | 84500 |  | 84500
| One Time Costs | [5 empty] | 0
| 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 150000
| Cad Station | [8 empty] | 5000
| Computers | [8 empty] | 5000
| Telephone System and Satalite Dish | [8 empty] | 10000
| Plotter | [8 empty] | 8000
| Fax Machine and Printers | [8 empty] | 3000
| Misc equip | [8 empty] | 5000
|  |  | Total Cost of Project Site Costs | [6 empty] | 270.5

## 12.1 Engineering
ENGINEERING
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Conceptual Engineering WGPS |  |  |  |  | 1 | 10000 | 10000
2 | Detailed Engineering per GTG |  |  |  |  | 2 | 200000 | 400000
3 | Detailed Engineering for Gas Compression |  |  |  |  | 1 | 45000 | 45000
4 | Detailed Engineering for Liquid Fuel Treatment |  |  |  |  | 1 | 20000 | 20000
5 | Detailed Engineering Substation |  |  |  |  | 1 | 20000 | 20000
6 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 15000 | 15000
7 | Detailed Engineering per Structural Steel/civil |  |  |  |  | 1 | 100000 | 100000
|  |  | Total Cost of Engineering |  |  |  |  | 610

## 12.2 Local Engr-Arch
LOCAL ENGINEERING
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Soils & Environmental Eng |  |  |  |  | 1 | 10000 | 10000
2 | Civil Engineer |  |  |  |  | 1 | 20000 | 20000
3 | Mechanical Engineer |  |  |  |  | 1 | 20000 | 20000
4 | Electrical Engineer |  |  |  |  | 1 | 20000 | 20000
5 | Other |  |  |  |  | 0 | 0 | 0
|  |  | Total Cost of Local Engineering |  |  |  |  | 70

## 12.3 Engr Trav & per diem
ENGINEERING TVL AND PER DIEM
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Round Trip Air Fare for Eng Visits to site |  |  |  |  | 6 | 2000 | 12000
2 | Days of Per Diem Cost for Eng Days at Site |  |  |  |  | 150 | 200 | 30000
3 | Auto Rental for Eng Days at Site |  |  |  |  | 150 | 80 | 12000
4 | Misc Travel Expentitures |  |  |  |  | 1 | 35000 | 35000
0
|  |  | Total Cost of Eng Tvl and Per Diem |  |  |  |  | 89

## 13.1 Proj Mgt Labor
PROJECT MANAGEMENT LABOR
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | No. | Cost | Total
Nol | [5 empty] | Mos | Per Mo | Cost
Home Office Proj Mgt
1 | Project Mgr Months on Project |  |  |  |  | 7 | 15000 | 105000
2 | Admin Mgr Months on Project |  |  |  |  | 7 | 5000 | 35000
3 | Scheduler |  |  |  |  | 2 | 6500 | 13000
4 | Purchasing Agent |  |  |  |  | 1 | 6000 | 6000
5 | Expediter |  |  |  |  | 2 | 5000 | 10000
6 | Home Office Logistic Coordinator |  |  |  |  | 0 | 9000 | 0
On Site Proj Mgt
7 | Secretary |  |  |  |  | 6 | 4000 | 24000
8 | Construction Mngr |  |  |  |  | 4 | 15000 | 60000
9 | Contract Cost admin |  |  |  |  | 0 | 7000 | 0
10 | Mechanical Supervisor |  |  |  |  | 5 | 14000 | 70000
11 | Electrical Supervisor |  |  |  |  | 5 | 14000 | 70000
12 | Civil Supervisor |  |  |  |  | 4 | 14000 | 56000
13 | Clerks |  |  |  |  | 6 | 5000 | 30000
14 | Warehousemen |  |  |  |  | 6 | 3000 | 18000
15 | Draftsman |  |  |  |  | 4 | 6000 | 24000
16 | Security |  |  |  |  | 7 | 10000 | 70000
17 | Safety |  |  |  |  | 7 | 10000 | 70000
18 | QA/QC Mngr |  |  |  |  | 7 | 10000 | 70000
|  |  |  | Total Proj Mgt Labor |  |  |  | 731000
0
19 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 6 | 15000 | 90000
0
20 | Inspectors | [6 empty] | 0
| Civil - Structual __ ea ___ mos |  |  |  |  | 2 | 14000 | 28000
| Mechanical __ ea ___ mos |  |  |  |  | 4 | 14000 | 56000
| Electrical __ ea ___ mos |  |  |  |  | 4 | 14000 | 56000
| Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 1 | 14000 | 14000
| US Welders and Electricians |  |  |  |  | 8 | 15000 | 120000
21 | Training |  |  |  |  | 1 | 25000 | 25000
|  |  | Total Cost of Project Mgt Labor |  |  |  |  | 1120

## 13.2 Proj MGT TVL Per
PROJECT MGT TVL AND PER DIEM
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | No. | Cost | Total
Nol | [5 empty] | Units | Per Unit | Cost
1 | R T Air Fares |  |  |  |  | 36 | 2000 | 72000
2 | Months of Per Diem at Site |  |  |  |  | 50 | 2500 | 125000
3 | Number of Months of Pick Up Trucks |  |  |  |  | 25 | 1500 | 37500
4 | Misc expenditures |  |  |  |  | 1 | 50000 | 50000
5 | [5 empty] | 0 | 0 | 0
6 | [5 empty] | 0 | 0 | 0
7 | [5 empty] | 0 | 0 | 0
8 | [5 empty] | 0 | 0 | 0
9 | [5 empty] | 0 | 0 | 0
10 | [5 empty] | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
0
0
0
0
0
|  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  |  |  | 284.5

## 15.0 Sales Tax
SALES TAXES
(1,000's)
Project Name: |  | Tacoa LM 2500 Power Plant |  |  |  |  | Date: | 2009-04-23
Customer: |  | EDC |  |  |  |  | Quote No: | T 9003 A - 5
Location: |  | Tacoa Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-16
Item |  | Description |  |  |  | Total | State | Total
Nol | [5 empty] | Cost | Tax | Taxes
1 | Major Mechanical Equipment |  |  |  |  | 1760 | 0.0825 | 145.2
2 | Major Electrical Equipment |  |  |  |  | 1780.1 | 0.0825 | 146.8582
3 | Substation Equipment |  |  |  |  | 356.2 | 0.0825 | 29.3865
4 | DCS Eqipment |  |  |  |  | 85 | 0.0825 | 7.0125
5 | Instrument |  |  |  |  | 125 | 0.0825 | 10.3125
|  |  | Total Cost of Plant Sales Taxes |  |  |  |  | 0