| DATE | 10/08/2010 |
| --- | --- |
| PROJECT # | T9018 |
| LOCATION | La Raisa, Charallave, Venezuela |
| PROJECT MANAGER | Steve Yates |
| SITE MANAGER | Dale Tafoya |
| WEATHER CONDITIONS | Cloudy |
| TEMPERATURE RANGE | 68 to 90 F |
| SITE CONDITIONS | Muddy |
| # PERSONNEL ON SITE |  |
| PROENERGY |  |
| CONTRACTORS | CONCIMECA ATIMECA MLORE |
| GENERAL ITEMS |  |
| CLIENT ISSUES / CONCERNS |  |
| CIVIL | - When weather permits. Density test needed at liquid fuel area foam building area. - Ready to place concrete in 60 footers for pipe supports and some pipe supports piers ready 10 need to dewater. - Working on compressor foundation - Moving mud at tank area. - Pumping water at pull boxes. - Pump water out |
| MECHANICAL |  |
| UNIT 100 | Working on flexible links |
| UNIT 200 | No update |
| UNIT 300 | No update |
| LOGISTIC | Shipments of cargo that is being held at port and airport for lack of customs warranty payments. Expected delivery on 10/11/10. Brief descriptions included, but not all inclusive!! 8 Shipments at port include: IND. CHAMP V 210072- BOL PBL01/OC2180-8 containers pvc duct, DCS cabinets, wire, 10”& 12” pipe erw, Battery Back-UPS. INDUSTRIAL CHAMP V 210093-BOL 511000717-Cable tray, 6”pipe, EDI skid, transformer rectifier INDUSTRIAL DREAM V 210074-BOL 511000614-Fittings, wire JANNIE C V /210076-BOL IDMC106156001-DC distribution panels, 6” pipe fusion bond INDUSTRIAL EDGE V 210081-BOL 511000640-Fire Protection system & foam. INDUSTRIAL EDGE V 210081-BOL 511000644- 15KV switchgear, wire, aux. current trans. panels Industrial Dart V /210083- BOL511000661-water softener skid Industrial Dart V /210091- BOL 511000709-water pump skid 4 Shipments at airport include: AWB: 5121025434- 4/0 bare copper wire AWB: 512102 5410-Startup-gaskets, flanges, AWB: 5121025376-Startup-Packing seals, SS mesh, pressure guages AWB: 5121025389-Startup-Nitrogen reg. set, Temp. guage, packing puller tool |
| ELECTRICAL | Continue pull and terminate cable from Utility Building to Auxiliary Transformers T-1 & T-2. |
| I&C START UP. | Continue with flushing guidelines, finishing up purchase orders, JSA template, spec out N2 sacrificial valves needed for blowing gas piping Deficiencies on getting percentage updated on all units, Missing parts on battery charger Unit-300 |
| QUALITY | Morning meeting. Gas Compressor: electrical conduit and rebar placement in progress. Fuel Offload: Area needs to dry enough for soil compaction and density testing. 53 pre-fab pipe support footers ready for 1st concrete pour when weather permits. GTG-200 & 300 cable trays supports and pull boxes excavations being de-watered for concrete pours and continued work. Raw Fuel Tank T-1000 x-rays from last night reviewed with Asincro QA/QC; all acceptable. Raw Fuel Tank T-1000 gas-oil contrast leak test of shell to bottom plates weld 100% complete acceptable. Action Items List meeting with Site Manager Dale Tafoya. |
| MILESTONE PROGRESS | Project Kickoff 100% Milestone 1- Civil Works GTG foundation poured 100% Milestone 2 - Gas Turbine set on Foundation 100% Milestone 3- Gas Turbine 1& 2 Erection complete 100% Milestone 4 - Mechanical - Electrical Gas Turbine 3 Erection Complete 100% Gas Turbine Auxiliary Equipment Set 85% Interconnect Piping Installed on Units 1 & 2 80% (1) Raw Fuel, (1) Treated Fuel Tank Complete 60% All Major Electrical Equipment Set and Installed 25% Milestone 5 - Electrical Complete Mechanical 20% Liquid Fuel Off Load Station Complete 5% Water Treatment System Installed 0% Interconnect Piping Installed on Unit 3 0% Gas Compressors Set on Foundation 0% Electrical Completion 0% All Electrical Interconnect Cabling Installed Units 1& 2 0% Pre commissioning Complete on Units 1 & 2 100% All Mechanical Equipment Flushed and Checked 25% All Hydrostatic Testing Complete 90% All Pumps Rotated and Tested 10% All Mechanical Systems Ready for Startup 15% All Electrical Equipment Statically Tested 0% All Electrical Systems Read for Startup 0% Milestone 6 Units1 & 2 Commissioning & Testing Complete 90% Gas Turbines Tested and Ready for Commercial Operation 80% All Mechanical Auxiliary Ready for commercial Operation 0% All Electrical Auxiliary Equipment Tested and Ready for Commercial Operation 60% Milestone 7 Mechanical All Plant Fuel and Water Tanks Complete 60% All Plant Fuel and Water Piping Complete 60% Electrical All Electrical Balance of Plant Complete 20% all Plant Fuel Interconnect Cabling Complete 60% Pre commissioning Complete on Unit 3 90% All Mechanical Equipment Flushed and Checked 30% All Hydrostatic Testing Complete 80% All Pumps Rotated and Tested 0% All Mechanical Systems Ready for Startup 0% All Electrical Equipment Statically Tested 0% All Electrical Systems read for startup 0% Milestone 8 Plant Commissioning & Testing Complete 0% GT Unit 3 Tested and Ready for Commercial Operation 70% Gas Compression Complete & Ready for PDVSA Gas 0% All Mechanical auxiliary and Balance of Plant Equipment Ready for Commercial Operation 0% All Buildings Finished and Complete 60% All Driveways and Finish Grading Complete 0% Major Milestones La Raisa Unit 300 Turned Over To Client 0% La Raisa Unit 100 Turned Over To Client 0% La Raisa Unit 200 Turned Over To Client 0% |
| STAFFING PLANS |  |
| CRITICAL AREAS OF CONCERN | - We are waiting for BOP material from the port and airport. - We waiting for Waiting on pipe fittings to complete plant piping (The work are delayed) - We lost about 5 days by heavy rains in the area. . |
| GENERAL COMMENTS | No Fittings for Concimeca to continue the fabrication piping tasks. |