| DATE | 10/13/2010 |
| --- | --- |
| PROJECT # | T9018 |
| LOCATION | La Raisa, Charallave, Venezuela |
| PROJECT MANAGER | Ed Martinez |
| SITE MANAGER | Dale Tafoya |
| WEATHER CONDITIONS | Cloudy |
| TEMPERATURE RANGE | 68 to 90 F |
| SITE CONDITIONS | Muddy in areas |
| # PERSONNEL ON SITE |  |
| PROENERGY |  |
| CONTRACTORS | CONCIMECA ATIMECA MLORE |
| GENERAL ITEMS | Concimeca people doesn’t work today for claims and their go home in the middle of the morning. ATIMECA people are working in a normal schedule. |
| CLIENT ISSUES / CONCERNS |  |
| CIVIL | No update |
| MECHANICAL | Sandblasting plate of steel for the tanks, Mount top ring on T-1005, assemble roof of T-1006. |
| UNIT 100 | No update |
| UNIT 200 | No update |
| UNIT 300 | No update |
| LOGISTIC | Were received on site the following: INDUSTRIAL EDGE V 210081-BOL 511000640-Fire Protection system & foam (Valves, Drum, fire alarm panel, red deluge cabinet). Industrial Dart V /210083- BOL511000661-water softener skid (Cable, alternating skid mounted softener systems). Shipments of cargo that is being held at port and airport for lack of customs warranty payments. Expected delivery on 10/13/10. Brief descriptions included, but not all inclusive!! 8 Shipments at port include: IND. CHAMP V 210072- BOL PBL01/OC2180-8 containers pvc duct, DCS cabinets, wire, 10”& 12” pipe erw, Battery Back-UPS. INDUSTRIAL CHAMP V 210093-BOL 511000717-Cable tray, 6”pipe, EDI skid, transformer rectifier INDUSTRIAL DREAM V 210074-BOL 511000614-Fittings, wire JANNIE C V /210076-BOL IDMC106156001-DC distribution panels, 6” pipe fusion bond Industrial Dart V /210091- BOL 511000709-water pump skid 4 Shipments at airport include: AWB: 5121025434- 4/0 bare copper wire AWB: 512102 5410-Startup-gaskets, flanges, AWB: 5121025376-Startup-Packing seals, SS mesh, pressure guages AWB: 5121025389-Startup-Nitrogen reg. set, Temp. guage, packing puller tool |
| ELECTRICAL | No update. Leader is working on schedule items. |
| I&C START UP. |  |
| QUALITY | Morning meeting. Atimeca working T-1000 Raw Fuel Tank repairs procedure and scheduling. T-1003 Clean Fuel Tank bottom plates layout and fit up in progress, Demin Water Tank roof fabrication in progress. Meeting with Concimeca Mechanical to get information required for completion schedule, materials needed, welds made and known welds to make; 1 inch lines will be add on due to Isometrics not engineered for below 2 inch and all are field fit and “As Built”. MTR for Gas Compressors foundation bolts incorrect; not proper material after cross reference check of materials designation with Asincro QC Euscher Bravo. Talked to Dale Tafoya about Derwick ordering these instead of Concimeca in order to get proper material and documentation. |
| MILESTONE PROGRESS | This section will be update after complete the new schedule. Project Kickoff 100% Milestone 1- Civil Works GTG foundation poured 100% Milestone 2 - Gas Turbine set on Foundation 100% Milestone 3- Gas Turbine 1& 2 Erection complete 100% Milestone 4 - Mechanical - Electrical Gas Turbine 3 Erection Complete 100% Gas Turbine Auxiliary Equipment Set 85% Interconnect Piping Installed on Units 1 & 2 80% (1) Raw Fuel, (1) Treated Fuel Tank Complete 60% All Major Electrical Equipment Set and Installed 25% Milestone 5 - Electrical Complete Mechanical 20% Liquid Fuel Off Load Station Complete 5% Water Treatment System Installed 0% Interconnect Piping Installed on Unit 3 0% Gas Compressors Set on Foundation 0% Electrical Completion 0% All Electrical Interconnect Cabling Installed Units 1& 2 0% Pre commissioning Complete on Units 1 & 2 100% All Mechanical Equipment Flushed and Checked 25% All Hydrostatic Testing Complete 90% All Pumps Rotated and Tested 10% All Mechanical Systems Ready for Startup 15% All Electrical Equipment Statically Tested 0% All Electrical Systems Read for Startup 0% Milestone 6 Units1 & 2 Commissioning & Testing Complete 90% Gas Turbines Tested and Ready for Commercial Operation 80% All Mechanical Auxiliary Ready for commercial Operation 0% All Electrical Auxiliary Equipment Tested and Ready for Commercial Operation 60% Milestone 7 Mechanical All Plant Fuel and Water Tanks Complete 60% All Plant Fuel and Water Piping Complete 60% Electrical All Electrical Balance of Plant Complete 20% all Plant Fuel Interconnect Cabling Complete 60% Pre commissioning Complete on Unit 3 90% All Mechanical Equipment Flushed and Checked 30% All Hydrostatic Testing Complete 80% All Pumps Rotated and Tested 0% All Mechanical Systems Ready for Startup 0% All Electrical Equipment Statically Tested 0% All Electrical Systems read for startup 0% Milestone 8 Plant Commissioning & Testing Complete 0% GT Unit 3 Tested and Ready for Commercial Operation 70% Gas Compression Complete & Ready for PDVSA Gas 0% All Mechanical auxiliary and Balance of Plant Equipment Ready for Commercial Operation 0% All Buildings Finished and Complete 60% All Driveways and Finish Grading Complete 0% Major Milestones La Raisa Unit 300 Turned Over To Client 0% La Raisa Unit 100 Turned Over To Client 0% La Raisa Unit 200 Turned Over To Client 0% |
| STAFFING PLANS |  |
| CRITICAL AREAS OF CONCERN | We are waiting for BOP material from the port and airport. We waiting for Waiting on pipe fittings to complete plant piping (The work are delayed) |
| GENERAL COMMENTS | No Fittings for Concimeca to continue the fabrication piping tasks. |