Electricidad de Caracas LM2500 Tacoa Power Plant Technical Scope Document

3.0          Equipment List – Detailed Division of Responsibility

Material/Responsibility OWNER

Qty                Description

1 Lot 1 Lot

1 Lot

1 Lot 1 Lot 1 Lot

1 Lot 1 Lot 1 Lot 1 Lot 1 Lot

Natural Fuel Gas supply at the Arrecifes Power House

Fuel Gas and Liquid Fuel for Commissioning / Start-up that meets PDVSA

Specifications supplied to Contractor by EDC.

Raw Water Supply and Fire Water Supply will be obtained from the existing

TACOA Systems.

Raw Water for Commissioning and Startup

Waste Oil Disposal from the existing tank at the Arrecife Power House

Permits for Environmental, Importation, Transportation, Building, Operations,

etc. to allow plant construction and commercial operations

Construction & Commissioning Water and 480V three phase power

Access Roads to site

Import Duties and Taxes

Construction lay down area

Owner Supplied Equipment

Right of Way, easements etc. to allow proposed interconnects as required

GE LM2500 PE (60Hz) Dual Fueled Gas Turbine Generator packages Exhaust Stack with Silencers Modular Control Buildings with:

- Turbine Control Panel

- Generator Control Panel and Protection Panel

- 24 VDC Batteries and Chargers

- 125 VDC Batteries and Chargers

- 125 VDC Rundown motor starter

- 13.8 KV Generator Breaker Nema 3R Fuel Gas Compressors Liquid Fuel Centrifuges Instrument Air Compressor 600 KW Black Start Generator Demin Water Treatment System Potable Water Treatment System Liquid Fuel Pumps Potable Water Pumps 4.16 KV MCC for (3) Gas Compressors 100% Duplex Gas Guel Filter / Coalescer Skids 480 V BOP MCC Demin Water Forwarding Pump and Filter Skid

CONTRACTOR -ProEnergy EPC Responsibility

1 Lot 1 Lot 1 Lot 1 Lot 1 Lot 1 Lot

Civil/Structural

Site Preparation, Rough Grading, Excavation, Final Grading and Fencing Construction Tools, Rental Equipment & Rental Cranes Temporary Power Distribution Plant Concrete Foundations

Plant Paving, Gravel and Pads for the GTG Turbines and Generators Structural piping supports, platforms, ladders, and Misc structural steel supports. (Note: Platforms and ladders for the exhaust stacks to be furnished by Owner)

Buildings

Water Treatment Building Liquid Fuel Treatment Shed Gas Compressor Shed

1-3

Revision 3 April 23, 2009

Section 2.0 Scope of Work and Supply

Electricidad de Caracas LM2500 Tacoa Power Plant Technical Scope Document

1 1 Lot

I Lot

1 2

Material/Responsibility Contractor (Continued) Mechanical

Qty                Description

Fuel Gas Plant ESD Valve

Furnish and install carbon steel pipe from tie-in point at the Arrecifes Power

House to fuel gas compressors and to each GTG fuel gas filter

Furnish and Install stainless Steel piping from GTG fuel gas filter to the GTG

gas fuel connection

Fire Water System with HDPE Pipe Loop, Monitors and Controls

21,000 Fiberglass Demin Water Storage Tanks

1	Oily Water Separator

1	Waste Water Tank 5,000 Gallon w/waste water pump to Truck for disposal

1	Waste Oil Delivery Pump to Truck for disposal

- 21,000 Gallon Liquid Fuel Storage Day Tanks

- Liquid Fuel Forwarding Pumps 1 Lot            Furnish and Install carbon steel piping from the liquid fuel supply to the liquid

fuel treatment. 1 Lot            Furnish and Install Stainless Steel piping from the liquid fuel treatment to the liquid fuel day tank, GTG liquid fuel filters and to the GTG liquid fuel connection

1 Lot

1	Lot

2

2	sets
2
1
1

1 Lot 1 1

1 Lot 1 Lot 1 Lot 1 Lot 1 Lot 1 Lot

HDPE – steel – SS Pipe, Valves and Fittings with Insulation as required Mechanical Labor

Electrical

13.8 KV Fused Disconnects (Station Service) NEMA 3R

13.8 KV Cable Bus

13.8 KV / 480 V 750 KVA Station Service Transformers

13.8KV/4160 V 2000 MVA transformer for fuel gas compressors

480 V Distribution Switch Board

BOP 480/240 V Transformers, Lights, Panels etc

120 V UPS System for Control Room

Plant Grounding Grid

Lightning Protection

Cathodic Protection for underground steel piping

Area Lighting

480 V Welding Receptacles

Electrical Labor

Local Subcontractor(s) Civil, Electrical & Mechanical Craft Labor

Instrumentation & Control

1 Lot 1 1 Lot

1 Lot 1 Lot 1 Lot 1 Lot 1 Lot 1 Lot 1 Lot

1 Lot 1 Lot 1 Lot 1 Lot 1 Lot

Plant Instrumentation

DCS PLC

I&C Installation and Construction

Construction

Major Equipment Erection

Mechanical Installation and Construction

Construction Tools, Rental Equipment & Rental Cranes

Lubricants, Chemicals, Filters, etc. for Plant commissioning and Start up

Balance of Plant Start up and Commissioning Spare Parts

Plant Commissioning and Performance Testing

Overall Plant Training

Engineering

Conceptual and Detail Design Engineering (Total Plant)

Project Detail Engineering

Project Manuals including O&M, Warranty, and Engineering Calculations

As Built Drawings

Recommended Vendor Spare Parts List

2-3

Revision 3 April 23, 2009

Section 2.0 Scope of Work and Supply

Electricidad de Caracas LM2500 Tacoa Power Plant Technical Scope Document

Material/Responsibility Contractor (Continued) Project Management

Qty                Description

1 Lot            Project Management with QA/QC, Safety, and Training

1 Lot            Project Manuals including Project Procedures, Systems Turnover Manuals,

Project Implementation, QA/QC, Safety and Training 1 Lot            Training

Section 2.0 Scope of Work and Supply

3-3

Revision 3 April 23, 2009