Electricidad de Caracas LM2500 Tacoa Power Plant Technical Scope Document

Section 4.0    Design Basis and Interconnection Points 4.1            Design Basis

Design Conditions

Site Elevation

Design Air Temperature

Air Temperature, Low

Maximum Wind Velocity

Design Relative Humidity

Seismic Zone

Fuel Gas Supply Pressure

Medium Voltage Interconnect

Instrument Air System

Demin. Water Supply (max liq. Fuel)

100 Ft.

80o F 75o F

100 mph

78%

4

230 psig minimum

13.8 KV

185 scfm

48 gpm

4.2          Interconnect Points

Interconnect Points with Owner Facilities

Fuel Gas

Plant Waste Water

Plant Waste Oil

Telephone

Fire Water Supply

Customer Meter Station 250 psig at Arrecife Power House

At existing waste water system

At waste oil tank at Arrecifes Power House

None

At existing Firewater System adjacent to the Site

Raw Water Supply          At existing Raw Water Tanks above the Site

Section 4.0 Design Basis

1-1

Revision 0 April 15, 2009