Electricidad de Caracas LM2500 Tacoa Power Plant Technical Scope Document

Section 5.0	Expected Performance Using Natural Gas and Diesel Fuel (Not Guaranteed)

The expected performance for the plant is presented in the performance calculations included in this section. Calculations were performed for operation on both Natural Gas and #2 Diesel for the LM2500 PE, with and without water injection, at the design conditions listed. A performance summary is attached on the following pages.

80DF; 78% RH; 100 ft (Design Conditions)

|  |  | Total (2) Units |  | Total (2) Units |  | Total (2) Units |  | Total (2) Units |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Natural Gas |  |  |  | Diesel |  |  |  |
|  | LM2500PE |  | LM2500PE Water Inject |  | LM2500PE |  | LM2500PE Water Inject |  |
| Gross GT Power ea. (kW) | 20894 |  | 22056 |  | 20973 |  | 22463 |  |
| Net LHV HR (BTU/kWh) | 9715 | 9711 | 10050 | 10046 | 9736 | 9732 | 10097 | 10093 |
| Net Power (kW) | 20393 | 40801 | 21477 | 42972 | 20597 | 41208 | 22022 | 44060 |
| Auxiliaries (kW) | 502 | 897 | 580 | 1141 | 375 | 737 | 441 | 865 |
| Fuel usage (pph) | 9956 | 19912 | 10850 | 21700 | 10960 | 21920 | 12150 | 24300 |
| Fuel usage (MMSCFD) | 5.1 | 10.2 | 5.6 | 11.2 | -- | -- | -- | -- |
| Fuel usage (gpm) | -- | -- | -- | -- | 25.3 | 50.6 | 28.1 | 56.2 |
| Fuel Chemical HHV/LHV ratio | 1.107 | 1.107 | 1.107 | 1.107 | 1.065 | 1.065 | 1.065 | 1.065 |
| Water Injection (pph) | N/A | N/A | 11320 | 22640 | N/A | N/A | 11990 | 23980 |
| Water Injection (gpm) | N/A | N/A | 22.6 | 45.3 | N/A | N/A | 24 | 48 |

Section 5.0 Expected Performance

1-1

Revision 0 April 15, 2009