Electricidad de Caracas LM6000 Tacoa Power Plant Technical Scope Document

Section 4.0    Design Basis and Interconnection Points 4.1 Design Conditions

Design Conditions (Assumed)

Site Elevation

Air Temperature, High

Air Temperature, Low

Maximum Wind Velocity

Relative Humidity

Seismic Zone

Fuel Gas Supply Pressure

Total NOx water Injection

Total Sprint water injection

High Voltage Interconnect

Instrument Air System

100 feet

80o F 75o F

100 mph

78%

4

230 psig minimum

37.5 gpm

36.2 gpm

13.8 KV At Owner GSU

185 scfm by Contractor

4.2          Interconnect Points

Interconnect Points with Owner Facilities

Fuel Gas

Plant Waste Water

Plant Waste Oil

13.8 KV

Telephone

Fire Water Supply

Downstream Customer Meter Station 230 psig at the Arrecifes Power House

A waste water interconnect to Owner’s existing Waste Water System

At waste oil tank pump to Owner’s truck

Owner’s 13.8 / 69KV GSU’s

None

At existing Main Firewater Header System adjacent to site

Raw Water Supply	At existing Raw Water Tanks above the site

Section 4.0 Design Basis

1-1

Revision 4 April 23, 2009