Electricidad de Caracas LM6000 Tacoa Power Plant Technical Scope Document

Section 5.0      Expected Performance – Using Natural Gas or Diesel Fuel – With/Without Inlet Chilling (Not Guaranteed)

The expected performance for the plant is presented in the performance calculations included in this section. Calculations were performed for operation on both Natural Gas for the LM6000 PC sprint and LM6000 PD sprint, with and without Chilling. A performance summary is included below with inlet air chilling to 48°F operating at the Design Conditions listed. Additional calculations were performed at higher ambient temperature for 48°F inlet air. A performance summary is attached on the following pages.

TACOA LM6000 PC Sprint & PD Sprint

| 80°F; 70% RH; 100 ft |  |  |  |
| --- | --- | --- | --- |
|  | Natural Gas 951.6 BTU/lb LHV |  |  |
|  | LM 6000 PC spt | LM 6000 PD spt | Total (Both) Units |
| Gross GT Power ea. (kW) | 45687 | 42401 | 88088 |
| Net LHV HR (BTU/kWh) | 8873 | 8601 | 8744 |
| Net Power (kW) | 44551 | 41367 | 85918 |
| Auxiliaries (kW) | 1136 | 1034 | 2170 |
| Fuel usage (pph) | 19910 | 17920 | 37830 |
| Fuel usage (MMSCFD) | 9.65 | 8.69 | 18.34 |
| Fuel Chemical LHV per GT (kBTU/h) | 395319 | 355802 | 751121 |
| Fuel Chemical HHV/LHV ratio | 1.105 | 1.105 | 1.105 |
| Water Injection (pph) | 18380 | N/A | 18380 |
| Water Injection (gpm) | 36.76 | N/A | 36.76 |
| Sprint (pph) | 9046 | 8992 | 18038 |
| Sprint (gpm) | 18.09 | 17.98 | 36.07 |

Section 5.0 Expected Performance

1-2

Revision 3 April 15, 2009

Electricidad de Caracas LM6000 Tacoa Power Plant Technical Scope Document

| Inlet chilled to 48⁰F w/ < 4000 tons total chilling (about 2900 tons for these conditions) |  |  |  |
| --- | --- | --- | --- |
| 80°F; 70% RH; 100 ft |  |  |  |
|  | Natural Gas 951.6 BTU/lb LHV |  |  |
|  | LM 6000 PC spt | LM 6000 PD spt | Total (Both) Units |
| Gross GT Power ea. (kW) | 51143 | 46977 | 98120 |
| Net LHV HR (BTU/kWh) | 8871 | 8503 | 8695 |
| Net Power (kW) | 49315 | 45286 | 94601 |
| Auxiliaries (kW) | 1829 | 1691 | 3520 |
| Fuel usage (pph) | 22040 | 19396 | 41436 |
| Fuel usage (gpm) | 10.69 | 9.41 | 20.1 |
| Fuel Chemical LHV per GT (kBTU/h) | 437476 | 385076 | 822552 |
| Fuel Chemical HHV/LHV ratio | 1.105 | 1.105 | 1.105 |
| Water Injection (pph) | 23220 | N/A | 23220 |
| Water Injection (gpm) | 46.44 | N/A | 46.44 |
| Sprint (pph) | 8600 | 6880 | 15480 |
| Sprint (gpm) | 17.2 | 13.8 | 31 |

Section 5.0 Expected Performance

2-2

Revision 3 April 15, 2009