## Recap
ProEnergy EPC
Job Description: |  |  | "2 ea LM 6000's "
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  |  | 2009-04-10
I. Balance of Plant
100 Civil Structural
|  | 101 | Site Preparation |  |  |  | 39.3333 | calc
|  | 102 | Excavation - Fill |  |  | Mhrs | 120 | calc
|  | 103 | Concrete Foundations |  |  | 6486.2963 | 843.2185 | calc
|  | 104 | Concrete Pilings |  |  |  | 0 | calc
|  | 105 | Paving Asphalt - Concrete |  |  |  | 276.0185 | calc
|  | 106 | Gravel - Sand |  |  |  | 41.8074 | calc
|  | 107 | Structual Steel |  |  |  | 119 | calc
|  | 108 | Fencing |  |  |  | 18 | calc
|  | 109 | Architectual Treatment |  |  |  |  | calc
|  | 110 | Evaporation Pond |  |  |  |  | calc
[7 empty] | 1457.3778 |  | 1457.3778
| 200 Buildings | [5 empty] | 338.7 | calc | 338.7
| 300 Mechanical |  |  |  |  | Mhrs
|  | 310 | Major Mechanical Equipment |  |  |  | 4009 | calc
|  | 320 | Pipe, Valves & Fitting labor |  |  | 43200 | 985.6728 | calc
|  | 330 | Mechanical Subcontractor |  |  | 15372 | 350.7352 | calc
|  | 340 | Pipe, Valves & Fitting Material |  |  |  | 950 | calc
[7 empty] | 6295.408 |  | 6295.408
400 Electrical
|  | 410 | Major Electrical Equipment |  |  |  | 860.4 | calc
|  | 420 | Substation Equipment |  |  |  | 91.8 | calc
|  | 430 | Plant Electrical Subcontractor |  |  | 16988.4 | 387.6158 | calc
|  | 440 | Substation Subcontractor |  |  | 676.8 | 15.4422 | calc
|  | 450 | Conduit, Cable & Wire Material |  |  |  | 1050 | calc
|  | 460 | Conduit, Cable & Wire Labor |  |  | 32400 | 739.2546 | calc
[7 empty] | 3144.5126 |  | 3144.5126
500 Instrumentation
|  | 510 | CEMS |  |  |  |  | calc
|  | 520 | Plant Instrumentation |  |  |  | 105 | calc
|  | 530 | Instrumentation Subcontractor |  |  | 2160 | 49.2836 | calc
[7 empty] | 154.2836 |  | 154.2836
600 DCS System / Communications
|  | 610 | Hardware / Software/ON Site support |  |  |  | 560 | calc
|  | 620 | Telephone System |  |  |  | 15 | calc
|  | 630 | Public Address System |  |  |  | 10 | calc
|  | 640 | TV / Security |  |  |  | 15 | calc
[7 empty] | 600 |  | 600
700 Plant Erection
|  | 700 | Plant Erection |  |  | 16236 | 370.4487 | calc
|  | 750 | Plant Dismantling |  |  |  | 0 | plgd/1000
|  | 755 | Plant Dismantling Labor |  |  |  | 0 | plgd/1000
|  |  |  | Total El/Mech Mhrs |  | 127033.2 | 370.4487 |  | 370.4487
| 800 Equipment Rental | [5 empty] | 537.2 | calc | 537.2
| 900 Painting | [5 empty] | 235 | calc | 235
1000 Transportation
|  | 1001 | US Inland Transportation |  |  |  | 293.8 | calc
|  | 1002 | Ocean/Air Freight BOP |  |  |  |  | plgd /1000
|  | 1003 | Destination Inland Freight |  |  |  |  | plgd /1000
|  | 1004 | Customs / Duties (plant equip & mat'l) |  |  |  | 0 | plgd /1000
|  | 1005 | Unload & Receive Mat'l at Site |  |  |  | 0 | plgd /1000
|  | 1006 | Receive, Inspect, Inventory |  |  |  | 0 | plgd /1000
|  | 1007 | Storage |  |  |  | 0 | plgd /1000
|  | 1008 | Local Registrations Fees, License, Etc. |  |  |  | 0 | plgd /1000
|  | 1009 | Transport of Damaged Goods for Repair |  |  |  | 0 | plgd /1000
[7 empty] | 293.8 |  | 293.8
| 1100 Site Costs | [5 empty] | 335.8 | calc | 335.8
1200 Engineering
|  | 1201 | EPC Eng Labor |  |  |  | 735 | calc
|  | 1202 | Local Eng |  |  |  | 85 | calc
[7 empty] | 820 |  | 820
1300 Project Management
|  | 1310 | Project & Construction |  |  |  | 1447 | calc
|  | 1320 | Inspectors |  |  |  | 287.5 | calc
[7 empty] | 1734.5 |  | 1734.5
1400 Travel & Perdiem
|  | 1410 | Project Meal Expense |  |  |  | 634.8 | calc
[7 empty] | 634.8 |  | 634.8
| 1500 Technical Reps |  |  |  |  | $/day
|  | 1501 | GTG Tech Rep |  | 90 | 2200 | 198 | plgd /1000
|  | 1502 | Fire Water |  | 15 | 2000 | 30 | plgd /1000
|  | 1503 | Gas Compressor |  | 20 | 2000 | 40 | plgd /1000
|  | 1504 | Chiller |  | 0 | 2000 | 0 | plgd /1000
|  | 1505 | Water Treatment |  | 20 | 2000 | 40 | plgd /1000
|  | 1506 | Commission / S/U / Trng |  | 100 | 2000 | 200 | plgd /1000
|  | 1507 | Controls Rep |  | 90 | 2000 | 180 | plgd /1000
|  | 1508 | Liquid Fuel |  |  | 2000 | 0 | plgd /1000
|  | 1509 | SCR |  | 0 | 2000 | 0 | plgd /1000
[7 empty] | 688 |  | 688
1600 Project Tests
|  | 1601 | Soil Boring / Compaction |  |  |  | 15 | plgd /1000
|  | 1602 | Concrete |  |  |  | 45 | plgd /1000
|  | 1603 | X Ray |  |  |  | 45 | plgd /1000
|  | 1604 | Plant Performance and Reliability |  |  |  | 150 | plgd /1000
|  | 1605 | Emission Tests |  |  |  | 0 | plgd /1000
|  | 1606 | Protective Relays |  |  |  | 20 | plgd /1000
|  | 1607 | Acoustics / Noise Test |  |  |  | 0 | plgd /1000
[7 empty] | 275 |  | 275
| 1700 Legal | [5 empty] | 50 | plgd /1000 | 50
1800 Insurance / Securities
|  | 1810 | Bonds |  |  |  | 0 | plgd /1000
|  | 1820 | Buildiers All Risk |  |  |  | 300 | plgd /1000
|  | 1830 | Marine / Cargo |  |  |  | 0 | plgd /1000
|  | 1840 | Professional |  |  |  | 0 | plgd /1000
[7 empty] | 300 |  | 300
| 1900 Taxes | [6 empty] | calc | 0
| 2000 Commissions | [5 empty] | 0 | plgd /1000 | 0
2100 Project Contingency / Risk
|  | 2110 | Project Contingency |  |  |  | 350 | plgd / 1000
|  | 2120 | GT Performance |  |  |  | 0 | plgd / 1000
|  | 2130 | Schedule LD |  |  |  | 0 | plgd / 1000
|  | 2140 | Material Escalation |  | 3% | 7666.2 | 229.986 | calc
|  | 2150 | Labor Contingency |  | 3% | 2898.453 | 86.9536 | calc
[7 empty] | 666.9396 |  | 666.9396
[5 empty] | BOP Cost |  |  |  | 18931.7704
[5 empty] | % Markup |  |  |  | 5200
[5 empty] | BOP Sales Price |  |  |  | 24131.7704
[5 empty] | 2% | Neil Karr Commission |  |  | 483
[5 empty] | Total Sale Price Rounded |  |  | 24700 | 24614.7704

## 101 Site Prep
|  |  | SITE PREP | [6 empty] | 101
(1,000's)
Project Name: |  | TACOA LM 6000 Power Plant | [5 empty] | Date: |  | 2009-04-10
Customer: |  | Electricidad de Caracas | [5 empty] | Quote No: |  | T 9003 B - 1
Location: |  | Venzuela | [5 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | "L" | "W" | "D" | Square | Square | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Clearing/Grubbing |  |  | 200 | 300 | 1 | 60000 | 2222.2222 | 15 | 33333.3333
2
3 | Demolition
4
5 | Special Shoring
6
7 | Drainage |  |  | 600 | 6 | 3 | 10800 | 400 | 15 | 6000
8
9 | Dewatering
10
11 | Railroads
12
13 | Docks
14
15 | Tunnels
16
17 | Wells
18
19 | Containment Systems
20
21 | Concrete Work
22
23 | Masonry
24
25
26
27
28
29
30
31
32
33
34
39.3333

## 102 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 102
(1,000's)
Project Name: |  | TACOA LM 6000 Power Plant | [6 empty] | Date: |  | 2009-04-10
Customer: |  | Electricidad de Caracas | [6 empty] | Quote No: |  | T 9003 B - 1
Location: |  | Venzuela | [6 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
2 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
3 | Control/Office/Maint |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
4 | Water Treatment Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
5 | Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
6 | Pwr Blk Utility Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
7 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
8 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
9 | Liquid Fuel Unloading Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
10
11 | Main Plant Area |  |  |  | 200 | 300 | 4.5 | 270000 | 10000 | 12 | 120000
12 | Fill |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
13 | Substation Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 |  |  | Total Cost of Excavation and Fill | [7 empty] | 120

## 103 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 103
(1,000's)
Project Name: |  | TACOA LM 6000 Power Plant | [7 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [7 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total | 5
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price | mhr/cy
1 | POWER ISLAND |  |  | Price: 650
2 | GT Generators |  |  | 2 | 65 | 20 | 4 | 10400 | 385.1852 | 650 | 250370.3704 | 1925.9259
3 | Exhaust Stack |  |  | 2 | 25 | 25 | 4 | 5000 | 185.1852 | 650 | 120370.3704 | 925.9259
4 | HRSG |  |  | 0 | 75 | 16 | 4 | 0 | 0 | 650 | 0 | 0
5 | SCR |  |  | 0 | 52 | 16 | 4 | 0 | 0 | 650 | 0 | 0
6 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
7 | STG Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
8 | STG Inlet Chillers |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
9 | STG Condenser Fndn |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
10 | Aux Skid(s) for GTG |  |  | 2 | 15 | 20 | 1 | 600 | 22.2222 | 650 | 14444.4444 | 111.1111
11
12
13 | BALANCE OF PLANT
14 | Chiller |  |  | 0 | 45 | 55 | 2 | 0 | 0 | 650 | 0 | 0
15 | Fuel Gas Regulator Skid |  |  | 2 | 18 | 8 | 1 | 288 | 10.6667 | 650 | 6933.3333 | 53.3333
16 | Fuel Gas GTG Meter Skid |  |  | 1 | 25 | 6 | 1 | 150 | 5.5556 | 650 | 3611.1111 | 27.7778
17 | Fin Fan L O Coolers |  |  | 2 | 15 | 15 | 2 | 900 | 33.3333 | 650 | 21666.6667 | 166.6667
18 | Gas Compressors |  |  | 1 | 45 | 25 | 3 | 3375 | 125 | 650 | 81250 | 625
19 | Fuel Gas Plant Metering Skid |  |  | 1 | 15 | 8 | 1 | 120 | 4.4444 | 650 | 2888.8889 | 22.2222
20 | Comp Fin Fans |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 650 | 0 | 0
21 | Waste Oil/Water Storage Tank |  |  | 1 | 15 | 12 | 1 | 180 | 6.6667 | 650 | 4333.3333 | 33.3333
22 | Oily Water Separator |  |  | 1 | 30 | 20 | 0.5 | 300 | 11.1111 | 650 | 7222.2222 | 55.5556
23 | Lubricant Storage Area |  |  | 1 | 45 | 30 | 1 | 1350 | 50 | 650 | 32500 | 250
24 | Instrument Air Comp Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 650 | 1925.9259 | 14.8148
25 | Pipe Rack Stanchons |  |  | 20 | 2.5 | 2.5 | 6 | 750 | 27.7778 | 650 | 18055.5556 | 138.8889
26 | 15KV Cable Tray Stanchons |  |  | 0 | 2.5 | 2.5 | 6 | 0 | 0 | 650 | 0 | 0
27 | Fire Water Pump Skid |  |  | 0 | 18 | 33 | 1 | 0 | 0 | 650 | 0 | 0
28 | Area Light Poles |  |  | 6 | 2.5 | 3 | 5 | 225 | 8.3333 | 650 | 5416.6667 | 41.6667
29 | Aux Trans fndns |  |  | 4 | 10 | 15 | 1.5 | 900 | 33.3333 | 650 | 21666.6667 | 166.6667
30 | Cable Trenches see est |  |  | 2 | 160 | 12 | 0.5 | 1920 | 71.1111 | 650 | 46222.2222 | 355.5556
31 | Water Treatment Plant |  |  | 1 | 30 | 40 | 1 | 1200 | 44.4444 | 650 | 28888.8889 | 222.2222
0 | Liquid Fuel Tank 20M gal |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 650 | 0 | 0
1 | Liquid Fuel Treatment systm |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 650 | 0 | 0
2 | Liquid Fuel Forwarding Pmps |  |  | 0 | 6 | 5 | 1 | 0 | 0 | 650 | 0 | 0
3 | Demin Water Pump skid |  |  | 2 | 8 | 6 | 1 | 96 | 3.5556 | 650 | 2311.1111 | 17.7778
4 | Demin Stg Tanks 20M Gal |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 650 | 10833.3333 | 83.3333
5 | Demin Forwarding Pumps |  |  | 4 | 8 | 6 | 1 | 192 | 7.1111 | 650 | 4622.2222 | 35.5556
6 | Chemical Injection Skid |  |  | 0 | 15 | 10 | 0 | 0 | 0 | 650 | 0 | 0
7 | Raw Water Tank Base |  |  | 0 | 50 | 50 | 1 | 0 | 0 | 650 | 0 | 0
8 | Fire Water Tank base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
9 | Emer Generator Base |  |  | 0 | 23 | 12 | 2 | 0 | 0 | 650 | 0 | 0
10
11 | BUILDINGS
12 | Control Bldg/Office |  |  | 1 | 40 | 40 | 1 | 1600 | 59.2593 | 650 | 38518.5185 | 296.2963
13 | Warehouse/Maintenance |  |  | 1 | 50 | 40 | 1 | 2000 | 74.0741 | 650 | 48148.1481 | 370.3704
14 | Water Treatment Bldg |  |  | 1 | 30 | 40 | 1 | 1200 | 44.4444 | 650 | 28888.8889 | 222.2222
15 | Gas Compressor Shed |  |  | 1 | 50 | 35 | 1 | 1750 | 64.8148 | 650 | 42129.6296 | 324.0741
16 | Electrical Bldg |  |  | 0 | 42 | 12 | 1 | 0 | 0 | 650 | 0 | 0
17 | Pwr Blk Utility Bldg's |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 650 | 0 | 0
18 | Substation Bldg |  |  | 0 | 15 | 12 | 1 | 0 | 0 | 650 | 0 | 0
19 | Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0
20 | Liquid Fuel Unloading |  |  | 0 | 60 | 25 | 1 | 0 | 0 | 650 | 0 | 0
21 | Fuel Shed |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 650 | 0 | 0
22 | Guard Bldg |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 650 | 0 | 0
23
24 | SUBSTATION
25 | GSU Transformer |  |  | 0 | 30 | 30 | 3 | 0 | 0 | 650 | 0 | 0
26 | (___)KV SF6 Circuit Breaker |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 650 | 0 | 0
27 | (___)KV Disc Switch w/ Stand |  |  | 0 | 10 | 15 | 1 | 0 | 0 | 650 | 0 | 0
28 | Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 650 | 0 | 0
29 | Transmission Line Poles |  |  | 0 | 5 | 5 | 20 | 0 | 0 | 650 | 0 | 0
30 | Insulator Support Base |  |  | 0 | 3 | 3 | 3 | 0 | 0 | 650 | 0 | 0
31 | PT Support Base |  |  | 0 | 3 | 3 | 3 | 0 | 0 | 650 | 0 | 0
32 | Static Pole Base |  |  | 0 | 3 | 3 | 5 | 0 | 0 | 650 | 0 | 0
33
34
35 |  |  | Total Cost of Foundations | Cubic: 1297.2593; Total: 843.2185 | 6486.2963
Note on K12: Insert Rate Here:

## 105 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 105
Project Name: |  | TACOA LM 6000 Power Plant | [6 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [6 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 | 500 | 0
2 | Gen Removal Areas |  |  | 40 | 30 | 1 | 1200 | 44.4444 | 500 | 22222.2222
3 | Turbine Removal Areas |  |  | 30 | 30 | 1 | 900 | 33.3333 | 500 | 16666.6667
4 | Entry Ways |  |  | 30 | 15 | 0.5 | 225 | 8.3333 | 500 | 4166.6667
5 | Walk ways |  |  | 60 | 6 | 0.5 | 180 | 6.6667 | 500 | 3333.3333
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 500 | 0
7
8
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 450 | 20 | 0.5 | 4500 | 166.6667 | 500 | 83333.3333
12 | Parking Lot |  |  | 100 | 50 | 0.5 | 2500 | 92.5926 | 500 | 46296.2963
13 | [6 empty] | 0 | 0 |  | 0
14 | Retaining Wall |  |  | 500 | 9 | 1 | 4500 | 166.6667 | 600 | 100000
15 | [6 empty] | 0 | 0 |  | 0
16 | [6 empty] | 0 | 0 |  | 0
17 | [6 empty] | 0 | 0 |  | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
36 | [6 empty] | 0 | 0 |  | 0
37 | [6 empty] | 0 | 0 |  | 0
38 | [6 empty] | 0 | 0 |  | 0
39 | [6 empty] | 0 | 0 |  | 0
40 | [9 empty] | 276.0185
Note on J12: Insert Rate Here:

## 106 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 106
Project Name: |  | TACOA LM 6000 Power Plant | [7 empty] | Date: |  | 2009-04-10
Customer: |  | Electricidad de Caracas | [7 empty] | Quote No: |  | T 9003 B - 1
Location: |  | Venzuela | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 200 | 300 | 0.5 | 30000 | 1111.1111 | 1844.4444 | 20 | 36888.8889
3
4 | Cooling Tower Area |  |  | 0 | 110 | 160 | 0.5 | 0 | 0 | 0 | 20 | 0
5 |  |  |  | Price: 20
6 | Substation |  |  | 0 | 400 | 150 | 1 | 0 | 0 | 0 | 20 | 0
7 |  |  |  | Price: 20
8 | Road ways |  |  | 1 | 400 | 20 | 0.5 | 4000 | 148.1481 | 245.9259 | 20 | 4918.5185
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Gravel | Total: 41.8074

## 107 Structural
STRUCTUAL STEEL
[5 empty] | (1,000's) |  |  |  | 107
Project Name: |  | TACOA LM 6000 Power Plant | [5 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [5 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | # of | Qty | Price | Total
No. | [5 empty] | Lbs / Tons |  |  | Price
1
2
3 | Misc Pipe Rack supports etc. | [5 empty] | 14 | 3500 | 49000
4 | [8 empty] | 0
5 | 15 KV Cable Tray Stanchons | [5 empty] | 0 | 3000 | 0
6 | [8 empty] | 0
7 | GTG walkways and stairs | [5 empty] | 2 | 15000 | 30000
8 | [8 empty] | 0
9 | Structual Steel for equip supports | [5 empty] | 0 | 0 | 0
10
11 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 1 | 15000 | 15000
12
13 | Steel Cover for Storm Water Catch Basin | [5 empty] | 1 | 5000 | 5000
14
15 | Steel Grating Walkways over pipe ways/ Comp Bldg | [5 empty] | 0 | 0 | 0
16
17 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 20000 | 20000
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41 |  |  | Total Cost of Stuctual Steel | [5 empty] | 119

## 108 Fence
FENCING
[5 empty] | (1,000's) |  |  | 108
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1200 | 15 | 18000
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 0 | 23 | 0
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 0 | 4000 | 0
10 | Motor Operated Double Gate(s) |  |  |  |  | 0 | 7500 | 0
11 | Personnel Gate(s) |  |  |  |  | 0 | 400 | 0
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 0 | 7000 | 0
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Fencing |  |  |  |  | 18

## 200 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 200
Project Name: |  | TACOA LM 6000 Power Plant | [5 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [5 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
No. |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 50 | 40 | 2000 | 40 | 80000
2 | Control/Office |  |  |  | 40 | 40 | 1600 | 65 | 104000
3 | Water Treatment |  |  |  | 30 | 40 | 1200 | 45 | 54000
4 | Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0
5 | Warehouse/Maintenance |  |  |  | 50 | 40 | 2000 | 50 | 100000
6 | Substation Bldg |  |  |  | 0 | 12 | 0 | 35 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Treatment |  |  |  | 0 | 20 | 0 | 35 | 0
9 | Fuel Shed |  |  |  | 0 | 30 | 20 | 35 | 700
10 | Control Room |  |  |  | 0 | 0 | 0 | 0 | 0
11 | Entry Guard House |  |  |  | 0 | 15 | 0 | 40 | 0
12 |  |  |  |  | 0 | 0 | 0 | 0 | 0
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39 |  |  | Total Cost of Other Buildings | [5 empty] | 338.7

## 310, 320, 330 & 340 Mechanical
MECHANICAL EQUIPMENT and Labor
(1,000's)
310 & 330
Project Name: |  | TACOA LM 6000 Power Plant | [9 empty] | Date: |  | 2009-04-10
Customer: |  | Electricidad de Caracas | [9 empty] | Quote No: |  | T 9003 B - 1
Location: |  | Venzuela | [9 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
| GTG |  |  | Unit: 3%; Hours: 9
1 | GTG Type GE LM 6000 PC |  |  | 2 | 0 | 0 | 0 | 0 | 9 | 6 | 35 | 3780 | 22.8165 | 86246.37
2 | Lube oils and Chemicals |  |  | 2 | 40000 | 80000 | 1000 | 2000 | 9 | 2 | 3 | 108 | 22.8165 | 2464.182
3 | Exhaust Stack |  |  | 2 | 200000 | 400000 | 40000 | 80000 | 9 | 3 | 2 | 108 | 22.8165 | 2464.182
4 | Project Grouting |  |  | 2 | 50000 | 100000 | 500 | 1000 | 9 | 0 | 0 | 0 | 22.8165 | 0
5 | GTG Tools |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 0 | 0 | 0 | 22.8165 | 0
6 | Anchor Bolts |  |  | 2 | 50000 | 100000 | 1000 | 2000 | 9 | 0 | 0 | 0 | 22.8165 | 0
7
8 | HRSG
9 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
10 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
11 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
12 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
13 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
14 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
15
16 | SCR
17 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
18 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
19
20 | STG
21 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
22 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
23 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
24 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
25 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
26 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
27
28 | Inlet Air Conditioning System
29 | Inlet Chilling Package 4000 Tons |  |  | 0 | 3000000 | 0 | 30000 | 0 | 9 | 6 | 40 | 0 | 22.8165 | 0
30 | Inlet Fogging System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
31 | Inlet Evap Cooling System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
32 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
33 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
34 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
35 | Chemical Inj Skid |  |  | 0 | 15000 | 0 | 0 | 0 | 9 | 2 | 3 | 0 | 22.8165 | 0
36
37 | Fuel Gas Systems
38 | Fuel Gas compressor w/ Fin Fans |  |  | 3 | 650000 | 1950000 | 10000 | 30000 | 9 | 4 | 8 | 864 | 22.8165 | 19713.456
39 | Fuel Gas Check Metering/Regulator Skid |  |  | 1 | 155000 | 155000 | 2000 | 2000 | 9 | 3 | 4 | 108 | 22.8165 | 2464.182
40 | Fuel Gas Turbine Metering Skid |  |  | 0 | 145000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
41 | Fuel Gas Filter Skid & Mnt (___) KW Htr(Htr in Elect) |  |  | 2 | 145000 | 290000 | 2500 | 5000 | 9 | 3 | 5 | 270 | 22.8165 | 6160.455
42 | ESD Valve, ___" ___# |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 1 | 18 | 22.8165 | 410.697
43
44 | Liquid Fuel Systems
45 | Unloading Pump Skid |  |  | 0 | 20000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
46 | Metering Skid |  |  | 0 | 135000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
47 | Forwarding Pump Skid |  |  | 0 | 30000 | 0 | 750 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
48 | Transfer Pump Skid |  |  | 0 | 24000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
49 | Fuel Heating |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
50 | Filters |  |  | 0 | 12000 | 0 | 500 | 0 | 9 | 2 | 1 | 0 | 22.8165 | 0
51 | Centrifuge |  |  | 0 | 250000 | 0 | 25000 | 0 | 9 | 3 | 5 | 0 | 22.8165 | 0
52 | Injection Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
53 | Storage Tank 250M Gal |  |  | 0 | 300000 | 0 | 15000 | 0 | 9 | 3 | 4 | 0 | 22.8165 | 0
54 | Day Tank |  |  | 0 | 25000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 22.8165 | 0
55
56 | Water Supply System
57 | Raw Water Storage Tank 750 M gal |  |  | 0 | 420000 | 0 | 25000 | 0 | 9 | 3 | 5 | 0 | 22.8165 | 0
58 | Raw Water Supply Pumps |  |  | 2 | 14000 | 28000 | 840 | 1680 | 9 | 2 | 3 | 108 | 22.8165 | 2464.182
59 | Raw Water Forwarding Pumps |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 2 | 4 | 144 | 22.8165 | 3285.576
60
61 | Water Treatment System
62 | Multi Media Filter Package |  |  | 0 | 65000 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 22.8165 | 0
63 | Water Injection Skid |  |  | 0 |  | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
64 | Demin Treatment 150m GPD |  |  | 1 | 400000 | 400000 | 25000 | 25000 | 9 | 4 | 20 | 720 | 22.8165 | 16427.88
65 | Demin Storage SS Tank 350M gal |  |  | 0 | 25000 | 0 | 20000 | 0 | 9 | 3 | 6 | 0 | 22.8165 | 0
66 | Demin water fiberglass tank |  |  | 2 | 20000 | 40000 | 2000 | 4000 | 9 | 3 | 5 | 270 | 22.8165 | 6160.455
67 | Demin forwarding pump skids |  |  | 2 | 30000 | 60000 | 3000 | 6000 | 9 | 2 | 4 | 144 | 22.8165 | 3285.576
68 | Demin Filter Skid |  |  | 4 | 14000 | 56000 | 1680 | 6720 | 9 | 2 | 3 | 216 | 22.8165 | 4928.364
69 | Demin Water Tank, SS 300M gal |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
70
71 | Waste Water and Oil Storage and Transfer
72 | Oily Water Separator |  |  | 1 | 50000 | 50000 | 2000 | 2000 | 9 | 3 | 8 | 216 | 22.8165 | 4928.364
73 | Oily Waste Tank 10000 gal |  |  | 1 | 10000 | 10000 | 300 | 300 | 9 | 2 | 2 | 36 | 22.8165 | 821.394
74 | Waste Water Tank 10000 gal |  |  | 0 | 10000 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
75 | Waste Oil and Water forwarding pumps w/ skid |  |  | 2 | 10000 | 20000 | 600 | 1200 | 9 | 2 | 2 | 72 | 22.8165 | 1642.788
76
77 | Fire Control Systems
78 | Fire Water Pump Skids (Diesel / Electric) |  |  | 0 | 650000 | 0 | 20000 | 0 | 9 | 4 | 7 | 0 | 22.8165 | 0
79 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 85000 | 85000 | 2550 | 2550 | 9 | 4 | 12 | 432 | 22.8165 | 9856.728
80
81 | Storm Water System
82 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
83 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
84 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
85
86 | Other Systems
87 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 70000 | 70000 | 2500 | 2500 | 9 | 2 | 4 | 72 | 22.8165 | 1642.788
88 | Potable Water System |  |  | 1 | 20000 | 20000 | 600 | 600 | 9 | 0 | 0 | 0 | 22.8165 | 0
89 | Anti-Icing Ducting |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
90 | Sanitary Sewer |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
91 | Emergency Generator |  |  | 0 | 200000 | 0 | 5000 |  | 9 | 4 | 20 | 0 | 40 | 0
92
93 |  |  | Total Cost | Total: 4009; Frt: 178.3; Qty: 7686
94 |  |  |  | Total: 175.3676
[9 empty] | Total Manhours |  |  | 7686
[9 empty] | Times Prod Factor |  | 2 | 15372 | 22.8165 | 350.7352
95 | BOP Pipe, Valves and Fittings Labor |  |  | 1 | 950000 | 950000 | 28500 | 28500 | 9 | 15 | 160 | 21600 | 22.8165 | 492836.4
96 |  |  | Total Cost | Total: 950; Frt: 28.5; Qty: 21600; Total: 492836.4
97
98 |  |  |  | Hours: Total Manhours; Qty: 21600
99 |  |  |  | Hours: Times Prod Factor; Qty: 2; Qty: 43200; Rate: 22.8165; Total: 985.6728
Price per hour based with all labor burdens as follows:
[8 empty] | Local Hrly Cost |  | 10
[8 empty] | Fringes |  | 2.5
[8 empty] | Small Tools |  | 1.5
[8 empty] | Labor Burden 35% |  | 3.5
17.5
[8 empty] | Contr G&A 8% |  | 1.4
[8 empty] | Contr Mark up 15% |  | 2.625
21.525
[7 empty] | 45 | Hour Work Week = |  | 22.8165
Work Week Hours Multiplier
[7 empty] | 45 | 50 | 60
[7 empty] | 1.06 | 1.1 | 1.17
Note on K127: Insert Weekly M/hrs Here: Weekly M/hrs automatically calculated hrs/day.
Note on N119: Insert Rate Here:

## 410, 430, 450 & 460 Electrical
ELECTRICAL EQUIPMENT and Labor
(1,000's)
410, 430, 450 & 460
Project Name: |  | TACOA LM 6000 Power Plant | [11 empty] | Date: |  | 2009-04-10
Customer: |  | Electricidad de Caracas | [11 empty] | Quote No: |  | T 9003 B - 1
Location: |  | Venzuela | [11 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Power Island Equipment | [7 empty] | 3% |  | 9
2 | Gas Turbine Generator |  |  |  |  | 2 |  |  | 0 |  | 9 | 6 | 40 | 4320 | 22.8165 | 98567.28
3 | HRSG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 22.8165 | 0
4 | SCR |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 22.8165 | 0
5 | STG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 22.8165 | 0
6 | STG Cooling Tower |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 22.8165 | 0
7 | Chiller Package |  |  |  |  | 0 |  |  | 0 |  | 9 | 6 | 30 | 0 | 22.8165 | 0
8 | Water Treatment Package |  |  |  |  | 1 |  |  | 0 |  | 9 | 6 | 20 | 1080 | 22.8165 | 24641.82
9 | [13 empty] | 0 | 22.8165 | 0
10 | 15KV | [13 empty] | 22.8165
11 | Generator Breaker(s) |  |  |  |  | 1 | 135000 | 135000 | 1500 | 1500 | 9 | 3 | 5 | 135 | 22.8165 | 3080.2275
12 | GSU Protective Relay Panel |  |  |  |  | 2 | 35000 | 70000 | 1000 | 2000 | 9 | 2 | 4 | 144 | 22.8165 | 3285.576
13 | Fused Disconnect(s) |  |  |  |  | 2 | 20000 | 40000 | 500 | 1000 | 9 | 2 | 4 | 144 | 22.8165 | 3285.576
14 | Bus Duct |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 4 | 0 | 22.8165 | 0
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 22.8165 | 0
16 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 22.8165 | 0
17 | 5KV | [13 empty] | 22.8165
18 | Distribution Breaker(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 22.8165 | 0
19 | Fused Disconnect(s) |  |  |  |  | 1 | 15000 | 15000 | 500 | 500 | 9 | 2 | 6 | 108 | 22.8165 | 2464.182
20 | MCC's |  |  |  |  | 3 | 20000 | 60000 | 1500 | 4500 | 9 | 3 | 3 | 243 | 22.8165 | 5544.4095
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 22.8165 | 0
22 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 22.8165 | 0
23 | 600V | [13 empty] | 22.8165
24 | Distribution Panel(s) |  |  |  |  | 1 | 150000 | 150000 | 1000 | 1000 | 9 | 2 | 5 | 90 | 22.8165 | 2053.485
25 | GTG MCC(s) |  |  |  |  | 0 | 48000 | 0 | 1500 | 0 | 9 | 3 | 5 | 0 | 22.8165 | 0
26 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 22.8165 | 0
27 | STG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
28 | BOP MCC(s) |  |  |  |  | 1 | 40000 | 40000 | 1200 | 1200 | 9 | 2 | 3 | 54 | 22.8165 | 1232.091
29 | Water Treatment MCC(s) |  |  |  |  | 1 | 15000 | 15000 | 1000 | 1000 | 9 | 2 | 3 | 54 | 22.8165 | 1232.091
30 | Fuel Treatment MCC |  |  |  |  | 0 | 35000 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 22.8165 | 0
31 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
32 | Aux Transformer(s) | [13 empty] | 22.8165
33 | 15/5KV ___________ MVA |  |  |  |  | 1 | 75000 | 75000 | 5000 | 5000 | 9 | 3 | 5 | 135 | 22.8165 | 3080.2275
34 | 15/600V ___________ MVA |  |  |  |  | 2 | 45000 | 90000 | 5000 | 10000 | 9 | 3 | 5 | 270 | 22.8165 | 6160.455
35 | 600/120/208V ________ KVA |  |  |  |  | 1 | 5000 | 5000 | 150 | 150 | 9 | 2 | 4 | 72 | 22.8165 | 1642.788
36 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
37 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
38 | Area Lighting | [13 empty] | 22.8165
39 | Poles _______ High |  |  |  |  | 6 | 1600 | 9600 | 150 | 900 | 9 | 2 | 1 | 108 | 22.8165 | 2464.182
40 | Floodlights _______ Watts |  |  |  |  | 18 | 600 | 10800 | 50 | 900 | 9 | 2 | 0.3 | 97.2 | 22.8165 | 2217.7638
41 | [5 empty] | 0 | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
42 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 60 | 0 | 22.8165 | 0
43 | Other Systems | [13 empty] | 22.8165
44 | UPS |  |  |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 4 | 72 | 22.8165 | 1642.788
45 | DC |  |  |  |  | 1 | 35000 | 35000 | 1000 | 1000 | 9 | 2 | 4 | 72 | 22.8165 | 1642.788
46 | Cathodic Protection |  |  |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 3 | 8 | 432 | 22.8165 | 9856.728
47 | Lightning Protection |  |  |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 3 | 6 | 324 | 22.8165 | 7392.546
48 | [11 empty] | 0 | 0 | 0 | 22.8165 | 0
49 | [14 empty] | 22.8165
50 | Temporary Electric |  |  |  |  | 1 | 35000 | 35000 | 1050 | 1050 | 9 | 2 | 30 | 540 | 22.8165 | 12320.91
51 | Electrical Control Module |  |  |  |  | 0 | 80000 | 0 | 5000 | 0 | 9 | 5 | 6 | 0 | 22.8165 | 0
52 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
53 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
54 | [6 empty] | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 22.8165 | 0
55 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 860.4 |  | 35.75 |  |  |  | 8494.2 |  | 193.8079
[12 empty] | Productivity | 2 | 16988.4 | 22.8165 | 387.6158
56 | Cable Tray, Conduit, & Cable |  |  |  |  | 1 | 1050000 | 1050000 | 50000 | 50000 | 9 | 12 | 150 | 16200 | 22.8165 | 369627.3
57 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 1050 |  | 50 |  |  |  | 16200 |  | 369.6273
58 | [10 empty] | Total Manhours |  |  | 16200
59 | [10 empty] | Times Prod Factor |  | 2 | 32400 | 22.8165 | 739.2546
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 10
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 3.5
17.5
[13 empty] | Contr G&A 8% |  | 1.4
[13 empty] | Contr Mark up 15% |  | 2.625
21.525
[12 empty] | 45 | Hour Work Week = |  | 22.8165
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N87: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q79: Insert Rate Here:

## 420 & 440 Substation
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | TACOA LM 6000 Power Plant | [12 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [12 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [12 empty] | Est By:
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Unit: 3%; Hours: 9
2 | Main Power Transformer ____ KV, _______ MVA |  |  |  |  | 0 | 950000 | 0 | 75000 | 0 | 9 | 4 | 5 | 0 | 22.8165 | 0
3 | SF6 Circuit Breaker(s) ____ KV |  |  |  |  | 0 | 55000 | 0 | 5000 | 0 | 9 | 2 | 5 | 0 | 22.8165 | 0
4 | Disconnect Switches ______ KV |  |  |  |  | 0 | 15000 | 0 | 1500 | 0 | 9 | 2 | 4 | 0 | 22.8165 | 0
5 | Station Post Insulators ____ KV |  |  |  |  | 6 | 550 | 3300 | 50 | 300 | 9 | 2 | 0.05 | 5.4 | 22.8165 | 123.2091
6 | Insulator Stanchons ______ High |  |  |  |  | 6 | 500 | 3000 | 50 | 300 | 9 | 1 | 0.5 | 27 | 22.8165 | 616.0455
7 | Insulator Stanchons ______ High |  |  |  |  | 0 | 650 | 0 | 0 | 0 | 9 | 1 | 0.4 | 0 | 22.8165 | 0
8 | Dead End Tower(s) |  |  |  |  | 0 | 35000 | 0 | 2500 | 0 | 9 | 4 | 15 | 0 | 22.8165 | 0
9 | Alum Bus ______ Dia |  |  |  |  | 0 | 15 | 0 | 4 | 0 | 9 | 1 | 0.02 | 0 | 22.8165 | 0
10 | Alum Bus Conn's |  |  |  |  | 0 | 65 | 0 | 10 | 0 | 9 | 1 | 0.02 | 0 | 22.8165 | 0
11 | Alum Bus End Plugs _____ Dia |  |  |  |  | 0 | 25 | 0 | 5 | 0 | 9 | 1 | 0.05 | 0 | 22.8165 | 0
12 | Alum Bus Support Clamps |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.1 | 0 | 22.8165 | 0
13 | Alum Bus "V" Conn's |  |  |  |  | 0 | 350 | 0 | 0 | 0 | 9 | 1 | 0.08 | 0 | 22.8165 | 0
14 | Static Wire Poles, ____ High |  |  |  |  | 0 | 3000 | 0 | 100 | 0 | 9 | 3 | 1 | 0 | 22.8165 | 0
15 | Area Lighting Poles, ____ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 1 | 0 | 22.8165 | 0
16 | Flood Lights, ______ Watts |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
17 | #4/0 Grounding Conductor |  |  |  |  | 0 | 15000 | 0 | 700 | 0 | 9 | 3 | 10 | 0 | 22.8165 | 0
18 | 3/4"x10'-0" Ground Rods & Clamps |  |  |  |  | 0 | 15 | 0 | 0 | 0 | 9 | 1 | 0.04 | 0 | 22.8165 | 0
19 | #90 Cadweld Shots |  |  |  |  | 0 | 15 | 0 | 0 | 0 | 9 | 2 | 0.3 | 0 | 22.8165 | 0
20 | Metering CT's & CPT's |  |  |  |  | 1 | 35000 | 35000 | 500 | 500 | 9 | 2 | 5 | 90 | 22.8165 | 2053.485 | 0
21 | Station Metering w/ In & Out Capabilities |  |  |  |  | 1 | 50000 | 500 | 50 | 50 | 9 | 2 | 5 | 90 | 22.8165 | 2053.485
22 | Station Protective Relay(s) |  |  |  |  | 1 | 50000 | 50000 | 100 | 100 | 9 | 2 | 5 | 90 | 22.8165 | 2053.485
23 | Station RTU |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 22.8165 | 0
24 | 125V DC System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
25 | Transmission Line Poles |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 2 | 0 | 22.8165 | 0
26 | Transmission Line Strain Insulators |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 22.8165 | 0 | 0
27 | Cable Bus, Type _____, Size _____ |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 6 | 0 | 22.8165 | 0
28 | Main Power Transformer Oil, ______ Gal |  |  |  |  | 0 | 40000 | 0 | 1500 | 0 | 9 | 2 | 3 | 0 | 22.8165 | 0
29 | Main Power Transformer Dress Out & Test |  |  |  |  | 0 | 50000 | 0 | 1000 | 0 | 9 | 2 | 2 | 36 | 22.8165 | 821.394
30 | Fiber Optic Cable w/ Messenger Cable |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 22.8165 | 0 | 0
31 | Fiber Optic Cable Fittings & Terminations |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 22.8165 | 0
32 |  |  |  | Hours: 9; Rate: 22.8165
33 |  |  |  | Hours: 9; Rate: 22.8165
34 |  |  |  | Hours: 9; Rate: 22.8165
35 |  |  |  | Hours: 9; Rate: 22.8165; Total: 0
36 |  |  | Total Cost of Substation Equipment | Total: 91.8; Frt: 1.25; Qty: 338.4; Total: 7.7211
[12 empty] | Total Hours |  | 338.4
[12 empty] | Prod Factor | 2 | 676.8 | 22.8165 | 15.4422
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 10
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 3.5
17.5
[13 empty] | Contr G&A 8% |  | 1.4
[13 empty] | Contr Mark up 15% |  | 2.625
21.525
[12 empty] | 45 | Hour Work Week = |  | 22.8165
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N61: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q53: Insert Rate Here:

## 520 & 530 Instrumentation
PLANT INSTRUMENTATION
(1,000's)
520 &530
Project Name: |  | TACOA LM 6000 Power Plant | [8 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [8 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [8 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Hours: 9
2 | Instrumentation for GTG |  |  | 2 | 25000 | 50000 | 9 | 2 | 10 | 360 | 22.8165 | 8213.94
3 |  |  |  | Hours: 9; Rate: 22.8165; Total: 0
4 | Instrumentation for SCR |  |  | 0 | 0 | 0 | 9 | 4 | 15 | 0 | 22.8165 | 0
5 |  |  |  | Hours: 9; Rate: 22.8165
6 | Instrumentation for HRSG |  |  | 0 | 0 | 0 | 9 | 4 | 15 | 0 | 22.8165 | 0
7 |  |  |  | Hours: 9; Rate: 22.8165
8 | Instrumentation for Injection Water Treatment |  |  | 1 | 25000 | 25000 | 9 | 2 | 10 | 180 | 22.8165 | 4106.97
9 |  |  |  | Hours: 9; Rate: 22.8165
10 | Instrumentation for Liquid Fuel |  |  | 0 | 25000 | 0 | 9 | 2 | 7 | 0 | 22.8165 | 0
11 |  |  |  | Hours: 9; Rate: 22.8165
12 | Instrumentation for gas compressors |  |  | 3 | 10000 | 30000 | 9 | 4 | 5 | 540 | 22.8165 | 12320.91
13 |  |  |  | Hours: 9; Rate: 22.8165
14 | Labor to Install CEMS |  |  | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 22.8165 | 0
15 |  |  |  | Hours: 9; Rate: 22.8165
16 |  |  |  | Hours: 9; Rate: 22.8165
17 |  |  |  | Hours: 9; Rate: 22.8165
18 |  |  |  | Hours: 9; Rate: 22.8165
19 |  |  |  | Hours: 9; Rate: 22.8165
20 |  |  |  | Hours: 9; Rate: 22.8165
21 |  |  |  | Hours: 9; Rate: 22.8165
22 |  |  |  | Hours: 9; Rate: 22.8165
23 |  |  | Total Cost of Plant Instrumentation | Total: 105; Qty: 1080; Total: 24.6418
[8 empty] | Total Hours |  | 1080
[8 empty] | Prod Factor | 2 | 2160 | 22.8165 | 49.2836
Price per hour based with all labor burdens as follows:
[9 empty] | Local Hrly Cost |  | 10
[9 empty] | Fringes |  | 2.5
[9 empty] | Small Tools |  | 1.5
[9 empty] | Labor Burden 35% |  | 3.5
17.5
[9 empty] | Contr G&A 8% |  | 1.4
[9 empty] | Contr Mark up 15% |  | 2.625
21.525
[8 empty] | 45 | Hour Work Week = |  | 22.8165
Work Week Hours Multiplier
[8 empty] | 45 | 50 | 60
[8 empty] | 1.06 | 1.1 | 1.17
Note on L50: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on O42: Inset Rate Here:

## 610, 620, 630 & 640 DCS
DCS
|  |  |  | (1,000's) |  |  |  | 610, 620, 630 & 640
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [6 empty] | Cost | Cost
1
2 | DCS Hardware / Software |  |  |  |  | 1 | 490000 | 490000
3
4 | Lot of Misc interconnecting cables etc. |  |  |  |  | 1 | 20000 | 20000
5
6 | Documentation |  |  |  |  | 1 | 50000 | 50000
7
8 |  |  |  |  | Total DCS |  |  | 560
9
10 | PBX Communications System |  |  |  |  | 1 | 15000 | 15
11
12 | Loud Speaker System |  |  |  |  | 1 | 10000 | 10
13
14 | TV / Security System |  |  |  |  | 1 | 15000 | 15
15
16
17
[7 empty] | taxable | 510040

## 700 Erection
PLANT ERECTION
(1,000's)
700
Project Name: |  | TACOA LM 6000 Power Plant | [6 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [6 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  | No | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  |  | 9
2 | GTG Erection |  |  | 2 | 9 | 12 | 30 | 6480 | 22.8165 | 147850.92
3 |  |  |  |  | 9 |  |  |  | 22.8165
4 | HRSG Erection |  |  | 0 | 9 | 10 | 60 | 0 | 22.8165 | 0
5 |  |  |  |  | 9 |  |  |  | 22.8165
6 | SCR Erection |  |  | 0 | 9 | 10 | 60 | 0 | 22.8165 | 0
7 |  |  |  |  | 9 |  |  |  | 22.8165
8 | Water Treatment and FW Systems |  |  | 1 | 9 | 5 | 10 | 450 | 22.8165 | 10267.425
9 |  |  |  |  | 9 |  |  |  | 22.8165
10 | Liquid Fuel System |  |  | 0 | 9 | 4 | 5 | 0 | 22.8165 | 0
11 |  |  |  |  | 9 |  |  |  | 22.8165
12 | BOP Equip Erection |  |  | 1 | 9 | 6 | 10 | 540 | 22.8165 | 12320.91
13 |  |  |  |  | 9 |  |  |  | 22.8165
14 | Gas Compressor Erection |  |  | 3 | 9 | 6 | 4 | 648 | 22.8165 | 14785.092
15 |  |  |  |  | 9 |  |  |  | 22.8165
16 | Chiller Package |  |  | 0 | 9 | 6 | 20 | 0 | 22.8165 | 0
17 |  |  |  |  | 9 |  |  |  | 22.8165
18 | Fire Water Pump Skid |  |  | 0 | 9 | 4 | 3 | 0 | 22.8165 | 0
19 |  |  |  |  | 9 |  |  |  | 22.8165
20 | STG Erection |  |  | 0 | 9 | 12 | 36 | 0 | 22.8165 | 0
21 |  |  |  |  | 9 |  |  |  | 22.8165
22 | STG Cooling Tower |  |  | 0 | 9 | 8 | 8 | 0 | 22.8165 | 0
23 |  |  |  |  | 9 |  |  |  | 22.8165
24 |  |  |  |  | 9 |  |  |  | 22.8165
25 |  |  | Total Cost of Plant Erection |  |  |  |  | 8118 |  | 185.2243
[6 empty] | Total Hours |  | 8118
[6 empty] | Prod Factor | 2 | 16236 | 22.8165 | 370.4487
Price per hour based with all labor burdens as follows:
[7 empty] | Local Hrly Cost |  | 10
[7 empty] | Fringes |  | 2.5
[7 empty] | Small Tools |  | 1.5
[7 empty] | Labor Burden 35% |  | 3.5
17.5
[7 empty] | Contr G&A 8% |  | 1.4
[7 empty] | Contr Mark up 15% |  | 2.625
21.525
[6 empty] | 45 | Hour Work Week = |  | 22.8165
Work Week Hours Multiplier
[6 empty] | 45 | 50 | 60
[6 empty] | 1.06 | 1.1 | 1.17
Note on J52: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on M44: Insert Rate Here:

## 800 Equip rent
EQUIPMENT RENTAL
[5 empty] | (1,000's) |  |  |  |  | 800
Project Name: |  | TACOA LM 6000 Power Plant | [6 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [6 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
No. | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
2 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 2 | 10 | 20 | 4000 | 80000
3 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
4 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 30 | 60 | 2000 | 120000
5 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 20 | 0 | 1500 | 0
6 | 2 ea Sky Tracs |  |  |  |  | 2 | 30 | 60 | 70 | 4200
7 | 2 ea Fork Lifts |  |  |  |  | 2 | 30 | 60 | 70 | 4200
8 | 1 ea Man Lift |  |  |  |  | 2 | 30 | 60 | 80 | 4800
9 | 2 ea Welders |  |  |  |  | 5 | 45 | 225 | 60 | 13500
10
11 | HRSG Erection
12 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
13 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
14 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
15 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
16 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
17 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
18 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
19
20 | SCR/CO
21 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
22 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
23 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
24 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
25 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
26 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
27 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
28
29 | STG
30 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
31 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
32 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
33 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
34 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
35 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
36
37 | STG Cooling Tower
38 | 150 Ton Crane |  |  |  |  | 0 | 0 | 0 | 3000 | 0
39 | 40 Ton Crane |  |  |  |  | 0 | 0 | 0 | 1500 | 0
40 | 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
41
42 | Fuel Gas Compressor Rental per Compr Skid
43 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
44 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 3 | 10 | 30 | 1500 | 45000
45
46 | BOP Equip Rental per ea GTG
47 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 5 | 0 | 4000 | 0
48 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
49 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
50 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 150 | 150 | 1500 | 225000
51 | 2 ea Fork Lifts |  |  |  |  | 1 | 150 | 150 | 70 | 10500
52 | 2 ea Sky Tracs |  |  |  |  | 1 | 150 | 150 | 70 | 10500
53 | 2 ea Pick ups |  |  |  |  | 2 | 150 | 300 | 30 | 9000
54 | 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 150 | 150 | 70 | 10500
55
56 | Substation Equip Rental
57 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 2 | 0 | 4000 | 0
58 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
59 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 20 | 0 | 1500 | 0
60 | 2 ea Man Lifts |  |  |  |  | 0 | 35 | 0 | 80 | 0
61 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
62 | 5 ea Welders |  |  |  |  | 0 | 35 | 0 | 80 | 0
63
64
65
66
67
68 |  |  | Total Cost of Plant Equip Rental |  |  |  |  | 1415 |  | 537.2

## 900 Paint
PLANT PAINTING
[5 empty] | (1,000's) |  |  | 900
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Paint for GTG |  |  |  |  | 2 | 50000 | 100000
3
4 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
5
6 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 135000 | 0
7
8 | Paint for Pipe Rack etc. |  |  |  |  | 1 | 25000 | 25000
9
10 | Paint for BOP Equipment |  |  |  |  | 1 | 45000 | 45000
11
12 | Paint for Gas Compressor |  |  |  |  | 3 | 15000 | 45000
13
14 | Paint for Water Treatment |  |  |  |  | 1 | 20000 | 20000
15
16 | Paint for Waste Water Treatment |  |  |  |  | 0 | 15000 | 0
17
18 | Paint for Tanks |  |  |  |  | 0 | 50000 | 0
19
20
21
22
23
24
25
26
27
28
29
30 |  |  | Total Cost of Plant Painting |  |  |  |  | 235

## 1000 Transportation
PLANT TRANSPORTATION
[5 empty] | (1,000's) |  |  | 1000
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 178.3 | 178.3
3
4 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 35.75 | 35.75
5
6 | Transportation Substation Equip |  |  |  |  | 1 | 1.25 | 1.25
7
8 | Transportation of GTG
9
10 | Transportation of SCR
11
12 | Transportation of HRSG
13
14 | Transportation of STG
15
16 | Pipe, Valves & Fittings |  |  |  |  | 1 | 28.5 | 28.5
17
18 | Conduit, Cable & Wire |  |  |  |  | 1 | 50 | 50
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Plant Transportation |  |  |  |  | 293.8

## 1100 Site Costs
SITE COSTS
[5 empty] | (1,000's) |  |  |  |  | 1100
Project Name: |  | TACOA LM 6000 Power Plant | [6 empty] | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas | [6 empty] | Quote No: | T 9003 B - 1
Location: |  | Venzuela | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
No. | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
2 | Office Trailers |  |  |  |  | 3 | 8 | 900 | 21600
3 | Porta Potties |  |  |  |  | 4 | 8 | 150 | 4800
4 | Water and Ice |  |  |  |  | 4 | 8 | 500 | 16000
5 | Fed X |  |  |  |  | 1 | 8 | 300 | 2400
6 | Telephone |  |  |  |  | 1 | 8 | 2000 | 16000
7 | Office Supplies |  |  |  |  | 1 | 8 | 1000 | 8000
8 | [6 empty] | 8
9 | Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 8 | 2500 | 20000
10 | Misc Items |  |  |  |  | 1 | 8 | 3000 | 24000
11 |  |  | Total Monthly Cost | [5 empty] | 112800
12
13
14
15
16
17
18 | Monthly Site Costs | [5 empty] | 1 | 112800 |  | 112800
19 | One Time Costs
20 | 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 150000
21 | Cad Station | [8 empty] | 5000
22 | Computers | [8 empty] | 10000
23 | Telephone System and Satalite Dish | [8 empty] | 10000
24 | Plotter | [8 empty] | 0
25 | Fax Machine and Printers | [8 empty] | 3000
26 | Misc equip | [8 empty] | 45000
27 | Signs | [8 empty] | 0
28
29
30
31
32 | Total Project Cost = Cost per Month Times Number of Mos
33 | Plus the Project One Time Costs.
34
35 |  |  | Total Cost of Project Site Costs | [6 empty] | 335.8

## 1200 Engineering
ENGINEERING
[5 empty] | (1,000's) |  |  | 1200
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total | Q=Quote
No. | [5 empty] | Units | Cost | Cost | E=Est
1
2 | Conceptual Engineering PEPC |  |  |  |  | 1 | 25000 | 25000 | E
3
4 | Detailed Engineering per GTG |  |  |  |  | 2 | 250000 | 500000
5
6 | Detailed Engineering per HRSG |  |  |  |  | 0 | 0 | 0
7
8 | Detailed Engineering Liquid Fuel Treatment |  |  |  |  | 1 | 25000 | 25000
9
10 | Detailed Engineering per Gas Compressor |  |  |  |  | 1 | 45000 | 45000
11
12 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 40000 | 40000
13
14 | Detailed Engineering per Structural Steel/ civil |  |  |  |  | 1 | 100000 | 100000
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33 |  |  | Total Cost of Engineering |  |  |  |  | 735

## 1210 Local Engineering
LOCAL ENGINEERING
[5 empty] | (1,000's) |  |  | 1210
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Soils & Environmental Eng |  |  |  |  | 1 | 15000 | 15000
3
4 | Civil Engineer |  |  |  |  | 1 | 20000 | 20000
5
6 | Mechanical Engineer |  |  |  |  | 1 | 25000 | 25000
7
8 | Electrical Engineer |  |  |  |  | 1 | 25000 | 25000
9
10 | Other |  |  |  |  | 0 | 0 | 0
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Local Engineering |  |  |  |  | 85

## 1310 & 1320 PM-CM-Insp
PROJECT MANAGEMENT LABOR
|  |  |  | (1,000's) |  |  |  | 1310 & 1320
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Mos | Per Mo | Cost
Home Office
1 | Project Mgr Months on Project |  |  |  |  | 9 | 16000 | 144000
2 | Admin Mgr Months on Project |  |  |  |  | 9 | 10000 | 90000
3 | Scheduler |  |  |  |  | 3 | 8000 | 24000
4 | Purchasing Agent |  |  |  |  | 2 | 8000 | 16000
5 | Expediter |  |  |  |  | 2 | 5000 | 10000
6 | Home Office Logistic Coordinator |  |  |  |  | 0 | 9000 | 0
7
8
9 | [6 empty] | 284000
10
11
12
13
14
15
16 | Site Construction
17 | Secretary |  |  |  |  | 7 | 5000 | 35000
18 | Construction Mngr |  |  |  |  | 7 | 15000 | 105000
19 | Contract Cost Admin |  |  |  |  | 0 | 10000 | 0
20 | Scheduler |  |  |  |  | 2 | 8000 | 16000
21 | Mechanical Supervisor |  |  |  |  | 7 | 14000 | 98000
22 | Electrical Supervisor |  |  |  |  | 7 | 14000 | 98000
23 | Civil Supervisor |  |  |  |  | 5 | 14000 | 70000
24 | Clerks |  |  |  |  | 12 | 5000 | 60000
25 | Warehousemen |  |  |  |  | 12 | 5000 | 60000
26 | Draftsman |  |  |  |  | 1 | 9000 | 9000
27 | Security |  |  |  |  | 8 | 15000 | 120000
28 | Safety |  |  |  |  | 8 | 8000 | 64000
29 | QA/QC Mngr |  |  |  |  | 8 | 13000 | 104000
h | US Welders and Electrician 4 for 4 mos |  |  |  |  | 16 | 15000 | 240000
1
2 | [6 empty] | 1079000
3
4 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 6 | 14000 | 84000
5
6
7
8 | Training |  |  |  |  | 0 | 0 | 0
9
10 |  |  |  |  | Total Project & Construction Management |  |  | 1447
11
12
13
14
15 | Inspectors
16 | Civil - Structual __ ea ___ mos |  |  |  |  | 5 | 11500 | 57500
17 | Mechanical __ ea ___ mos |  |  |  |  | 7 | 11500 | 80500
18 | Electrical __ ea ___ mos |  |  |  |  | 7 | 11500 | 80500
19 | Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 6 | 11500 | 69000
20
21 |  |  |  |  | Total Inspectors |  |  | 287500
22

## 1400 & 1410 Travel & Perdiem
PROJECT MGT TVL AND PER DIEM
|  |  |  | (1,000's) |  |  |  | 1400 & 1410
Project Name: |  | TACOA LM 6000 Power Plant |  |  |  |  | Date: | 2009-04-10
Customer: |  | Electricidad de Caracas |  |  |  |  | Quote No: | T 9003 B - 1
Location: |  | Venzuela |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-04-10
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Units | Per Unit | Cost
1
2 | Project & Construciton Management
3 | R T Air Fares |  |  |  |  | 40 | 4000 | 160000
4 | Months of Per Diem at Site (Mgt) |  | Assumes Apartment Rental, meals, etc. |  |  | 64 | 2500 | 160000
5 | Number of Months of Pick Up Trucks |  |  |  |  | 24 | 1200 | 28800
6 | Misc expenditures |  |  |  |  | 1 | 150000 | 150000
7 | Days Per Diem - Lodging & Meals (Techs) |  |  |  |  | 150 | 200 | 30000
8
9
10
11
12
13 | Engineering
14 | Round Trip Air Fare for Eng Visits to site |  |  |  |  | 6 | 4000 | 24000
15 | Days of Per Diem Cost for Eng Days at Site |  |  |  |  | 120 | 200 | 24000
16 | Auto Rental for Eng Days at Site |  |  |  |  | 120 | 150 | 18000
17 | Misc Travel Expentitures |  |  |  |  | 1 | 40000 | 40000
18
19
20 |  |  |  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  | 634.8
21
22
23
24 | Engineering Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
25
26 | Project Mgt Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
27
28 |  |  |  |  | Total Meal Expense |  |  | 0
29
30
31
32
33
34
35
36