## Recap
ProEnergy EPC
Job Description: |  | "2 GE Fr VII EA's for Corprolec w/o Civil"
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
[16 empty] | Manhours | Manhours
I. Balance of Plant | [15 empty] | US | 1.25 | Local Contr
| 1.0 Civil - Structual | [8 empty] | Dismantle | Shipping | BOP Equipment | Engineering | Construciton | Start Up
|  | 1.1 Site Preparation | [15 empty] | 89
|  | 1.2 Excavation - Fill | [13 empty] | 148.1481 | 185.1852 | 144
|  | 1.3 Concrete Foundations | [13 empty] | 676.6037 | 845.7546 | 2030
|  | 1.4 Concrete Pilings | [14 empty] | 0
|  | 1.5 Paving Asphalt - Concrete | [14 empty] | 0 | 670
|  | 1.6 Gravel - Sand | [14 empty] | 0 | 181
|  | 1.7 Structual Steel |  |  |  | 186 | [10 empty] | 0
|  | 1.8 Fencing | [13 empty] | 0 | 0 | 88
|  | 1.9 Architectual Treatment |  |  |  | 0 | [10 empty] | 0
|  | 1.9 Evaporation Pond |  |  |  | 0 | [10 empty] | 0
[6 empty] | 186 |  | 186 | 234.36 |  |  |  |  | 234.36 |  |  | 0
0
| 2.0 Buildings | [15 empty] | 0
|  | 2.1 Various Bldgs |  |  |  | 664.5 | [10 empty] | 0
[6 empty] | 0 | [10 empty] | 0
[6 empty] | 664.5 |  | 664.5 | 837.27 |  |  |  |  | 837.27 |  |  | 0
0
| 3.0 Mechanical | [15 empty] | 0
|  | 3.1 Major Mechanical Equipment |  |  |  | 2872 |  |  | 3618.72 |  |  | 3618.72 |  |  |  |  | 0
|  | 3.2 Pipe, Valves and Fittings Material |  |  |  | 1500 |  |  | 1890 | [7 empty] | 0
|  | 3.3 Mechanical Subcontractor |  |  |  | 1428.111
|  | 3.4 Pipe, Valves and FTG Labor |  |  |  | 612.36 |  |  | 771.5736 |  |  |  |  | 771.5736 |  | 32650 | 40812.5
[6 empty] | 6412.471 |  | 6412.471 | [8 empty] | 0
0
| 4.0 Electrical | [15 empty] | 0
|  | 4.1 Major Electrical Equipment |  |  |  | 547.1 |  |  | 689.346 |  |  | 689.346 |  |  |  |  | 0
|  | 4.2 Substation Equipment |  |  |  | 424 |  |  | 534.24 |  |  | 534.24 |  |  |  |  | 0
|  | 4.3 Cable, Conduit, and Tray |  |  |  | 1900
|  | 4.4 Plant Electrical Subcontractor |  |  |  | 1128.9148
|  | 4.5 Substation Subcontractor |  |  |  | 58.806 |  |  | 74.0956 |  |  |  |  | 74.0956 |  | 28156 | 35195
|  | 4.6 Cable, Conduit, and Tray Labor |  |  |  | 681.615 |  |  | 858.8349 | [6 empty] | 1100 | 1375
[6 empty] | 4740.4358 |  | 4740.4358 | [8 empty] | 0
0
| 5.0 Instrumentation | [15 empty] | 0
|  | 5.1 Cems |  |  |  | 0 | [10 empty] | 0
|  | 5.2 Plant Instrumentation |  |  |  | 230 | [10 empty] | 0
|  | 5.3 Instrumentation Subcontractor |  |  |  | 95.5152 | [9 empty] | 1340 | 1675
0
[6 empty] | 325.5152 |  | 325.5152 | 410.1492 |  |  |  |  | 410.1492 |  |  | 0
0
| 6.0 DCS System | [15 empty] | 0
|  | 6.1 Hardware |  |  |  | 320 | [10 empty] | 0
|  | 6.2 Software |  |  |  | 148.5 | [10 empty] | 0
[6 empty] | 468.5 |  | 468.5 | 590.31 |  |  |  |  | 590.31 |  |  | 0
0
0
| 7.0 Plant Erection | [15 empty] | 0
|  | 7.1 Plant Erection |  |  |  | 1657.26 | [9 empty] | 62000 | 77500
0
[6 empty] | 1657.26 |  | 1657.26 | 2088.1476 |  |  |  |  | 2088.1476 |  |  | 0
0
| 8.0 Equipment Rental | [15 empty] | 0
|  | 8.2 Plant Equipment Rental |  |  |  | 1445 | [10 empty] | 0
0
[6 empty] | 1445 |  | 1445 | 1820.7 |  |  |  |  | 1820.7 |  |  | 0
0
| 9.0 Painting |  |  |  |  | 265 |  | 265 | 333.9 |  |  |  |  | 333.9
0
| 10.0 Transportation | [15 empty] | 0
|  | 10.1 BOP US Frt |  |  |  | 194.8 | [10 empty] | 0
|  | 10.2 Ocean Frt BOP |  |  |  | 50 | [10 empty] | 0
|  | 10.3 Inland Frt BOP |  |  |  | 50 | [10 empty] | 0
[6 empty] | 294.8 |  | 294.8 | 371.448 |  | 371.448 | [5 empty] | 0
0
0
| 11.0 Site Costs |  |  |  |  | 559.2 |  | 559.2 | 704.592 |  |  |  |  | 704.592 |  |  | 0
0
| 12.0 Engineering | [15 empty] | 0
|  | 12.1 EPC Eng Labor |  |  |  | 575 | [10 empty] | 0
|  | 12.2 Local Eng |  |  |  | 165 | [10 empty] | 0
|  | 12.3 Eng Travel & Per Diem |  |  |  | 118.9 | [10 empty] | 0
[6 empty] | 858.9 |  | 858.9 | 1082.214 |  |  |  | 1082.214 |  |  |  | 0
0
| 13.0 Project Management | [15 empty] | 0
|  | 13.1 Project - Inspectors - Commissioning Lab |  |  |  | 3229 | [9 empty] | 39520 | 39520
|  | 13.2 Travel & Per Diem |  |  |  | 1177 | [10 empty] | 0
[6 empty] | 0 | [10 empty] | 0
0
[6 empty] | 4406 |  | 4406 | 5551.56 | 2220.624 |  |  |  | 3330.936 |  |  | 0
0
| 14.0 Technical Reps | [15 empty] | 0
|  | 14.1 GTG Tech Rep |  | 260 | 1200 | 312000 | [10 empty] | 0
|  | 14.2 Fire Water |  | 0 | 2000 | 0 | [10 empty] | 0
|  | 14.3 Gas Compressor |  | 0 | 2000 | 0 | [10 empty] | 0
|  | 14.4 Evap Cooler Pkg |  | 0 | 2000 | 0 | [10 empty] | 0
|  | 14.5 Water Treatment |  | 15 | 2000 | 30000 | [10 empty] | 0
|  | 14.6 Commissioning / Start |  | 120 | 1200 | 144000 | [10 empty] | 0
|  | 14.7 Controls Rep |  | 100 | 1200 | 120000 | [10 empty] | 0
0
[6 empty] | 606 |  | 606 | 763.56 | [5 empty] | 763.56 |  | 0
0
| 15.0 Project Tests | [15 empty] | 0
|  | 15.1 Soils Compaction |  |  |  | 0 | [10 empty] | 0
|  | 15.2 Concrete Testing | [14 empty] | 0 | 80
|  | 15.3 X Ray |  |  |  | 80 | [10 empty] | 0
|  | 15.4 Plant Performance and Reliability |  |  |  | 200 | [10 empty] | 0
|  | 15.5 Noise Emission Tests | [14 empty] | 0
|  | 15.6 Protective Relays |  |  |  | 30 | [10 empty] | 0
[6 empty] | 310 |  | 310 | 390.6 |  |  |  |  | 195.3 | 195.3 |  | 0
0
| 16.0 Legal |  |  |  |  | 75 |  | 75 | 94.5 | 47.25 |  |  |  | 47.25 |  |  | 0
0
| 17.0 Insurance | [15 empty] | 0
|  | 17.1 Project Insurance |  |  |  | 350 |  | 350 | 441 | 220.5 |  |  |  | 220.5
| 18.0 Dismantling |  |  | 0 | 1150 | 0 |  | 0 | 0 | 0 | [5 empty] | 165590.7519 | 197108.4398
| 19.0 Project Contingency/Risk |  |  |  |  | 23624.582 |  | 1181.2291 | 0.032029 | [8 empty] | 100
| 19.1 GT Performance Contingency | [6 empty] | 1000
| 20.0 Sales Tax |  |  |  |  | 0 |  |  |  | 2488.374 | 371.448 | 4842.306 | 1082.214 | 11659.0839 | 958.86
|  | BOP Cost | [5 empty] | 25805.8111 | [9 empty] | 3382
|  | Gross Profit |  |  |  |  | 38.75% | 10000 | 0.27115
|  | GTG Warranty and 5% Markup | [5 empty] | 0
| 21.0 Commissions |  | BOP 3% | Plugged |  | 1074.1743 |  | 1074.1743 | 1319.4597
0
|  |  |  | BOP Sales Price |  |  |  | 36879.9855 | 24151.424 | [8 empty] | 3382
II. Liquid Fuel Breakout
|  | Civil Concrete |  |  |  | 0 | [11 empty] | 316
|  | Centrifuges |  |  |  | 700
|  | Tanks |  |  |  | 1400
|  | Pumps, Filters, Meter, etc |  |  |  | 279
|  | Pipe Valves and Fittings |  |  |  | 200
|  | Mech Labor |  |  |  | 57
|  | Elect Equip and cable, cond, etc |  |  |  | 200
|  | Elect Labor |  |  |  | 40
|  | Erection |  |  |  | 27
|  | Equip Rental |  |  |  | 30
|  | Transportation |  |  |  | 150
|  | Engineering |  |  |  | 15
[6 empty] | 3098 | [11 empty] | 316
|  |  | Mark Up |  | 0.25 | 774.5 | [11 empty] | 79
|  |  | Breakout for Liquid Fuel |  |  | 3872.5 |  | 3872.5 | [9 empty] | 395
Based on 1,250,000 gal storage
NOTES
Transportation seems low -
raised various labor figures
reduced various mod factors from 2.0 to 1.5
Should buy cranes - will check on cost / avail
price per yard on foundations at 600? Verify estimate
assumptions on compaction test results…

## 1.1 Site Prep
|  |  | SITE PREP | [6 empty] | 1.1
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [5 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [5 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Site |  |  | 500 | 400 | 0.5 | 200000 | 7407.4074 | 12 | 88888.8889
2
3 | [9 empty] | 0
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
88.8889

## 1.2 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 1.2
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [6 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [6 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
| Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Control/Office/Maint |  |  |  | 120 | 60 | 1 | 7200 | 266.6667 | 12 | 3200
| Water Treatment Area |  |  |  | 60 | 50 | 1 | 3000 | 111.1111 | 12 | 1333.3333
| Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Pwr Blk Utility GTG's |  |  |  | 350 | 150 | 2 | 105000 | 3888.8889 | 12 | 46666.6667
| Substation GSU's |  |  |  | 80 | 30 | 3 | 7200 | 266.6667 | 12 | 3200
| Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Liquid Fuel Unloading Shed |  |  |  | 60 | 30 | 1 | 1800 | 66.6667 | 12 | 800
12
2 | Main Plant Area |  |  |  | 500 | 400 | 1 | 200000 | 7407.4074 | 12 | 88888.8889 | 148.1481
3 | Fill |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0
4 | Substation Area |  |  |  | 0 | 0 | 1 | 0 | 0 | 12 | 0 | 0
5
6 | [11 empty] | 148.1481
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Excavation and Fill | [7 empty] | 144.0889
Evaporation Pond - Option 1 - RO w/EDI Water Treatment w/pond
[5 empty] | 675 | 200 | 5 | 135000 | 25000 | 2.5 | 62500 | 0 | 0 | 62500
Evaporation Pond - Option 2 - Deionizing trailers w/pond
[5 empty] | 475 | 200 | 5 | 95000 | 17592.5926 | 2.5 | 43981.4815 | 0 | 0 | 43981.4815

## 1.3 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 1.3
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [7 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | POWER ISLAND
| GT Generators |  |  | 2 | 60 | 25 | 6 | 18000 | 666.6667 | 600 | 400000
| Exhaust Stack |  |  | 2 | 30 | 30 | 4 | 7200 | 266.6667 | 600 | 160000
| Generator Base |  |  | 2 | 30 | 12 | 6 | 4320 | 160 | 600 | 96000
| Leg A |  |  | 2 | 27 | 7 | 3 | 1134 | 42 | 600 | 25200
| Leg B |  |  | 2 | 27 | 7 | 3 | 1134 | 42 | 600 | 25200
| Base |  |  | 2 | 25 | 14 | 4 | 2800 | 103.7037 | 600 | 62222.2222
| Emergency Gen Base |  |  | 1 | 16 | 8 | 2 | 256 | 9.4815 | 600 | 5688.8889
| Black Start Gen Base |  |  | 0 | 25 | 12 | 3 | 0 | 0 | 600 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
600
600
2 | BALANCE OF PLANT |  |  | Price: 600
| Gas Valve Module |  |  | 1 | 12 | 9 | 1 | 108 | 4 | 600 | 2400
| PEECC Vault |  |  | 2 | 40 | 16 | 2 | 2560 | 94.8148 | 600 | 56888.8889
| Fin Fan L O Coolers |  |  | 2 | 40 | 20 | 1.5 | 2400 | 88.8889 | 600 | 53333.3333
| Mech Elec Bldg Vault |  |  | 1 | 40 | 23 | 1.5 | 1380 | 51.1111 | 600 | 30666.6667
| Water Wash Skid |  |  | 1 | 19 | 9 | 2 | 342 | 12.6667 | 600 | 7600
| Exhaust Gas Blowers |  |  | 1 | 13.5 | 4 | 2 | 108 | 4 | 600 | 2400
| Mist Elimenator |  |  | 1 | 8 | 8 | 1 | 64 | 2.3704 | 600 | 1422.2222
| Air Processing skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| 15KV Switch Gear NEMA 3R |  |  | 2 | 17 | 9 | 1 | 306 | 11.3333 | 600 | 6800
| 15KV Breaker |  |  | 2 | 19 | 12 | 1 | 456 | 16.8889 | 600 | 10133.3333
| Sump Basin |  |  | 2 | 12 | 10 | 2 | 480 | 17.7778 | 600 | 10666.6667
| Waste Oil Storage Tank |  |  | 1 | 12 | 12 | 1 | 144 | 5.3333 | 600 | 3200
| Oily Water Separator |  |  | 1 | 30 | 15 | 2 | 900 | 33.3333 | 600 | 20000
| Fire Water Pump Skid |  |  | 1 | 35 | 15 | 2 | 1050 | 38.8889 | 600 | 23333.3333
| Instrument air Compressor |  |  | 2 | 10 | 8 | 1 | 160 | 5.9259 | 600 | 3555.5556
| Pipe Rack Stanchons |  |  | 28 | 2.5 | 2.5 | 3 | 525 | 19.4444 | 600 | 11666.6667
| 15 LV Cable Stanchons |  |  | 10 | 2.5 | 2.5 | 3 | 187.5 | 6.9444 | 600 | 4166.6667
| Water Treatment Plant |  |  | 1 | 60 | 40 | 1 | 2400 | 88.8889 | 600 | 53333.3333
| Fire Water Tank base |  |  | 1 | 40 | 40 | 1 | 1600 | 59.2593 | 600 | 35555.5556
| Raw Water Tank Base |  |  | 0 | 35 | 35 | 1 | 0 | 0 | 600 | 0
| Area Light Poles |  |  | 8 | 3 | 3 | 4 | 288 | 10.6667 | 600 | 6400
| Demin Water Pump skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| Demin Stg Tanks 250MGal |  |  | 1 | 38 | 38 | 1 | 1444 | 53.4815 | 600 | 32088.8889
| Demin Forwarding Pumps |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| 4160 V Aux Transformers |  |  | 2 | 12 | 12 | 1 | 288 | 10.6667 | 600 | 6400
| 480 V Aux Transformers |  |  | 2 | 10 | 10 | 1 | 200 | 7.4074 | 600 | 4444.4444
| CO2 Tanks |  |  | 4 | 11 | 7 | 1 | 308 | 11.4074 | 600 | 6844.4444
| Cable Trenches / Power Blk |  |  | 2 | 90 | 12 | 1 | 2160 | 80 | 600 | 48000
| Cable Trenches Utilities |  |  | 1 | 250 | 12 | 1 | 3000 | 111.1111 | 600 | 66666.6667
| Diesel Unloading Shed |  |  | 1 | 60 | 25 | 1 | 1500 | 55.5556 | 600 | 33333.3333
| Fuel Forwarding Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 600 | 1777.7778
| Fuel Heater Skid |  |  | 2 | 20 | 15 | 1 | 600 | 22.2222 | 600 | 13333.3333
| Fuel Tank |  |  | 3 | 65 | 65 | 1 | 12675 | 469.4444 | 600 | 281666.6667
3 | BUILDINGS |  |  | Price: 600
| Control Bldg/Office |  |  | 1 | 75 | 60 | 1 | 4500 | 166.6667 | 600 | 100000
| Warehouse/Maintenance |  |  | 1 | 80 | 60 | 1 | 4800 | 177.7778 | 600 | 106666.6667
| Water Treatment Bldg |  |  | 1 | 60 | 40 | 1 | 2400 | 88.8889 | 600 | 53333.3333
| Gas Compressor Bldg |  |  | 0 | 120 | 45 | 1 | 0 | 0 | 600 | 0
| Electrical Bldg |  |  | 1 | 42 | 20 | 1 | 840 | 31.1111 | 600 | 18666.6667
| Pwr Blk Utility Bldg's |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 600 | 0
| Substation Bldg |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 600 | 0
| Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
| Liquid Fuel Unloading |  |  | 0 | 40 | 60 | 1 | 0 | 0 | 600 | 0
| Pump Bldg |  |  | 1 | 40 | 30 | 1 | 1200 | 44.4444 | 600 | 26666.6667
| Control Room |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
600
4 | SUBSTATION |  |  | Price: 600
| GSU Transformer |  |  | 2 | 35 | 35 | 2 | 4900 | 181.4815 | 600 | 108888.8889
| GSU Blast Wall |  |  | 0 | 35 | 20 | 1.5 | 0 | 0 | 600 | 0
| (132)KV SF6 Circuit Breaker |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 600 | 0
| (132)KV Disc Switch w/ Stand |  |  | 0 | 10 | 15 | 1 | 0 | 0 | 600 | 0
| Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 600 | 0
| Transmission Line Poles |  |  | 0 | 5 | 5 | 20 | 0 | 0 | 600 | 0
| Insulator Support Base |  |  | 0 | 2.5 | 2.5 | 3 | 0 | 0 | 600 | 0
| PT Support Base |  |  | 0 | 2.5 | 2.5 | 3 | 0 | 0 | 600 | 0
| Static Pole Base |  |  | 0 | 3 | 3 | 5 | 0 | 0 | 600 | 0
|  |  | Total Cost of Foundations | Cubic: 3383.0185; Total: 2029.8111
[9 empty] | 676.6037 | mhrs @ 5mhr/cy

## 1.4 Pilings
PILINGS
|  |  |  | (1,000's) | [7 empty] | 1.4
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [7 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description | [7 empty] | Cu | Price | Total
Nol |  |  |  |  | Units | Qty | "L" | "D" | "W" | Yd | CuYd | Price
1 | Concrete Pilings
| Pilings GTG x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 119 | 550 | 59259
| Pilings Stack x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 36 | 550 | 17778
| Pilings GSU x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 18 | 550 | 8889
| Pilings Gas Comp x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0
| Pilings HRSG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0
| Pilings STG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
0
0
0
0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
Total Cost of Retaining Walls

## 1.5 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 1.5
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
2 | Gen Removal Areas |  |  | 120 | 30 | 1 | 3600 | 133.3333 | 400 | 53333.3333
3 | Turbine Removal Areas |  |  | 120 | 30 | 1 | 3600 | 133.3333 | 400 | 53333.3333
4 | Entry Ways |  |  | 80 | 15 | 0.5 | 600 | 22.2222 | 400 | 8888.8889
5 | Walk ways |  |  | 220 | 6 | 0.5 | 660 | 24.4444 | 400 | 9777.7778
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 400 | 0
7 | [6 empty] | 0 | 0 |  | 0
8 | [6 empty] | 0 | 0 |  | 0
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 1600 | 20 | 0.7 | 22400 | 829.6296 | 500 | 414814.8148
12 | Parking Lot |  |  | 200 | 50 | 0.7 | 7000 | 259.2593 | 500 | 129629.6296
13 | [6 empty] | 0 | 0 |  | 0
14 | [6 empty] | 0 | 0 |  | 0
15 | [6 empty] | 0 | 0 |  | 0
16 | [6 empty] | 0 | 0 |  | 0
17 | [6 empty] | 0 | 0 |  | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
669.7778

## 1.6 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 1.6
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [7 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 500 | 400 | 0.5 | 100000 | 3703.7037 | 6148.1481 | 25 | 153703.7037
3
4 | Cooling Tower Area |  |  | 0 | 110 | 160 | 0.5 | 0 | 0 | 0 | 25 | 0
5
6 | Substation |  |  | 0 | 600 | 300 | 0.7 | 0 | 0 | 0 | 25 | 0
7
8 | Road ways |  |  | 1 | 1400 | 25 | 0.5 | 17500 | 648.1481 | 1075.9259 | 25 | 26898.1481
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Gravel | Total: 180.6019

## 1.7 Structural
STRUCTUAL STEEL
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [5 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | # of | Qty | Price | Total
Nol | [5 empty] | Lbs / Tons |  |  | Price
1 | Misc Pipe Rack supports etc. | [5 empty] | 15 | 3500 | 52500
0
2 | 15 KV Cable Tray Stanchons | [5 empty] | 15 | 3000 | 45000
0
3 | GTG walkways and stairs | [5 empty] | 3 | 15000 | 45000
0
4 | Structual Steel for equip supports | [5 empty] | 0 | 0 | 0
5 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 1 | 15000 | 15000
6 | Steel Cover for Oily Catch Basin | [5 empty] | 1 | 3500 | 3500
7 | [6 empty] | 0 | 0 | 0
8 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 25000 | 25000
9
|  |  | Total Cost of Stuctual Steel | [5 empty] | 186 | 0

## 1.8 Fence
FENCING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1800 | 10 | 18000
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 2000 | 19 | 38000
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 14 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 4 | 3000 | 12000
10 | Motor Operated Double Gate(s) |  |  |  |  | 1 | 7000 | 7000
11 | Personnel Gate(s) |  |  |  |  | 6 | 500 | 3000
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 1 | 10000 | 10000
15
|  |  | Total Cost of Fencing |  |  |  |  | 88

## 2.1 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 2.1
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [5 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
Nol |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0
2 | Control/Office |  |  |  | 75 | 60 | 4500 | 65 | 292500
3 | Water Treatment |  |  |  | 60 | 40 | 2400 | 45 | 108000
4 | Electric Bldg |  |  |  | 0 | 0 | 0 | 45 | 0
5 | Warehouse/Maintenance |  |  |  | 75 | 60 | 4500 | 45 | 202500
6 | Substation Bldg |  |  |  | 0 | 15 | 0 | 40 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Unloading Shed |  |  |  | 60 | 25 | 1500 | 35 | 52500
9 | Pump Room |  |  |  | 0 | 30 | 0 | 45 | 0
10 | Control Room |  |  |  | 0 | 0 | 0 | 0 | 0
11 | Entry Guard House |  |  |  | 15 | 15 | 225 | 40 | 9000
12 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
|  |  | Total Cost of Other Buildings | [5 empty] | 664.5

## 3.1 & 3.3 Mech Equip & Labor
MECHANICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [9 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [9 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [9 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
GTG
1 | GTG Type GE Frame VII EA's |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 12 | 120 | 28800 | 29.16 | 839808
2 | Lube oils and Chemicals 2600 gal ea @ 6.50 |  |  | 2 | 40000 | 80000 | 3000 | 6000 | 10 | 2 | 1 | 40 | 29.16 | 1166.4
3 | Exhaust Stack |  |  | 0 | 1800000 | 0 | 150000 | 0 | 10 | 6 | 15 | 0 | 29.16 | 0
4 | Exhaust Expansion Joint |  |  | 2 | 15000 | 30000 | 500 | 1000 | 10 | 0 | 15 | 0 | 29.16 | 0
| LO Fin Fans |  |  | 0 | 120000 | 0 | 15000 | 0 | 10 | 4 | 10 | 0 | 29
5 | Anchor Bolts/Fixators |  |  | 2 | 75000 | 150000 | 500 | 1000 | 10 | 0 | 15 | 0 | 29.16 | 0
6
7 | HRSG
8 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
9 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
10 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
11 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
10 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
11 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
12
13 | SCR
14 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
15 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
16
17 | STG
18 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
19 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
20 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
21 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
22 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
23 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
24
25 | Inlet Air Conditioning System
26 | Inlet Chilling Package (Generator) |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
27 | Inlet Fogging System |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
28 | Inlet Overspray System (Includes installation) |  |  | 0 | 427300 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 29.16 | 0
29 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
30 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
31 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
32 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
33
34 | Fuel Gas Systems
35 | Fuel Gas compressor w/ Fin Fans |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
36 | Fuel Gas Regulator Skid |  |  | 0 | 150000 | 0 | 1000 | 0 | 10 | 4 | 3 | 0 | 29.16 | 0
37 | Fuel Gas Turbine Metering Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
37 | Fuel Gas Filter Skid & Mnt (___) KW Htr(Htr in Elect) |  |  | 0 | 380000 | 0 | 5000 | 0 | 10 | 4 | 5 | 0 | 29.16 | 0
38 | ESD Valve, ___" ___# |  |  | 1 | 25000 | 25000 | 500 | 500 | 10 | 2 | 1 | 20 | 29.16 | 583.2
39
40 | Liquid Fuel Systems
41 | Unloading Pump Skid |  |  | 2 | 12000 | 24000 | 500 | 1000 | 10 | 3 | 3 | 180 | 29.16 | 5248.8
42 | Metering Skid |  |  | 1 | 135000 | 135000 | 500 | 500 | 10 | 3 | 3 | 90 | 29.16 | 2624.4
43 | Forwarding Pump Skid |  |  | 1 | 35000 | 35000 | 1000 | 1000 | 10 | 3 | 5 | 150 | 29.16 | 4374
44 | Transfer Pump Skid |  |  | 1 | 25000 | 25000 | 1000 | 1000 | 10 | 3 | 3 | 90 | 29.16 | 2624.4
45 | Fuel Heating |  |  | 0 | 85000 | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 29.16 | 0
46 | Filters |  |  | 4 | 15000 | 60000 | 500 | 2000 | 10 | 2 | 2 | 160 | 29.16 | 4665.6
47 | Centrifuge |  |  | 2 | 200000 | 400000 | 30000 | 60000 | 10 | 3 | 5 | 300 | 29.16 | 8748
48 | Injection Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
49 | Storage Tank (1000M Gal) |  |  | 0 | 1300000 | 0 | 50000 | 0 | 10 | 4 | 8 | 0 | 29.16 | 0
50 | Day Tank (250M Gal) |  |  | 0 | 250000 | 0 | 25000 | 0 | 10 | 3 | 5 | 0 | 29.16 | 0
51 | Water Supply System
52 | Raw Water Storage Tank 500 M gal |  |  | 0 | 450000 | 0 | 20000 | 0 | 10 | 4 | 5 | 0 | 29.16 | 0
53 | Raw Water Supply Pumps |  |  | 2 | 12000 | 24000 | 2000 | 4000 | 10 | 2 | 2 | 80 | 29.16 | 2332.8
54 | Raw Water Forwarding Pumps |  |  | 0 | 8000 | 0 | 1500 | 0 | 10 | 2 | 2 | 0 | 29.16 | 0
55 | Water Treatment System
56 | Multi Media Filter Package |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 1 | 0 | 29.16 | 0
57 | Water Wash Skid |  |  | 1 | 110000 | 110000 | 5000 | 5000 | 10 | 4 | 5 | 200 | 29.16 | 5832
58 | Demin Treatment System |  |  | 1 | 700000 | 700000 | 5000 | 5000 | 10 | 4 | 20 | 800 | 29.16 | 23328
59 | Demin Storage SS Tank gal |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
60 | Demin water fiberglass tank |  |  | 6 | 25000 | 150000 | 2500 | 15000 | 10 | 4 | 3 | 720 | 29.16 | 20995.2
61 | Demin forwarding pumps (50%) |  |  | 2 | 15000 | 30000 | 500 | 1000 | 10 | 2 | 1 | 40 | 29.16 | 1166.4
62 | Demin Filter Skid |  |  | 2 | 30000 | 60000 | 500 | 1000 | 10 | 2 | 1 | 40 | 29.16 | 1166.4
63 | Demin Water Tank, SS 300M gal |  |  | 0 | 320000 | 0 | 15000 | 0 | 10 | 4 | 4 | 0 | 29.16 | 0
64
65 | Waste Water and Oil Storage and Transfer
66 | Oily Water Separator |  |  | 1 | 55000 | 55000 | 0 | 0 | 10 | 2 | 5 | 100 | 29.16 | 2916
67 | Oily Waste Tank 10000 gal |  |  | 1 | 10000 | 10000 | 2500 | 2500 | 10 | 4 | 2 | 80 | 29.16 | 2332.8
68 | Waste Water Tank 10000 gal |  |  | 1 | 10000 | 10000 | 2500 | 2500 | 10 | 4 | 2 | 80 | 29.16 | 2332.8
69 | Waste Oil and Water forwarding pumps w/ skid |  |  | 2 | 7000 | 14000 | 500 | 1000 | 10 | 2 | 1 | 40 | 29.16 | 1166.4
70
71 | Fire Control Systems
72 | Fire Water Pump Skids (Diesel / Electric) |  |  | 1 | 500000 | 500000 | 5000 | 5000 | 10 | 4 | 5 | 200 | 29.16 | 5832
73 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 85000 | 85000 | 10000 | 10000 | 10 | 4 | 4 | 160 | 29.16 | 4665.6
| Foam System |  |  | 1 | 75000 | 75000 | 1000 | 1000 | 10 | 4 | 4 | 160 | 29.16 | 4665.6
74 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0
75 | Storm Water System
76 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
77 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
78 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
79
80 | Other Systems
81 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 85000 | 85000 | 0 | 0 | 10 | 4 | 3 | 120 | 29.16 | 3499.2
82 | Emergency Generator 300KW |  |  | 0 | 200000 | 0 | 1500 | 0 | 10 | 4 | 4 | 0 | 29.16 | 0
83 | Black Start Generator 2 MW |  |  | 0 | 0 | 0 | 5000 | 0 | 10 | 4 | 10 | 0 | 29.16 | 0
84
85 |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29.16 | 0
86 |  |  | Total Cost | Total: 2872; Frt: 127; Hours: 10
[12 empty] | 32650 |  | 952.074
[9 empty] | Total Manhours |  |  | 32650
[9 empty] | Times Prod Factor |  | 1.5 | 48975 | 29.16 | 1428.111
Price per hour based on a 60 hr week with all labor
burdens as follows:
[8 empty] | Local Hrly Cost |  | 15
[8 empty] | Labor Burden 35% |  | 5.25
20.25
[8 empty] | Contr Mark up 20% |  | 4.05
24.3
[8 empty] | 50hrs = x1.2 |  | 29.16
| BOP Pipe, Valves, and Fittings, Labor |  |  | Total: 1500; Frt: Pipe, Vlv, and Ftg Labor; Qty: 14000
[9 empty] | Productivity |  | 1.5 | 21000 | 29.16 | 612.36

## 4.1 & 4.3 El Equip & Labor
ELECTRICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [11 empty] | Date: |  | 2009-01-22
Customer: |  | Corprolec | [11 empty] | Quote No: |  | T-8041 - 2A3
Location: |  | Venn | [11 empty] | Est By: |  | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
Power Island Equipment
1 | Gas Turbine Generator GE Frame VII ea's |  |  |  |  | 2 |  |  |  |  | 10 | 10 | 120 | 24000 | 26.73 | 641520
2 | HRSG |  |  |  |  | 0 | [7 empty] | 0 | 26.73 | 0
3 | SCR |  |  |  |  | 0 | [7 empty] | 0 | 26.73 | 0
4 | STG |  |  |  |  | 0 | [7 empty] | 0 | 26.73 | 0
5 | STG Cooling Tower |  |  |  |  | 0 | [7 empty] | 0 | 26.73 | 0
6 | Chiller Package |  |  |  |  | 0 | [7 empty] | 0 | 26.73 | 0
7 | Water Treatment Package |  |  |  |  | 1 |  |  |  |  | 10 | 4 | 15 | 600 | 26.73 | 16038
8 | [13 empty] | 0 | 26.73 | 0
9 | 15KV
10 | Generator Breaker(s) |  |  |  |  | 0 | 550000 | 0 | 75000 | 0 | 10 | 4 | 5 | 0 | 26.73 | 0
11 | Distribution Breaker(s) |  |  |  |  | 2 | 55000 | 110000 | 2500 | 5000 | 10 | 4 | 4 | 320 | 26.73 | 8553.6
12 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 4 | 0 | 26.73 | 0
13 | Cable Bus Duct |  |  |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 10 | 5 | 6 | 600 | 26.73 | 16038
14 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 26.73 | 0
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 26.73 | 0
16 | 5KV
17 | Distribution Breaker(s) |  |  |  |  | 0 | 60000 | 0 | 5000 | 0 | 10 | 2 | 5 | 0 | 26.73 | 0
18 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 26.73 | 0
10 | MCC's |  |  |  |  | 0 | 20000 | 0 | 0 | 0 | 10 | 1 | 1 | 0 | 101 | 0
11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 26.73 | 0
12 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 26.73 | 0
13 | 600V
14 | Distribution Panel(s) |  |  |  |  | 1 | 85000 | 85000 | 2500 | 2500 | 10 | 2 | 5 | 100 | 26.73 | 2673
15 | GTG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 26.73 | 0
16 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 26.73 | 0
17 | Liquid Fuel MCC |  |  |  |  | 1 | 20000 | 20000 | 2000 | 2000 | 10 | 3 | 2 | 60 | 26.73 | 1603.8
18 | BOP MCC(s) |  |  |  |  | 1 | 25000 | 25000 | 1000 | 1000 | 10 | 2 | 3 | 60 | 26.73 | 1603.8
19 | Water Treatment MCC(s) |  |  |  |  | 1 | 10000 | 10000 | 500 | 500 | 10 | 2 | 3 | 60 | 26.73 | 1603.8
20 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 8 | 0 | 26.73 | 0
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 26.73 | 0
22 | Aux Transformer(s)
23 | 15/5KV ___________ MVA |  |  |  |  | 0 | 75000 | 0 | 5000 | 0 | 10 | 3 | 5 | 0 | 26.73 | 0
24 | 15/600V ___________ MVA |  |  |  |  | 0 | 80000 | 0 | 5000 | 0 | 10 | 3 | 4 | 0 | 26.73 | 0
25 | 600/120/208V ________ KVA |  |  |  |  | 1 | 5000 | 5000 | 500 | 500 | 10 | 2 | 2 | 40 | 26.73 | 1069.2
26 | [5 empty] | 1 | 45000 | 45000 | 0 | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
27 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
28 | Area Lighting
29 | Poles _______ High |  |  |  |  | 6 | 1500 | 9000 | 250 | 1500 | 10 | 4 | 2 | 480 | 26.73 | 12830.4
30 | Floodlights _______ Watts |  |  |  |  | 18 | 450 | 8100 | 100 | 1800 | 10 | 1 | 0.2 | 36 | 26.73 | 962.28
31 | [5 empty] | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
32 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 60 | 0 | 26.73 | 0
33 | Other Systems
34 | UPS |  |  |  |  | 1 | 10000 | 10000 | 0 | 0 | 10 | 3 | 4 | 120 | 26.73 | 3207.6
35 | DC |  |  |  |  | 1 | 20000 | 20000 | 5000 | 5000 | 10 | 3 | 4 | 120 | 26.73 | 3207.6
36 | Cathodic Protection |  |  |  |  | 2 | 15000 | 30000 | 1500 | 3000 | 10 | 3 | 8 | 480 | 26.73 | 12830.4
37 | Lightning Protection |  |  |  |  | 2 | 15000 | 30000 | 1500 | 3000 | 10 | 3 | 8 | 480 | 26.73 | 12830.4
38 | [10 empty] | 10 | 0 | 0 | 0 | 26.73 | 0
39
40 | Temporary Electric |  |  |  |  | 1 | 40000 | 40000 | 2000 | 2000 | 10 | 2 | 30 | 600 | 26.73 | 16038
41 | Electrical Control Module |  |  |  |  | 0 | 65000 | 0 | 3000 | 0 | 10 | 4 | 6 | 0 | 26.73 | 0
42 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
43 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
44 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
45 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 26.73 | 0
|  |  | Total Cost of Electrical Equipment |  |  |  |  | 547.1 |  | 33.8 |  |  |  | 28156 |  | 752.6099
28156
[12 empty] | Productivity | 1.5 | 42234 | 26.73 | 1128.9148
Price per hour based on a 60 hr week with all labor
burdens as follows:
[13 empty] | Local Hrly Cost |  | 15
[13 empty] | Labor Burden 35% |  | 5.25
20.25
[13 empty] | Contr Mark up 20% |  | 4.05
24.3
[13 empty] | 45 hrs = 1.1 |  | 26.73
| Cable, Conduit and Tray - Labor | [6 empty] | 1900 |  |  | Labor |  |  | 17000
[12 empty] | Productivity | 1.5 | 25500 | 26.73 | 681.615
[11 empty] | 4 | 2 | 45 | 0 | 93.0386 | 0
[11 empty] | 16 | 32 | 45 | 0 | 93.0386 | 0
Blended
51.05
17.8675
68.9175
13.7835
82.701
93.0386

## 4.2 & 4.4 Substa Eq & Labor
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [13 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [13 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [13 empty] | Est By:
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [7 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Main Power Transformer 345 KV, 200 MVA (All-in Price) | [5 empty] | 0 | 1500000 | 0 | 200000 | 0 | 10 | 4 | 6 | 0 | 35.64 | 0
2 | SF6 Circuit Breaker(s) _132 KV | [5 empty] | 0 | 125000 | 0 | 2500 | 0 | 10 | 4 | 3 | 0 | 35.64 | 0
3 | Disconnect Switches _132_ KV | [5 empty] | 0 | 15000 | 0 | 1000 | 0 | 10 | 4 | 1 | 0 | 35.64 | 0
4 | Station Post Insulators ____ KV | [5 empty] | 0 | 550 | 0 | 0 | 0 | 10 | 2 | 0.05 | 0 | 35.64 | 0
5 | Insulator Stanchons __21__ High | [5 empty] | 0 | 500 | 0 | 0 | 0 | 10 | 1 | 0.5 | 0 | 35.64 | 0
6 | Insulator Stanchons __13__ High | [5 empty] | 0 | 500 | 0 | 0 | 0 | 10 | 1 | 0.4 | 0 | 35.64 | 0
7 | Dead End Tower(s) | [5 empty] | 2 | 40000 | 80000 | 7000 | 14000 | 10 | 6 | 5 | 600 | 35.64 | 21384
8 | Alum Bus ______ Dia | [5 empty] | 0 | 18 | 0 | 3 | 0 | 10 | 1 | 0.08 | 0 | 35.64 | 0
9 | Alum Bus Conn's | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 35.64 | 0
10 | Alum Bus End Plugs _____ Dia | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.05 | 0 | 35.64 | 0
11 | Alum Bus Support Clamps | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 35.64 | 0
12 | Alum Bus "V" Conn's | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.08 | 0 | 35.64 | 0
13 | Static Wire Poles, ____ High | [5 empty] | 1 | 4000 | 4000 | 0 | 0 | 10 | 4 | 1 | 40 | 35.64 | 1425.6
14 | Area Lighting Poles, ____ High | [5 empty] | 0 | 1500 | 0 | 0 | 0 | 10 | 4 | 1 | 0 | 35.64 | 0
15 | Flood Lights, ______ Watts | [5 empty] | 0 | 450 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
16 | #4/0 Grounding Conductor | [5 empty] | 0 | 20000 | 0 | 0 | 0 | 10 | 2 | 20 | 0 | 35.64 | 0
17 | 3/4"x10'-0" Ground Rods & Clamps | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | .04 | 0 | 35.64 | 0
18 | #90 Cadweld Shots | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | .3 | 0 | 35.64 | 0
19 | Metering CT's & CPT's | [5 empty] | 1 | 50000 | 50000 | 0 | 0 | 10 | 2 | 5 | 100 | 35.64 | 3564 | 0
20 | Station Metering w/ In & Out Capabilities | [5 empty] | 1 | 50000 | 50000 | 0 | 0 | 10 | 2 | 5 | 100 | 35.64 | 3564
21 | Station Protective Relay(s) | [5 empty] | 1 | 50000 | 50000 | 0 | 0 | 10 | 2 | 5 | 100 | 35.64 | 3564
22 | Station RTU | [5 empty] | 0 | 40000 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
23 | 125V DC System | [5 empty] | 0 | 25000 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
24 | Transmission Line Poles | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 2 | 0 | 35.64 | 0
25 | Transmission Line Strain Insulators | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 35.64 | 0 | 0
26 | Cable Bus, Type _____, Size _____ | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 6 | 0 | 35.64 | 0
27 | Main Power Transformer Oil, ______ Gal | [5 empty] | 2 | 50000 | 100000 | 10000 | 20000 | 10 | 2 | 2 | 80 | 35.64 | 2851.2
28 | Main Power Transformer Dress Out & Test | [5 empty] | 2 | 45000 | 90000 | 0 | 0 | 10 | 2 | 2 | 80 | 35.64 | 2851.2
29 | Fiber Optic Cable w/ Messenger Cable | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 35.64 | 0 | 0
30 | Fiber Optic Cable Fittings & Terminations | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 |  |  | 0
31
32 | Price per hour based on a 60 hr week with all labor |  |  |  | Total: 0
33 | burdens as follows: |  |  |  | Total: 0
34 |  |  |  |  | Total: 0
35 |  | Local Hrly Cost |  | 20 | Total: 0
36 |  | Labor Burden 35% |  | 7 | Total: 0
37 |  |  |  | 27 | Total: 0
38 |  | Contr Mark up 20% |  | 5.4 | Total: 0
39 |  |  |  | 32.4
40 |  | 60hrs = x1.1 |  | 35.64
41
42
43
44 |  |  |  |  | Total: 0
|  |  | Total Cost of Substation Equipment |  | Total: 424; Frt: 34; Qty: 1100; Total: 39.204
[13 empty] | Total Hours |  | 1100
[13 empty] | Prod Factor | 1.5 | 1650 | 35.64 | 58.806

## 5.1 CEMS
CEM's
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Cems | Cost | Cost
1 | Rosemont CEM's Unit Most States for 1 ea GTG |  |  |  |  | 0 | 120 | 0
2 | Rosemont CEM's Unit for Califormia for 1 ea GTG |  |  |  |  | 0 | 130 | 0
3 | Installation Support |  |  |  |  | 0 | 18 | 0
|  |  | Total Cost of CEM's |  |  |  |  | 0

## 5.2 Instrument
PLANT INSTRUMENTATION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [9 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [9 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [9 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Instrumentation for GTG |  |  |  | 2 | 65000 | 130000 | 10 | 4 | 10 | 800 | 35.64 | 28512
0
2 | Instrumentation for SCR |  |  |  | 0 | 0 | 0 | 10 | 4 | 15 | 0 | 35.64 | 0
3 | Instrumentation for HRSG |  |  |  | 0 | 0 | 0 | 10 | 4 | 15 | 0 | 62 | 0
4 | Instrumentation for Injection Water Treatment |  |  |  | 1 | 25000 | 25000 | 10 | 4 | 5 | 200 | 35.64 | 7128
5 | Instrumentation for Liquid Fuel System |  |  |  | 1 | 25000 | 25000 | 10 | 2 | 7 | 140 | 35.64 | 4989.6
6 | Instrumentation for gas compressors |  |  |  | 1 | 50000 | 50000 | 10 | 4 | 5 | 200 | 35.64 | 7128
7 | Labor to Install CEMS |  |  |  | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 35.64 | 0
Price per hour based on a 60 hr week with all labor
burdens as follows:
|  | Local Hrly Cost |  | 20
|  | Labor Burden 35% |  | 7
27
|  | Contr Mark up 20% |  | 5.4
32.4
|  | 45hrs = x1.1 |  | 35.64
|  |  | Total Cost of Plant Instrumentation |  | Total: 230; Qty: 1340; Total: 47.7576
[9 empty] | Total Hours |  | 1340
[9 empty] | Prod Factor | 2 | 2680 | 35.64 | 95.5152

## 6.1 DCS Hard
DCS HARDWARE
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [6 empty] | Cost | Cost
1 | DCS Hardware |  |  |  |  | 1 | 200000 | 200000
0
0
2 | Lot of Misc interconnecting cables etc. |  |  |  |  | 2 | 15000 | 30000
3 | PBX Communications System |  |  |  |  | 1 | 20000 | 20000
0
4 | Loud Speaker System |  |  |  |  | 1 | 20000 | 20000
5 | Documentation |  |  |  |  | 1 | 50000 | 50000
|  |  | Total Cost of DCS Software |  |  |  |  | 320

## 6.2 DCS Soft
DCS SOFTWARE
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Hrs | Cost | Cost
1 | Software for DCS |  |  |  |  | 1500 | 75 | 112500
2 | Software for O & M Package |  |  |  |  | 600 | 60 | 36000
3 | Mark VI Download |  |  |  |  | 0 | 6000 | 0
|  |  | Total Cost of DCS Software |  |  |  |  | 148.5

## 7.1 Erection
PLANT ERECTION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: | 2009-01-22 | *.2
Customer: |  | Corprolec | [7 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  | No | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | GTG Erection |  |  |  | 2 | 10 | 24 | 120 | 57600 | 26.73 | 1539648
2 | HRSG Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 26.73 | 0
3 | SCR Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 26.73 | 0
4 | Water Treatment and FW Systems |  |  |  | 1 | 6 | 6 | 30 | 1080 | 26.73 | 28868.4
5 | Liquid Fuel system |  |  |  | 1 | 6 | 6 | 20 | 720 | 26.73 | 19245.6
6 | BOP Equip Erection |  |  |  | 1 | 10 | 10 | 20 | 2000 | 26.73 | 53460
7 | Gas Compressor Erection |  |  |  | 2 | 10 | 6 | 5 | 600 | 26.73 | 16038
8 | Evap Cooling Erection |  |  |  | 0 | 10 | 4 | 4 | 0 | 26.73 | 0
9 | Fire Water Pump Skid |  |  |  | 0 | 10 | 4 | 4 | 0 | 26.73 | 0
10 | STG Erection |  |  |  | 0 | 10 | 12 | 36 | 0 | 26.73 | 0
11 | STG Cooling Tower |  |  |  | 0 | 10 | 8 | 8 | 0 | 26.73 | 0
Price per hour built up as follows:
Blended
|  | Local Hrly Cost |  | 15
|  | Lab Burden 35% |  | 5.25
20.25
|  | Contr Mark up 20% |  | 4.05
24.3
| For 45 hr / wk multiply by 1.1 |  |  | 26.73
|  |  | Total Cost of Plant Erection | [5 empty] | 62000 |  | 1657.26
[7 empty] | Total Hours |  | 62000
[7 empty] | Prod Factor | 1.5 | 93000 | 26.73 | 2485.89

## 8.2 Equip rent
EQUIPMENT RENTAL
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
Nol | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 2 | 30 | 60 | 4000 | 240000
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 120 | 240 | 2000 | 480000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Sky Tracs |  |  |  |  | 2 | 120 | 240 | 70 | 16800
| 2 ea Fork Lifts |  |  |  |  | 2 | 120 | 240 | 70 | 16800
| 1 ea Man Lift |  |  |  |  | 2 | 120 | 240 | 80 | 19200
| 2 ea Welders |  |  |  |  | 2 | 150 | 300 | 60 | 18000
2 | HRSG Erection
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
3 | SCR/CO
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
4 | STG
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
5 | STG Cooling Tower
| 150 Ton Crane |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 40 Ton Crane |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
6 | Fuel Gas Compressor Rental per Compr Skid
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 1 | 10 | 10 | 3000 | 30000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
7 | BOP Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 1 | 40 | 40 | 2000 | 80000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 180 | 180 | 1500 | 270000
| 2 ea Fork Lifts |  |  |  |  | 1 | 120 | 120 | 70 | 8400
| 2 ea Sky Tracs |  |  |  |  | 2 | 160 | 320 | 70 | 22400
| 2 ea Pick ups |  |  |  |  | 2 | 90 | 180 | 30 | 5400
| 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 160 | 160 | 70 | 11200
8 | Substation Equip Rental (GSU Only)
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 2 | 5 | 10 | 4000 | 40000
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 20 | 20 | 1500 | 30000
| 2 ea Man Lifts |  |  |  |  | 1 | 45 | 45 | 80 | 3600
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 1 | 40 | 40 | 80 | 3200
9 | Heavy Lift of GTG and Gen |  |  |  |  | 1 | 150000 |  |  | 150000
|  |  | Total Cost of Plant Equip Rental |  |  |  |  | 2360 |  | 1445

## 9.0 Paint
PLANT PAINTING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Paint for GTG |  |  |  |  | 2 | 80000 | 160000
2 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
3 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 135000 | 0
4 | Paint for Pipe Rack etc. |  |  |  |  | 2 | 25000 | 50000
5 | Paint for BOP Equipment |  |  |  |  | 1 | 40000 | 40000
6 | Paint for Gas Compressor |  |  |  |  | 0 | 15000 | 0
7 | Paint for Water Treatment |  |  |  |  | 1 | 15000 | 15000
8 | Paint for Waste Water Treatment |  |  |  |  | 0 | 15000 | 0
9 | Paint for HRSG |  |  |  |  | 0 | 95000 | 0
|  |  | Total Cost of Plant Painting |  |  |  |  | 265
0

## 10.0 Transportation
PLANT TRANSPORTATION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 127 | 127
2 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 33.8 | 33.8
3 | Transportation Substation Equip |  |  |  |  | 1 | 34 | 34
4 | Transportation of GTG
5 | Transportation of SCR
6 | Transportation of HRSG
7 | Transportation of STG
|  |  | Total Cost of Plant Transportation |  |  |  |  | 194.8

## 11.0 Site Costs
SITE COSTS
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2009-01-22
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A3
Location: |  | Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
Nol | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
| Office Trailers |  |  |  |  | 4 | 12 | 1500 | 72000
| Porta Potties |  |  |  |  | 4 | 12 | 150 | 7200
| Water and Ice |  |  |  |  | 4 | 12 | 500 | 24000
| Fed X |  |  |  |  | 1 | 12 | 1000 | 12000
| Telephone |  |  |  |  | 1 | 12 | 2500 | 30000
| Office Supplies |  |  |  |  | 1 | 12 | 2000 | 24000
| Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 12 | 4000 | 48000
| Misc Items |  |  |  |  | 1 | 12 | 3000 | 36000
|  |  | Total Monthly Cost | [5 empty] | 253200
2 | Total Project Cost = Cost per Month Times Number of Mos
Plus the Project One Time Costs.
| Monthly Site Costs | [5 empty] | 1 | 253200 |  | 253200
| One Time Costs | [5 empty] | 0
| 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 100000
| Cad Station | [8 empty] | 10000
| Computers | [8 empty] | 15000
| Telephone System and Satalite Dish | [8 empty] | 15000
| Plotter | [8 empty] | 10000
| Fax Machine and Printers | [8 empty] | 6000
| Misc equip | [8 empty] | 150000
|  |  | Total Cost of Project Site Costs | [6 empty] | 559.2

## 12.1 Engineering
ENGINEERING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Conceptual Engineering PEPC |  |  |  |  | 1 | 25000 | 25000 | 200
2 | Detailed Engineering per GTG |  |  |  |  | 2 | 125000 | 250000 | 2000
3 | Detailed Engineering per HRSG |  |  |  |  | 0 | 0 | 0
4 | Detailed Engineering Liquid Fuel |  |  |  |  | 1 | 15000 | 15000 | 120
5 | Detailed Engineering of Substation |  |  |  |  | 1 | 40000 | 40000 | 320
6 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 35000 | 35000 | 280
7 | Detailed Engineering for civil/structural |  |  |  |  | 1 | 150000 | 150000 | 1200
8 | Documentation |  |  |  |  | 1 | 60000 | 60000 | 480
[9 empty] | 4600 | manhours@125/hr
|  |  | Total Cost of Engineering |  |  |  |  | 575

## 12.2 Local Engr-Arch
LOCAL ENGINEERING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Soils & Environmental Eng |  |  |  |  | 1 | 15000 | 15000
2 | Civil Engineer |  |  |  |  | 1 | 50000 | 50000
3 | Mechanical Engineer |  |  |  |  | 1 | 50000 | 50000
4 | Electrical Engineer |  |  |  |  | 1 | 50000 | 50000
5 | Other |  |  |  |  | 0 | 0 | 0
|  |  | Total Cost of Local Engineering |  |  |  |  | 165

## 12.3 Engr Trav & per diem
ENGINEERING TVL AND PER DIEM
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | [5 empty] | 0 | 0 | 0
2 | RT to Job Site |  |  |  |  | 10 | 2500 | 25000
3 | [5 empty] | 0 | 250 | 0
4 | Days of Per Diem cost for Eng Days at Job Site |  |  |  |  | 90 | 250 | 22500
5 | [5 empty] | 0 | 100 | 0
6 | Auto Rental for Eng Days at Job Site |  |  |  |  | 120 | 220 | 26400
4 | Misc Travel Expentitures |  |  |  |  | 1 | 45000 | 45000
|  |  | Total Cost of Eng Tvl and Per Diem |  |  |  |  | 118.9

## 13.1 Proj Mgt Labor
PROJECT MANAGEMENT LABOR
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
160
Item |  | Description |  |  |  | No. | Cost | Total | hr/mo
Nol | [5 empty] | Mos | Per Mo | Cost
Project Mng't Home Office
1 | Project Mgr Months on Project |  |  |  |  | 11 | 20000 | 220000 | 1760
2 | Admin Mgr Months on Project |  |  |  |  | 11 | 7000 | 77000 | 1760
3 | Scheduler |  |  |  |  | 11 | 10000 | 110000 | 1760
4 | Purchasing Agent |  |  |  |  | 6 | 7000 | 42000 | 960
5 | Expediter |  |  |  |  | 1 | 5000 | 5000 | 160
6 | Home Office Logistic Coordinator |  |  |  |  | 8 | 12000 | 96000 | 1280
Project at Job Site
7 | Secretary at Job Site |  |  |  |  | 11 | 10000 | 110000 | 1760
8 | Construction Mngr |  |  |  |  | 11 | 18000 | 198000 | 1760
9 | Contract Cost admin |  |  |  |  | 0 | 8000 | 0 | 0
10 | Mechanical Supervisor |  |  |  |  | 11 | 18000 | 198000 | 1760
11 | Electrical Supervisor |  |  |  |  | 11 | 18000 | 198000 | 1760
12 | Civil Supervisor |  |  |  |  | 8 | 15000 | 120000 | 1280
13 | Clerks |  |  |  |  | 12 | 5000 | 60000 | 1920
14 | Warehousemen |  |  |  |  | 12 | 4000 | 48000 | 1920
15 | Draftsman |  |  |  |  | 6 | 9000 | 54000 | 960
16 | Security |  |  |  |  | 11 | 15000 | 165000 | 1760
17 | Safety |  |  |  |  | 11 | 12000 | 132000 | 1760
18 | QA/QC Mngr |  |  |  |  | 11 | 16000 | 176000 | 1760
|  |  |  | Total Proj Mgt Labor |  |  |  | 2009000 | 0
| US Electricians and Welders 6ea plus 6 ea 6 mos |  |  |  |  | 36 | 15000 | 540000 | 5760
19 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 8 | 20000 | 160000 | 1280
[8 empty] | 0 | 0
20 | Inspectors | [6 empty] | 0 | 0
| Civil - Structual __ ea ___ mos |  |  |  |  | 8 | 12000 | 96000 | 1280
| Mechanical __ ea ___ mos |  |  |  |  | 12 | 12000 | 144000 | 1920
| Electrical __ ea ___ mos |  |  |  |  | 12 | 12000 | 144000 | 1920
| Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 8 | 12000 | 96000 | 1280
0
21 | Training |  |  |  |  | 1 | 40000 | 40000
|  |  | Total Cost of Project Mgt Labor |  |  |  |  | 3229 | 39520

## 13.2 Proj MGT TVL Per
PROJECT MGT TVL AND PER DIEM
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | No. | Cost | Total
Nol | [5 empty] | Units | Per Unit | Cost
1 | [5 empty] | 0 | 0 | 0
2 | RT Fares to Job Site 12 people @ 5 trips |  |  |  |  | 105 | 2000 | 210000
3 | [5 empty] | 0 | 2200 | 0
4 | [5 empty] | 0 | 1000 | 0
5 | Months of Per Diem at Job site (10 men 8 mos) |  |  |  |  | 150 | 3500 | 525000
6 | Months of Pick up Trucks (6ea 12 mos) |  |  |  |  | 160 | 1200 | 192000
7 | Misc Expenditures |  |  |  |  | 1 | 250000 | 250000
8 | [5 empty] | 0 | 0 | 0
9 | [5 empty] | 0 | 0 | 0
10 | [5 empty] | 0 | 0 | 0
11 | [5 empty] | 0 | 0 | 0
12 | [5 empty] | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
0
0
0
0
0
|  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  |  |  | 1177

## 15.0 Sales Tax
SALES TAXES
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2009-01-22
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A3
Location: |  | Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2009-01-23
Item |  | Description |  |  |  | Total | State | Total
Nol | [5 empty] | Cost | Tax | Taxes
1 | Major Mechanical Equipment |  |  |  |  | 2872 | 0.0825 | 236.94
2 | Major Electrical Equipment |  |  |  |  | 547.1 | 0.0825 | 45.1358
3 | Substation Equipment |  |  |  |  | 424 | 0.0825 | 34.98
4 | DCS Eqipment |  |  |  |  | 320 | 0.0825 | 26.4
5 | Instrument |  |  |  |  | 230 | 0.0825 | 18.975
|  |  | Total Cost of Plant Sales Taxes |  |  |  |  | 0