## Recap
ProEnergy EPC
Job Description: |  | "2 GE Fr VII EA's for Corprolec"
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
[16 empty] | Manhours | Manhours
I. Balance of Plant | [15 empty] | US | 1.25
| 1.0 Civil - Structual | [8 empty] | Dismantle | Shipping | BOP Equipment | Engineering | Construciton | Start Up
|  | 1.1 Site Preparation |  |  |  | 88.8889
|  | 1.2 Excavation - Fill |  |  |  | 144.0889 | [9 empty] | 148.1481 | 185.1852
|  | 1.3 Concrete Foundations |  |  |  | 1808.7 | [9 empty] | 602.9 | 753.625
|  | 1.4 Concrete Pilings | [14 empty] | 0
|  | 1.5 Paving Asphalt - Concrete |  |  |  | 669.7778 | [10 empty] | 0
|  | 1.6 Gravel - Sand |  |  |  | 180.6019 | [10 empty] | 0
|  | 1.7 Structual Steel |  |  |  | 211 | [10 empty] | 0
|  | 1.8 Fencing |  |  |  | 88 | [9 empty] | 0 | 0
|  | 1.9 Architectual Treatment |  |  |  | 0 | [10 empty] | 0
|  | 1.9 Evaporation Pond |  |  |  | 0 | [10 empty] | 0
[6 empty] | 3191.0574 |  | 3191.0574 | 4020.7323 |  |  |  |  | 4020.7323 |  |  | 0
0
| 2.0 Buildings | [15 empty] | 0
|  | 2.1 Various Bldgs |  |  |  | 718.5 | [10 empty] | 0
[6 empty] | 0 | [10 empty] | 0
[6 empty] | 718.5 |  | 718.5 | 905.31 |  |  |  |  | 905.31 |  |  | 0
0
| 3.0 Mechanical | [15 empty] | 0
|  | 3.1 Major Mechanical Equipment |  |  |  | 8212 |  |  | 10347.12 |  |  | 10347.12 |  |  |  |  | 0
|  | 3.2 Pipe, Valves and Fittings Material |  |  |  | 1000 |  |  | 1260 | [7 empty] | 0
|  | 3.3 Mechanical Subcontractor |  |  |  | 1960.3296
|  | 3.4 Pipe, Valves and FTG Labor |  |  |  | 1088.64 |  |  | 1371.6864 |  |  |  |  | 1371.6864 |  | 25210 | 31512.5
[6 empty] | 12260.9696 |  | 12260.9696 | [8 empty] | 0
0
| 4.0 Electrical | [15 empty] | 0
|  | 4.1 Major Electrical Equipment |  |  |  | 2982.1 |  |  | 3757.446 |  |  | 3757.446 |  |  |  |  | 0
|  | 4.2 Substation Equipment |  |  |  | 3290 |  |  | 4145.4 |  |  | 4145.4 |  |  |  |  | 0
|  | 4.3 Cable, Conduit, and Tray |  |  |  | 1100
|  | 4.4 Plant Electrical Subcontractor |  |  |  | 1448.8373
|  | 4.5 Substation Subcontractor |  |  |  | 52.7472 |  |  | 66.4615 |  |  |  |  | 66.4615 |  | 20326 | 25407.5
|  | 4.6 Cable, Conduit, and Tray Labor |  |  |  | 1211.76 |  |  | 1526.8176 | [6 empty] | 740 | 925
[6 empty] | 10085.4445 |  | 10085.4445 | [8 empty] | 0
0
| 5.0 Instrumentation | [15 empty] | 0
|  | 5.1 Cems |  |  |  | 0 | [10 empty] | 0
|  | 5.2 Plant Instrumentation |  |  |  | 130 | [10 empty] | 0
|  | 5.3 Instrumentation Subcontractor |  |  |  | 81.2592 | [9 empty] | 1140 | 1425
0
[6 empty] | 211.2592 |  | 211.2592 | 266.1866 |  |  |  |  | 266.1866 |  |  | 0
0
| 6.0 DCS System | [15 empty] | 0
|  | 6.1 Hardware |  |  |  | 320 | [10 empty] | 0
|  | 6.2 Software |  |  |  | 148.5 | [10 empty] | 0
[6 empty] | 468.5 |  | 468.5 | 590.31 |  |  |  |  | 590.31 |  |  | 0
0
0
| 7.0 Plant Erection | [15 empty] | 0
|  | 7.1 Plant Erection |  |  |  | 1604.8692 | [9 empty] | 60040 | 75050
0
[6 empty] | 1604.8692 |  | 1604.8692 | 2022.1352 |  |  |  |  | 2022.1352 |  |  | 0
0
| 8.0 Equipment Rental | [15 empty] | 0
|  | 8.2 Plant Equipment Rental |  |  |  | 1395 | [10 empty] | 0
0
[6 empty] | 1395 |  | 1395 | 1757.7 |  |  |  |  | 1757.7 |  |  | 0
0
| 9.0 Painting |  |  |  |  | 265 |  | 265 | 333.9 |  |  |  |  | 333.9
0
| 10.0 Transportation | [15 empty] | 0
|  | 10.1 BOP US Frt |  |  |  | 1155.3 | [10 empty] | 0
|  | 10.2 Ocean Frt BOP |  |  |  | 900 | [10 empty] | 0
|  | 10.3 Inland Frt BOP |  |  |  | 600 | [10 empty] | 0
[6 empty] | 2655.3 |  | 2655.3 | 3345.678 |  | 3345.678 | [5 empty] | 0
0
0
| 11.0 Site Costs |  |  |  |  | 388.5 |  | 388.5 | 489.51 |  |  |  |  | 489.51 |  |  | 0
0
| 12.0 Engineering | [15 empty] | 0
|  | 12.1 EPC Eng Labor |  |  |  | 1170 | [10 empty] | 0
|  | 12.2 Local Eng |  |  |  | 105 | [10 empty] | 0
|  | 12.3 Eng Travel & Per Diem |  |  |  | 118.1 | [10 empty] | 0
[6 empty] | 1393.1 |  | 1393.1 | 1755.306 |  |  |  | 1755.306 |  |  |  | 0
0
| 13.0 Project Management | [15 empty] | 0
|  | 13.1 Project - Inspectors - Commissioning Lab |  |  |  | 2455 | [9 empty] | 33120 | 33120
|  | 13.2 Travel & Per Diem |  |  |  | 1015 | [10 empty] | 0
[6 empty] | 0 | [10 empty] | 0
0
[6 empty] | 3470 |  | 3470 | 4372.2 | 1748.88 |  |  |  | 2623.32 |  |  | 0
0
| 14.0 Technical Reps | [15 empty] | 0
|  | 14.1 GTG Tech Rep |  | 180 | 2200 | 396000 | [10 empty] | 0
|  | 14.2 Fire Water |  | 15 | 2000 | 30000 | [10 empty] | 0
|  | 14.3 Gas Compressor |  | 0 | 2000 | 0 | [10 empty] | 0
|  | 14.4 Evap Cooler Pkg |  | 0 | 2000 | 0 | [10 empty] | 0
|  | 14.5 Water Treatment |  | 15 | 2000 | 30000 | [10 empty] | 0
|  | 14.6 Commissioning / Start |  | 90 | 2000 | 180000 | [10 empty] | 0
|  | 14.7 Controls Rep |  | 90 | 2000 | 180000 | [10 empty] | 0
0
[6 empty] | 816 |  | 816 | 1028.16 | [5 empty] | 1028.16 |  | 0
0
| 15.0 Project Tests | [15 empty] | 0
|  | 15.1 Soils Compaction |  |  |  | 40 | [10 empty] | 0
|  | 15.2 Concrete Testing |  |  |  | 80 | [10 empty] | 0
|  | 15.3 X Ray |  |  |  | 80 | [10 empty] | 0
|  | 15.4 Plant Performance and Reliability |  |  |  | 200 | [10 empty] | 0
|  | 15.5 Noise Emission Tests | [14 empty] | 0
|  | 15.6 Protective Relays |  |  |  | 30 | [10 empty] | 0
[6 empty] | 430 |  | 430 | 541.8 |  |  |  |  | 270.9 | 270.9 |  | 0
0
| 16.0 Legal |  |  |  |  | 75 |  | 75 | 94.5 | 47.25 |  |  |  | 47.25 |  |  | 0
0
| 17.0 Insurance | [15 empty] | 0
|  | 17.1 Project Insurance |  |  |  | 450 |  | 450 | 567 | 283.5 |  |  |  | 283.5
| 18.0 Dismantling |  |  | 0 | 1150 | 0 |  | 0 | 0 | 0 | [5 empty] | 141327.0481 | 168378.8102
| 19.0 Project Contingency/Risk |  |  |  |  | 39878.4999 |  | 1400 | 0.025464
| 19.1 GT Performance Contingency | [6 empty] | 250
| 20.0 Sales Tax |  |  |  |  | 0 |  |  |  | 2079.63 | 3345.678 | 18249.966 | 1755.306 | 15048.902 | 1299.06
|  | BOP Cost | [5 empty] | 41528.4999
|  | Gross Profit |  |  |  |  | 25% | 10382.125 | 0.18883
|  | GTG Warranty and 5% Markup | [5 empty] | 0
| 21.0 Commissions |  | BOP 3% | Plugged |  | 1557.3187 |  | 1557.3187 | 1928.2216
|  |  | GT 3% |  |  | 1512 |  | 1512
|  |  |  | BOP Sales Price |  |  |  | 54979.9436 | 44565.5739
II. Gas Turbine Generator
|  | Gas Turbine Cost |  |  |  | 42000
|  | Gas Turbine Ocean Frt |  |  |  | 2000
|  | Warranty |  |  |  | 2000
|  | Dual Fuel Conversion |  |  |  | 4000
|  | Gas Turbine Inland Frt |  |  |  | 800
|  |  |  | Mark Up | 0.2 | 8400
[6 empty] | 59200 |  | 59200
|  |  |  | Total Sales Price |  |  |  | 114179.9436

## 1.1 Site Prep
|  |  | SITE PREP | [6 empty] | 1.1
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [5 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [5 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Site |  |  | 500 | 400 | 0.5 | 200000 | 7407.4074 | 12 | 88888.8889
2
3 | [9 empty] | 0
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
88.8889

## 1.2 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 1.2
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [6 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [6 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
| Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Control/Office/Maint |  |  |  | 120 | 60 | 1 | 7200 | 266.6667 | 12 | 3200
| Water Treatment Area |  |  |  | 60 | 50 | 1 | 3000 | 111.1111 | 12 | 1333.3333
| Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Pwr Blk Utility GTG's |  |  |  | 350 | 150 | 2 | 105000 | 3888.8889 | 12 | 46666.6667
| Substation GSU's |  |  |  | 80 | 30 | 3 | 7200 | 266.6667 | 12 | 3200
| Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0
| Liquid Fuel Unloading Shed |  |  |  | 60 | 30 | 1 | 1800 | 66.6667 | 12 | 800
12
2 | Main Plant Area |  |  |  | 500 | 400 | 1 | 200000 | 7407.4074 | 12 | 88888.8889 | 148.1481
3 | Fill |  |  |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0
4 | Substation Area |  |  |  | 0 | 0 | 1 | 0 | 0 | 12 | 0 | 0
5
6 | [11 empty] | 148.1481
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Excavation and Fill | [7 empty] | 144.0889
Evaporation Pond - Option 1 - RO w/EDI Water Treatment w/pond
[5 empty] | 675 | 200 | 5 | 135000 | 25000 | 2.5 | 62500 | 0 | 0 | 62500
Evaporation Pond - Option 2 - Deionizing trailers w/pond
[5 empty] | 475 | 200 | 5 | 95000 | 17592.5926 | 2.5 | 43981.4815 | 0 | 0 | 43981.4815

## 1.3 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 1.3
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [7 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [7 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | POWER ISLAND
| GT Generators |  |  | 2 | 60 | 25 | 6 | 18000 | 666.6667 | 600 | 400000
| Exhaust Stack |  |  | 2 | 30 | 30 | 4 | 7200 | 266.6667 | 600 | 160000
| Generator Base |  |  | 2 | 30 | 12 | 6 | 4320 | 160 | 600 | 96000
| Leg A |  |  | 2 | 27 | 7 | 3 | 1134 | 42 | 600 | 25200
| Leg B |  |  | 2 | 27 | 7 | 3 | 1134 | 42 | 600 | 25200
| Base |  |  | 2 | 25 | 14 | 4 | 2800 | 103.7037 | 600 | 62222.2222
| Emergency Gen Base |  |  | 1 | 16 | 8 | 2 | 256 | 9.4815 | 600 | 5688.8889
| Black Start Gen Base |  |  | 0 | 25 | 12 | 3 | 0 | 0 | 600 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
600
600
2 | BALANCE OF PLANT |  |  | Price: 600
| Gas Valve Module |  |  | 1 | 12 | 9 | 1 | 108 | 4 | 600 | 2400
| PEECC Vault |  |  | 2 | 40 | 16 | 2 | 2560 | 94.8148 | 600 | 56888.8889
| Fin Fan L O Coolers |  |  | 2 | 40 | 20 | 1.5 | 2400 | 88.8889 | 600 | 53333.3333
| Mech Elec Bldg Vault |  |  | 1 | 40 | 23 | 1.5 | 1380 | 51.1111 | 600 | 30666.6667
| Water Wash Skid |  |  | 1 | 19 | 9 | 2 | 342 | 12.6667 | 600 | 7600
| Exhaust Gas Blowers |  |  | 1 | 13.5 | 4 | 2 | 108 | 4 | 600 | 2400
| Mist Elimenator |  |  | 1 | 8 | 8 | 1 | 64 | 2.3704 | 600 | 1422.2222
| Air Processing skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| 15KV Switch Gear NEMA 3R |  |  | 2 | 17 | 9 | 1 | 306 | 11.3333 | 600 | 6800
| 15KV Breaker |  |  | 2 | 19 | 12 | 1 | 456 | 16.8889 | 600 | 10133.3333
| Sump Basin |  |  | 2 | 12 | 10 | 2 | 480 | 17.7778 | 600 | 10666.6667
| Waste Oil Storage Tank |  |  | 1 | 12 | 12 | 1 | 144 | 5.3333 | 600 | 3200
| Oily Water Separator |  |  | 1 | 30 | 15 | 2 | 900 | 33.3333 | 600 | 20000
| Fire Water Pump Skid |  |  | 1 | 35 | 15 | 2 | 1050 | 38.8889 | 600 | 23333.3333
| Instrument air Compressor |  |  | 2 | 10 | 8 | 1 | 160 | 5.9259 | 600 | 3555.5556
| Pipe Rack Stanchons |  |  | 28 | 2.5 | 2.5 | 3 | 525 | 19.4444 | 600 | 11666.6667
| 15 LV Cable Stanchons |  |  | 10 | 2.5 | 2.5 | 3 | 187.5 | 6.9444 | 600 | 4166.6667
| Water Treatment Plant |  |  | 1 | 60 | 40 | 1 | 2400 | 88.8889 | 600 | 53333.3333
| Fire Water Tank base |  |  | 1 | 40 | 40 | 1 | 1600 | 59.2593 | 600 | 35555.5556
| Raw Water Tank Base |  |  | 0 | 35 | 35 | 1 | 0 | 0 | 600 | 0
| Area Light Poles |  |  | 8 | 3 | 3 | 4 | 288 | 10.6667 | 600 | 6400
| Demin Water Pump skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| Demin Stg Tanks 250MGal |  |  | 1 | 38 | 38 | 1 | 1444 | 53.4815 | 600 | 32088.8889
| Demin Forwarding Pumps |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 600 | 1066.6667
| 4160 V Aux Transformers |  |  | 2 | 12 | 12 | 1 | 288 | 10.6667 | 600 | 6400
| 480 V Aux Transformers |  |  | 2 | 10 | 10 | 1 | 200 | 7.4074 | 600 | 4444.4444
| CO2 Tanks |  |  | 4 | 11 | 7 | 1 | 308 | 11.4074 | 600 | 6844.4444
| Cable Trenches / Power Blk |  |  | 2 | 90 | 12 | 1 | 2160 | 80 | 600 | 48000
| Cable Trenches Utilities |  |  | 1 | 250 | 12 | 1 | 3000 | 111.1111 | 600 | 66666.6667
| Fuel Forwarding Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 600 | 1777.7778
| Fuel Heater Skid |  |  | 2 | 20 | 15 | 1 | 600 | 22.2222 | 600 | 13333.3333
| Fuel Tank |  |  | 1 | 65 | 65 | 1 | 4225 | 156.4815 | 600 | 93888.8889
3 | BUILDINGS |  |  | Price: 600
| Control Bldg/Office |  |  | 1 | 75 | 60 | 1 | 4500 | 166.6667 | 600 | 100000
| Warehouse/Maintenance |  |  | 1 | 80 | 60 | 1 | 4800 | 177.7778 | 600 | 106666.6667
| Water Treatment Bldg |  |  | 1 | 60 | 40 | 1 | 2400 | 88.8889 | 600 | 53333.3333
| Gas Compressor Bldg |  |  | 0 | 120 | 45 | 1 | 0 | 0 | 600 | 0
| Electrical Bldg |  |  | 1 | 42 | 20 | 1 | 840 | 31.1111 | 600 | 18666.6667
| Pwr Blk Utility Bldg's |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 600 | 0
| Substation Bldg |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 600 | 0
| Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
| Liquid Fuel Unloading |  |  | 0 | 40 | 60 | 1 | 0 | 0 | 600 | 0
| Pump Bldg |  |  | 1 | 40 | 30 | 1 | 1200 | 44.4444 | 600 | 26666.6667
| Control Room |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0
600
4 | SUBSTATION |  |  | Price: 600
| GSU Transformer |  |  | 2 | 35 | 35 | 2 | 4900 | 181.4815 | 600 | 108888.8889
| GSU Blast Wall |  |  | 0 | 35 | 20 | 1.5 | 0 | 0 | 600 | 0
| (132)KV SF6 Circuit Breaker |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 600 | 0
| (132)KV Disc Switch w/ Stand |  |  | 0 | 10 | 15 | 1 | 0 | 0 | 600 | 0
| Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 600 | 0
| Transmission Line Poles |  |  | 0 | 5 | 5 | 20 | 0 | 0 | 600 | 0
| Insulator Support Base |  |  | 0 | 2.5 | 2.5 | 3 | 0 | 0 | 600 | 0
| PT Support Base |  |  | 0 | 2.5 | 2.5 | 3 | 0 | 0 | 600 | 0
| Static Pole Base |  |  | 0 | 3 | 3 | 5 | 0 | 0 | 600 | 0
|  |  | Total Cost of Foundations | Cubic: 3014.5; Total: 1808.7
[9 empty] | 602.9 | mhrs @ 5mhr/cy

## 1.4 Pilings
PILINGS
|  |  |  | (1,000's) | [7 empty] | 1.4
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [7 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [7 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description | [7 empty] | Cu | Price | Total
Nol |  |  |  |  | Units | Qty | "L" | "D" | "W" | Yd | CuYd | Price
1 | Concrete Pilings
| Pilings GTG x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 119 | 550 | 59259
| Pilings Stack x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 36 | 550 | 17778
| Pilings GSU x _____ |  |  |  | 0 | 0 | 40 | 1 | 1 | 18 | 550 | 8889
| Pilings Gas Comp x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0
| Pilings HRSG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0
| Pilings STG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
0
0
0
0
0
0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
[9 empty] | 0 | 0 |  | 0
Total Cost of Retaining Walls

## 1.5 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 1.5
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [6 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
Nol |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
2 | Gen Removal Areas |  |  | 120 | 30 | 1 | 3600 | 133.3333 | 400 | 53333.3333
3 | Turbine Removal Areas |  |  | 120 | 30 | 1 | 3600 | 133.3333 | 400 | 53333.3333
4 | Entry Ways |  |  | 80 | 15 | 0.5 | 600 | 22.2222 | 400 | 8888.8889
5 | Walk ways |  |  | 220 | 6 | 0.5 | 660 | 24.4444 | 400 | 9777.7778
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 400 | 0
7 | [6 empty] | 0 | 0 |  | 0
8 | [6 empty] | 0 | 0 |  | 0
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 1600 | 20 | 0.7 | 22400 | 829.6296 | 500 | 414814.8148
12 | Parking Lot |  |  | 200 | 50 | 0.7 | 7000 | 259.2593 | 500 | 129629.6296
13 | [6 empty] | 0 | 0 |  | 0
14 | [6 empty] | 0 | 0 |  | 0
15 | [6 empty] | 0 | 0 |  | 0
16 | [6 empty] | 0 | 0 |  | 0
17 | [6 empty] | 0 | 0 |  | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
[7 empty] | 0 | 0 |  | 0
669.7778

## 1.6 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 1.6
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [7 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [7 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
Nol |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 500 | 400 | 0.5 | 100000 | 3703.7037 | 6148.1481 | 25 | 153703.7037
3
4 | Cooling Tower Area |  |  | 0 | 110 | 160 | 0.5 | 0 | 0 | 0 | 25 | 0
5
6 | Substation |  |  | 0 | 600 | 300 | 0.7 | 0 | 0 | 0 | 25 | 0
7
8 | Road ways |  |  | 1 | 1400 | 25 | 0.5 | 17500 | 648.1481 | 1075.9259 | 25 | 26898.1481
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
|  |  | Total Cost of Gravel | Total: 180.6019

## 1.7 Structural
STRUCTUAL STEEL
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [5 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [5 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | # of | Qty | Price | Total
Nol | [5 empty] | Lbs / Tons |  |  | Price
1 | Misc Pipe Rack supports etc. | [5 empty] | 15 | 3500 | 52500
0
2 | 15 KV Cable Tray Stanchons | [5 empty] | 15 | 3000 | 45000
0
3 | GTG walkways and stairs | [5 empty] | 3 | 15000 | 45000
0
4 | Structual Steel for equip supports | [5 empty] | 0 | 0 | 0
5 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 1 | 15000 | 15000
6 | Steel Cover for Oily Catch Basin | [5 empty] | 1 | 3500 | 3500
7 | [6 empty] | 0 | 0 | 0
8 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 50000 | 50000
9
|  |  | Total Cost of Stuctual Steel | [5 empty] | 211 | 0

## 1.8 Fence
FENCING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1800 | 10 | 18000
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 2000 | 19 | 38000
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 14 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 4 | 3000 | 12000
10 | Motor Operated Double Gate(s) |  |  |  |  | 1 | 7000 | 7000
11 | Personnel Gate(s) |  |  |  |  | 6 | 500 | 3000
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 1 | 10000 | 10000
15
|  |  | Total Cost of Fencing |  |  |  |  | 88

## 2.1 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 2.1
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [5 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [5 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [5 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
Nol |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0
2 | Control/Office |  |  |  | 75 | 60 | 4500 | 65 | 292500
3 | Water Treatment |  |  |  | 60 | 40 | 2400 | 45 | 108000
4 | Electric Bldg |  |  |  | 40 | 30 | 1200 | 45 | 54000
5 | Warehouse/Maintenance |  |  |  | 75 | 60 | 4500 | 45 | 202500
6 | Substation Bldg |  |  |  | 0 | 15 | 0 | 40 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Unloading Shed |  |  |  | 60 | 25 | 1500 | 35 | 52500
9 | Pump Room |  |  |  | 0 | 30 | 0 | 45 | 0
10 | Control Room |  |  |  | 0 | 0 | 0 | 0 | 0
11 | Entry Guard House |  |  |  | 15 | 15 | 225 | 40 | 9000
12 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
|  |  | Total Cost of Other Buildings | [5 empty] | 718.5

## 3.1 & 3.3 Mech Equip & Labor
MECHANICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [9 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [9 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [9 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
GTG
1 | GTG Type GE Frame VII EA's |  |  | 2 | 0 | 0 | 0 | 0 | 10 | 10 | 90 | 18000 | 38.88 | 699840
2 | Lube oils and Chemicals 2600 gal ea @ 6.50 |  |  | 2 | 40000 | 80000 | 3000 | 6000 | 10 | 2 | 1 | 40 | 38.88 | 1555.2
3 | Exhaust Stack |  |  | 2 | 1800000 | 3600000 | 150000 | 300000 | 10 | 6 | 15 | 1800 | 38.88 | 69984
4 | Exhaust Expansion Joint |  |  | 2 | 15000 | 30000 | 500 | 1000 | 10 | 0 | 15 | 0 | 38.88 | 0
| LO Fin Fans |  |  | 2 | 120000 | 240000 | 15000 | 30000 | 10 | 4 | 10 | 800 | 29
5 | Anchor Bolts/Fixators |  |  | 2 | 75000 | 150000 | 500 | 1000 | 10 | 0 | 15 | 0 | 38.88 | 0
6
7 | HRSG
8 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
9 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
10 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
11 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
10 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
11 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
12
13 | SCR
14 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
15 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
16
17 | STG
18 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
19 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
20 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
21 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
22 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
23 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
24
25 | Inlet Air Conditioning System
26 | Inlet Chilling Package (Generator) |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
27 | Inlet Fogging System |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
28 | Inlet Overspray System (Includes installation) |  |  | 0 | 427300 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 38.88 | 0
29 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
30 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
31 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
32 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
33
34 | Fuel Gas Systems
35 | Fuel Gas compressor w/ Fin Fans |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
36 | Fuel Gas Regulator Skid |  |  | 2 | 150000 | 300000 | 1000 | 2000 | 10 | 4 | 3 | 240 | 38.88 | 9331.2
37 | Fuel Gas Turbine Metering Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
37 | Fuel Gas Filter Skid & Mnt (___) KW Htr(Htr in Elect) |  |  | 2 | 380000 | 760000 | 5000 | 10000 | 10 | 4 | 5 | 400 | 38.88 | 15552
38 | ESD Valve, ___" ___# |  |  | 1 | 25000 | 25000 | 500 | 500 | 10 | 2 | 1 | 20 | 38.88 | 777.6
39
40 | Liquid Fuel Systems
41 | Unloading Pump Skid |  |  | 2 | 12000 | 24000 | 500 | 1000 | 10 | 3 | 3 | 180 | 38.88 | 6998.4
42 | Metering Skid |  |  | 1 | 135000 | 135000 | 500 | 500 | 10 | 3 | 3 | 90 | 38.88 | 3499.2
43 | Forwarding Pump Skid |  |  | 1 | 35000 | 35000 | 1000 | 1000 | 10 | 3 | 5 | 150 | 38.88 | 5832
44 | Transfer Pump Skid |  |  | 1 | 25000 | 25000 | 1000 | 1000 | 10 | 3 | 3 | 90 | 38.88 | 3499.2
45 | Fuel Heating |  |  | 0 | 85000 | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 38.88 | 0
46 | Filters |  |  | 4 | 15000 | 60000 | 500 | 2000 | 10 | 2 | 2 | 160 | 38.88 | 6220.8
47 | Centrifuge |  |  | 2 | 350000 | 700000 | 30000 | 60000 | 10 | 3 | 5 | 300 | 38.88 | 11664
48 | Injection Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
49 | Storage Tank (300M Gal) |  |  | 1 | 200000 | 200000 | 15000 | 15000 | 10 | 3 | 5 | 150 | 38.88 | 5832
50 | Day Tank |  |  | 1 | 120000 | 120000 | 5000 | 5000 | 10 | 3 | 3 | 90 | 38.88 | 3499.2
51 | Water Supply System
52 | Raw Water Storage Tank 350 M gal |  |  | 1 | 220000 | 220000 | 15000 | 15000 | 10 | 4 | 5 | 200 | 38.88 | 7776
53 | Raw Water Supply Pumps |  |  | 2 | 12000 | 24000 | 2000 | 4000 | 10 | 2 | 2 | 80 | 38.88 | 3110.4
54 | Raw Water Forwarding Pumps |  |  | 0 | 8000 | 0 | 1500 | 0 | 10 | 2 | 2 | 0 | 38.88 | 0
55 | Water Treatment System
56 | Multi Media Filter Package |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 1 | 0 | 38.88 | 0
57 | Water Wash Skid |  |  | 1 | 110000 | 110000 | 5000 | 5000 | 10 | 4 | 5 | 200 | 38.88 | 7776
58 | Demin Treatment System |  |  | 1 | 200000 | 200000 | 5000 | 5000 | 10 | 4 | 20 | 800 | 38.88 | 31104
59 | Demin Storage SS Tank gal |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
60 | Demin water fiberglass tank |  |  | 2 | 25000 | 50000 | 2500 | 5000 | 10 | 4 | 3 | 240 | 38.88 | 9331.2
61 | Demin forwarding pumps (50%) |  |  | 2 | 15000 | 30000 | 500 | 1000 | 10 | 2 | 1 | 40 | 38.88 | 1555.2
62 | Demin Filter Skid |  |  | 2 | 30000 | 60000 | 500 | 1000 | 10 | 2 | 1 | 40 | 38.88 | 1555.2
63 | Demin Water Tank, SS 300M gal |  |  | 0 | 320000 | 0 | 15000 | 0 | 10 | 4 | 4 | 0 | 38.88 | 0
64
65 | Waste Water and Oil Storage and Transfer
66 | Oily Water Separator |  |  | 1 | 55000 | 55000 | 0 | 0 | 10 | 2 | 5 | 100 | 38.88 | 3888
67 | Oily Waste Tank 10000 gal |  |  | 1 | 10000 | 10000 | 2500 | 2500 | 10 | 4 | 2 | 80 | 38.88 | 3110.4
68 | Waste Water Tank 10000 gal |  |  | 1 | 10000 | 10000 | 2500 | 2500 | 10 | 4 | 2 | 80 | 38.88 | 3110.4
69 | Waste Oil and Water forwarding pumps w/ skid |  |  | 2 | 7000 | 14000 | 500 | 1000 | 10 | 2 | 1 | 40 | 38.88 | 1555.2
70
71 | Fire Control Systems
72 | Fire Water Pump Skids (Diesel / Electric) |  |  | 1 | 500000 | 500000 | 5000 | 5000 | 10 | 4 | 5 | 200 | 38.88 | 7776
73 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 85000 | 85000 | 10000 | 10000 | 10 | 4 | 4 | 160 | 38.88 | 6220.8
| Foam System |  |  | 1 | 75000 | 75000 | 1000 | 1000 | 10 | 4 | 4 | 160 | 38.88 | 6220.8
74 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0
75 | Storm Water System
76 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
77 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
78 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
79
80 | Other Systems
81 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 85000 | 85000 | 0 | 0 | 10 | 4 | 3 | 120 | 38.88 | 4665.6
82 | Emergency Generator 300KW |  |  | 1 | 200000 | 200000 | 1500 | 1500 | 10 | 4 | 4 | 160 | 38.88 | 6220.8
83 | Black Start Generator 2 MW |  |  | 0 | 0 | 0 | 5000 | 0 | 10 | 4 | 10 | 0 | 38.88 | 0
84
85 |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 38.88 | 0
86 |  |  | Total Cost | Total: 8212; Frt: 495.5; Hours: 10
[12 empty] | 25210 |  | 949.0608
[9 empty] | Total Manhours |  |  | 25210
[9 empty] | Times Prod Factor |  | 2 | 50420 | 38.88 | 1960.3296
Price per hour based on a 60 hr week with all labor
burdens as follows:
[8 empty] | Local Hrly Cost |  | 20
[8 empty] | Labor Burden 35% |  | 7
27
[8 empty] | Contr Mark up 20% |  | 5.4
32.4
[8 empty] | 50hrs = x1.2 |  | 38.88
| BOP Pipe, Valves, and Fittings, Labor |  |  | Total: 1000; Frt: Pipe, Vlv, and Ftg Labor; Qty: 14000
[9 empty] | Productivity |  | 2 | 28000 | 38.88 | 1088.64

## 4.1 & 4.3 El Equip & Labor
ELECTRICAL EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [11 empty] | Date: |  | 2008-09-26
Customer: |  | Corprolec | [11 empty] | Quote No: |  | T-8041 - 2A
Location: |  | Venn | [11 empty] | Est By: |  | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
Power Island Equipment
1 | Gas Turbine Generator GE Frame VII ea's |  |  |  |  | 2 |  |  |  |  | 10 | 8 | 90 | 14400 | 35.64 | 513216
2 | HRSG |  |  |  |  | 0 | [7 empty] | 0 | 35.64 | 0
3 | SCR |  |  |  |  | 0 | [7 empty] | 0 | 35.64 | 0
4 | STG |  |  |  |  | 0 | [7 empty] | 0 | 35.64 | 0
5 | STG Cooling Tower |  |  |  |  | 0 | [7 empty] | 0 | 35.64 | 0
6 | Chiller Package |  |  |  |  | 0 | [7 empty] | 0 | 35.64 | 0
7 | Water Treatment Package |  |  |  |  | 1 |  |  |  |  | 10 | 4 | 15 | 600 | 35.64 | 21384
8 | [13 empty] | 0 | 35.64 | 0
9 | 15KV
10 | Generator Breaker(s) |  |  |  |  | 2 | 550000 | 1100000 | 75000 | 150000 | 10 | 4 | 5 | 400 | 35.64 | 14256
11 | Distribution Breaker(s) |  |  |  |  | 2 | 55000 | 110000 | 2500 | 5000 | 10 | 4 | 4 | 320 | 35.64 | 11404.8
12 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 4 | 0 | 35.64 | 0
13 | Cable Bus Duct |  |  |  |  | 2 | 350000 | 700000 | 3000 | 6000 | 10 | 5 | 6 | 600 | 35.64 | 21384
14 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 35.64 | 0
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 35.64 | 0
16 | 5KV
17 | Distribution Breaker(s) |  |  |  |  | 9 | 60000 | 540000 | 5000 | 45000 | 10 | 2 | 5 | 900 | 35.64 | 32076
18 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 35.64 | 0
10 | MCC's |  |  |  |  | 2 | 20000 | 40000 | 0 | 0 | 10 | 1 | 1 | 20 | 101 | 2020
11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 6 | 0 | 35.64 | 0
12 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
13 | 600V
14 | Distribution Panel(s) |  |  |  |  | 1 | 85000 | 85000 | 2500 | 2500 | 10 | 2 | 5 | 100 | 35.64 | 3564
15 | GTG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
16 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 4 | 0 | 35.64 | 0
17 | STG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
18 | BOP MCC(s) |  |  |  |  | 1 | 25000 | 25000 | 1000 | 1000 | 10 | 2 | 3 | 60 | 35.64 | 2138.4
19 | Water Treatment MCC(s) |  |  |  |  | 1 | 10000 | 10000 | 500 | 500 | 10 | 2 | 3 | 60 | 35.64 | 2138.4
20 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 8 | 0 | 35.64 | 0
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
22 | Aux Transformer(s)
23 | 15/5KV ___________ MVA |  |  |  |  | 1 | 75000 | 75000 | 5000 | 5000 | 10 | 3 | 5 | 150 | 35.64 | 5346
24 | 15/600V ___________ MVA |  |  |  |  | 1 | 80000 | 80000 | 5000 | 5000 | 10 | 3 | 4 | 120 | 35.64 | 4276.8
25 | 600/120/208V ________ KVA |  |  |  |  | 1 | 5000 | 5000 | 500 | 500 | 10 | 2 | 2 | 40 | 35.64 | 1425.6
26 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
27 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
28 | Area Lighting
29 | Poles _______ High |  |  |  |  | 6 | 1500 | 9000 | 250 | 1500 | 10 | 4 | 2 | 480 | 35.64 | 17107.2
30 | Floodlights _______ Watts |  |  |  |  | 18 | 450 | 8100 | 100 | 1800 | 10 | 1 | 0.2 | 36 | 35.64 | 1283.04
31 | [5 empty] | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
32 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 60 | 0 | 35.64 | 0
33 | Other Systems
34 | UPS |  |  |  |  | 1 | 10000 | 10000 | 0 | 0 | 10 | 3 | 4 | 120 | 35.64 | 4276.8
35 | DC |  |  |  |  | 1 | 20000 | 20000 | 5000 | 5000 | 10 | 3 | 4 | 120 | 35.64 | 4276.8
36 | Cathodic Protection |  |  |  |  | 2 | 15000 | 30000 | 1500 | 3000 | 10 | 3 | 8 | 480 | 35.64 | 17107.2
37 | Lightning Protection |  |  |  |  | 2 | 15000 | 30000 | 1500 | 3000 | 10 | 3 | 8 | 480 | 35.64 | 17107.2
38 | [10 empty] | 10 | 0 | 0 | 0 | 35.64 | 0
39
40 | Temporary Electric |  |  |  |  | 1 | 40000 | 40000 | 2000 | 2000 | 10 | 2 | 30 | 600 | 35.64 | 21384
41 | Electrical Control Module |  |  |  |  | 1 | 65000 | 65000 | 3000 | 3000 | 10 | 4 | 6 | 240 | 35.64 | 8553.6
42 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
43 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
44 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
45 | [6 empty] | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 35.64 | 0
|  |  | Total Cost of Electrical Equipment |  |  |  |  | 2982.1 |  | 239.8 |  |  |  | 20326 |  | 725.7258
20326
[12 empty] | Productivity | 2 | 40652 | 35.64 | 1448.8373
Price per hour based on a 60 hr week with all labor
burdens as follows:
[13 empty] | Local Hrly Cost |  | 20
[13 empty] | Labor Burden 35% |  | 7
27
[13 empty] | Contr Mark up 20% |  | 5.4
32.4
[13 empty] | 45 hrs = 1.1 |  | 35.64
| Cable, Conduit and Tray - Labor | [6 empty] | 1100 |  |  | Labor |  |  | 17000
[12 empty] | Productivity | 2 | 34000 | 35.64 | 1211.76
[11 empty] | 4 | 2 | 45 | 0 | 93.0386 | 0
[11 empty] | 16 | 32 | 45 | 0 | 93.0386 | 0
Blended
51.05
17.8675
68.9175
13.7835
82.701
93.0386

## 4.2 & 4.4 Substa Eq & Labor
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [13 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [13 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [13 empty] | Est By:
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
Nol | [7 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Main Power Transformer 345 KV, 200 MVA (All-in Price) | [5 empty] | 2 | 1500000 | 3000000 | 200000 | 400000 | 10 | 4 | 6 | 480 | 35.64 | 17107.2
2 | SF6 Circuit Breaker(s) _132 KV | [5 empty] | 0 | 125000 | 0 | 2500 | 0 | 10 | 4 | 3 | 0 | 35.64 | 0
3 | Disconnect Switches _132_ KV | [5 empty] | 0 | 15000 | 0 | 1000 | 0 | 10 | 4 | 1 | 0 | 35.64 | 0
4 | Station Post Insulators ____ KV | [5 empty] | 0 | 550 | 0 | 0 | 0 | 10 | 2 | 0.05 | 0 | 35.64 | 0
5 | Insulator Stanchons __21__ High | [5 empty] | 0 | 500 | 0 | 0 | 0 | 10 | 1 | 0.5 | 0 | 35.64 | 0
6 | Insulator Stanchons __13__ High | [5 empty] | 0 | 500 | 0 | 0 | 0 | 10 | 1 | 0.4 | 0 | 35.64 | 0
7 | Dead End Tower(s) | [5 empty] | 0 | 40000 | 0 | 7000 | 0 | 10 | 6 | 5 | 0 | 35.64 | 0
8 | Alum Bus ______ Dia | [5 empty] | 0 | 18 | 0 | 3 | 0 | 10 | 1 | 0.08 | 0 | 35.64 | 0
9 | Alum Bus Conn's | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 35.64 | 0
10 | Alum Bus End Plugs _____ Dia | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.05 | 0 | 35.64 | 0
11 | Alum Bus Support Clamps | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.1 | 0 | 35.64 | 0
12 | Alum Bus "V" Conn's | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0.08 | 0 | 35.64 | 0
13 | Static Wire Poles, ____ High | [5 empty] | 0 | 4000 | 0 | 0 | 0 | 10 | 4 | 1 | 0 | 35.64 | 0
14 | Area Lighting Poles, ____ High | [5 empty] | 0 | 1500 | 0 | 0 | 0 | 10 | 4 | 1 | 0 | 35.64 | 0
15 | Flood Lights, ______ Watts | [5 empty] | 0 | 450 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
16 | #4/0 Grounding Conductor | [5 empty] | 0 | 20000 | 0 | 0 | 0 | 10 | 2 | 20 | 0 | 35.64 | 0
17 | 3/4"x10'-0" Ground Rods & Clamps | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | .04 | 0 | 35.64 | 0
18 | #90 Cadweld Shots | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | .3 | 0 | 35.64 | 0
19 | Metering CT's & CPT's | [5 empty] | 1 | 50000 | 50000 | 0 | 0 | 10 | 2 | 5 | 100 | 35.64 | 3564 | 0
20 | Station Metering w/ In & Out Capabilities | [5 empty] | 0 | 50000 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
21 | Station Protective Relay(s) | [5 empty] | 0 | 50000 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
22 | Station RTU | [5 empty] | 0 | 40000 | 0 | 0 | 0 | 10 | 2 | 5 | 0 | 35.64 | 0
23 | 125V DC System | [5 empty] | 0 | 25000 | 0 | 0 | 0 | 10 | 2 | 2 | 0 | 35.64 | 0
24 | Transmission Line Poles | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 2 | 0 | 35.64 | 0
25 | Transmission Line Strain Insulators | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 35.64 | 0 | 0
26 | Cable Bus, Type _____, Size _____ | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 6 | 0 | 35.64 | 0
27 | Main Power Transformer Oil, ______ Gal | [5 empty] | 2 | 50000 | 100000 | 10000 | 20000 | 10 | 2 | 2 | 80 | 35.64 | 2851.2
28 | Main Power Transformer Dress Out & Test | [5 empty] | 2 | 70000 | 140000 | 0 | 0 | 10 | 2 | 2 | 80 | 35.64 | 2851.2
29 | Fiber Optic Cable w/ Messenger Cable | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 35.64 | 0 | 0
30 | Fiber Optic Cable Fittings & Terminations | [5 empty] | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 2 |  |  | 0
31
32 | Price per hour based on a 60 hr week with all labor |  |  |  | Total: 0
33 | burdens as follows: |  |  |  | Total: 0
34 |  |  |  |  | Total: 0
35 |  | Local Hrly Cost |  | 20 | Total: 0
36 |  | Labor Burden 35% |  | 7 | Total: 0
37 |  |  |  | 27 | Total: 0
38 |  | Contr Mark up 20% |  | 5.4 | Total: 0
39 |  |  |  | 32.4
40 |  | 60hrs = x1.1 |  | 35.64
41
42
43
44 |  |  |  |  | Total: 0
|  |  | Total Cost of Substation Equipment |  | Total: 3290; Frt: 420; Qty: 740; Total: 26.3736
[13 empty] | Total Hours |  | 740
[13 empty] | Prod Factor | 2 | 1480 | 35.64 | 52.7472

## 5.1 CEMS
CEM's
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Cems | Cost | Cost
1 | Rosemont CEM's Unit Most States for 1 ea GTG |  |  |  |  | 0 | 120 | 0
2 | Rosemont CEM's Unit for Califormia for 1 ea GTG |  |  |  |  | 0 | 130 | 0
3 | Installation Support |  |  |  |  | 0 | 18 | 0
|  |  | Total Cost of CEM's |  |  |  |  | 0

## 5.2 Instrument
PLANT INSTRUMENTATION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [9 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [9 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [9 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Instrumentation for GTG |  |  |  | 2 | 45000 | 90000 | 10 | 4 | 10 | 800 | 35.64 | 28512
0
2 | Instrumentation for SCR |  |  |  | 0 | 0 | 0 | 10 | 4 | 15 | 0 | 35.64 | 0
3 | Instrumentation for HRSG |  |  |  | 0 | 0 | 0 | 10 | 4 | 15 | 0 | 62 | 0
4 | Instrumentation for Injection Water Treatment |  |  |  | 1 | 25000 | 25000 | 10 | 4 | 5 | 200 | 35.64 | 7128
5 | Instrumentation for Liquid Fuel System |  |  |  | 1 | 15000 | 15000 | 10 | 2 | 7 | 140 | 35.64 | 4989.6
6 | Instrumentation for gas compressors |  |  |  | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 35.64 | 0
7 | Labor to Install CEMS |  |  |  | 0 | 0 | 0 | 10 | 4 | 5 | 0 | 35.64 | 0
Price per hour based on a 60 hr week with all labor
burdens as follows:
|  | Local Hrly Cost |  | 20
|  | Labor Burden 35% |  | 7
27
|  | Contr Mark up 20% |  | 5.4
32.4
|  | 45hrs = x1.1 |  | 35.64
|  |  | Total Cost of Plant Instrumentation |  | Total: 130; Qty: 1140; Total: 40.6296
[9 empty] | Total Hours |  | 1140
[9 empty] | Prod Factor | 2 | 2280 | 35.64 | 81.2592

## 6.1 DCS Hard
DCS HARDWARE
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [6 empty] | Cost | Cost
1 | DCS Hardware |  |  |  |  | 1 | 200000 | 200000
0
0
2 | Lot of Misc interconnecting cables etc. |  |  |  |  | 2 | 15000 | 30000
3 | PBX Communications System |  |  |  |  | 1 | 20000 | 20000
0
4 | Loud Speaker System |  |  |  |  | 1 | 20000 | 20000
5 | Documentation |  |  |  |  | 1 | 50000 | 50000
|  |  | Total Cost of DCS Software |  |  |  |  | 320

## 6.2 DCS Soft
DCS SOFTWARE
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Hrs | Cost | Cost
1 | Software for DCS |  |  |  |  | 1500 | 75 | 112500
2 | Software for O & M Package |  |  |  |  | 600 | 60 | 36000
3 | Mark VI Download |  |  |  |  | 0 | 6000 | 0
|  |  | Total Cost of DCS Software |  |  |  |  | 148.5

## 7.1 Erection
PLANT ERECTION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [7 empty] | Date: | 2008-09-26 | *.2
Customer: |  | Corprolec | [7 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [7 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  | No | Hours | Qty | Qty | Qty | Rate | Total
Nol |  |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | GTG Erection |  |  |  | 2 | 10 | 24 | 120 | 57600 | 26.73 | 1539648
2 | HRSG Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 26.73 | 0
3 | SCR Erection |  |  |  | 0 | 10 | 10 | 60 | 0 | 26.73 | 0
4 | Water Treatment and FW Systems |  |  |  | 1 | 6 | 6 | 20 | 720 | 26.73 | 19245.6
5 | Liquid Fuel system |  |  |  | 1 | 6 | 6 | 20 | 720 | 26.73 | 19245.6
6 | BOP Equip Erection |  |  |  | 1 | 10 | 10 | 10 | 1000 | 26.73 | 26730
7 | Gas Compressor Erection |  |  |  | 0 | 10 | 6 | 5 | 0 | 26.73 | 0
8 | Evap Cooling Erection |  |  |  | 0 | 10 | 4 | 4 | 0 | 26.73 | 0
9 | Fire Water Pump Skid |  |  |  | 0 | 10 | 4 | 4 | 0 | 26.73 | 0
10 | STG Erection |  |  |  | 0 | 10 | 12 | 36 | 0 | 26.73 | 0
11 | STG Cooling Tower |  |  |  | 0 | 10 | 8 | 8 | 0 | 26.73 | 0
Price per hour built up as follows:
Blended
|  | Local Hrly Cost |  | 15
|  | Lab Burden 35% |  | 5.25
20.25
|  | Contr Mark up 20% |  | 4.05
24.3
| For 45 hr / wk multiply by 1.1 |  |  | 26.73
|  |  | Total Cost of Plant Erection | [5 empty] | 60040 |  | 1604.8692
[7 empty] | Total Hours |  | 60040
[7 empty] | Prod Factor | 2 | 120080 | 26.73 | 3209.7384

## 8.2 Equip rent
EQUIPMENT RENTAL
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [6 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
Nol | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 2 | 30 | 60 | 4000 | 240000
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 120 | 240 | 2000 | 480000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Sky Tracs |  |  |  |  | 2 | 120 | 240 | 70 | 16800
| 2 ea Fork Lifts |  |  |  |  | 2 | 120 | 240 | 70 | 16800
| 1 ea Man Lift |  |  |  |  | 2 | 120 | 240 | 80 | 19200
| 2 ea Welders |  |  |  |  | 2 | 150 | 300 | 60 | 18000
2 | HRSG Erection
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
3 | SCR/CO
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
| 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
4 | STG
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
| 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
5 | STG Cooling Tower
| 150 Ton Crane |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 40 Ton Crane |  |  |  |  | 0 | 0 | 0 | 1500 | 0
| 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
6 | Fuel Gas Compressor Rental per Compr Skid
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
7 | BOP Equip Rental per ea GTG
| 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
| 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
| 1 ea 50 Ton Crane w/ operator |  |  |  |  | 1 | 30 | 30 | 2000 | 60000
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 180 | 180 | 1500 | 270000
| 2 ea Fork Lifts |  |  |  |  | 1 | 120 | 120 | 70 | 8400
| 2 ea Sky Tracs |  |  |  |  | 2 | 160 | 320 | 70 | 22400
| 2 ea Pick ups |  |  |  |  | 2 | 90 | 180 | 30 | 5400
| 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 160 | 160 | 70 | 11200
8 | Substation Equip Rental (GSU Only)
| 1 ea 200 Ton Crane w/ operator |  |  |  |  | 2 | 5 | 10 | 4000 | 40000
| 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
| 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 20 | 20 | 1500 | 30000
| 2 ea Man Lifts |  |  |  |  | 1 | 45 | 45 | 80 | 3600
| 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
| 5 ea Welders |  |  |  |  | 1 | 40 | 40 | 80 | 3200
9 | Heavy Lift of GTG and Gen |  |  |  |  | 1 | 150000 |  |  | 150000
|  |  | Total Cost of Plant Equip Rental |  |  |  |  | 2340 |  | 1395

## 9.0 Paint
PLANT PAINTING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Paint for GTG |  |  |  |  | 2 | 80000 | 160000
2 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
3 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 135000 | 0
4 | Paint for Pipe Rack etc. |  |  |  |  | 2 | 25000 | 50000
5 | Paint for BOP Equipment |  |  |  |  | 1 | 40000 | 40000
6 | Paint for Gas Compressor |  |  |  |  | 0 | 15000 | 0
7 | Paint for Water Treatment |  |  |  |  | 1 | 15000 | 15000
8 | Paint for Waste Water Treatment |  |  |  |  | 0 | 15000 | 0
9 | Paint for HRSG |  |  |  |  | 0 | 95000 | 0
|  |  | Total Cost of Plant Painting |  |  |  |  | 265
0

## 10.0 Transportation
PLANT TRANSPORTATION
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 495.5 | 495.5
2 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 239.8 | 239.8
3 | Transportation Substation Equip |  |  |  |  | 1 | 420 | 420
4 | Transportation of GTG
5 | Transportation of SCR
6 | Transportation of HRSG
7 | Transportation of STG
|  |  | Total Cost of Plant Transportation |  |  |  |  | 1155.3

## 11.0 Site Costs
SITE COSTS
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant | [6 empty] | Date: | 2008-09-26
Customer: |  | Corprolec | [6 empty] | Quote No: | T-8041 - 2A
Location: |  | Venn | [6 empty] | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
Nol | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
| Office Trailers |  |  |  |  | 4 | 8 | 900 | 28800
| Porta Potties |  |  |  |  | 4 | 8 | 150 | 4800
| Water and Ice |  |  |  |  | 4 | 8 | 500 | 16000
| Fed X |  |  |  |  | 1 | 8 | 300 | 2400
| Telephone |  |  |  |  | 1 | 8 | 2500 | 20000
| Office Supplies |  |  |  |  | 1 | 8 | 1000 | 8000
| Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 8 | 4000 | 32000
| Misc Items |  |  |  |  | 1 | 8 | 3000 | 24000
|  |  | Total Monthly Cost | [5 empty] | 136000
2 | Total Project Cost = Cost per Month Times Number of Mos
Plus the Project One Time Costs.
| Monthly Site Costs | [5 empty] | 1 | 136000 |  | 136000
| One Time Costs | [5 empty] | 0
| 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 50000
| Cad Station | [8 empty] | 10000
| Computers | [8 empty] | 15000
| Telephone System and Satalite Dish | [8 empty] | 15000
| Plotter | [8 empty] | 10000
| Fax Machine and Printers | [8 empty] | 2500
| Misc equip | [8 empty] | 150000
|  |  | Total Cost of Project Site Costs | [6 empty] | 388.5

## 12.1 Engineering
ENGINEERING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Conceptual Engineering PEPC |  |  |  |  | 1 | 25000 | 25000
2 | Detailed Engineering per GTG |  |  |  |  | 2 | 450000 | 900000
3 | Detailed Engineering per HRSG |  |  |  |  | 0 | 0 | 0
4 | Detailed Engineering per STG |  |  |  |  | 0 | 0 | 0
5 | Detailed Engineering of Substation |  |  |  |  | 1 | 75000 | 75000
6 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 35000 | 35000
7 | Detailed Engineering for civil/structural |  |  |  |  | 1 | 75000 | 75000
8 | Documentation |  |  |  |  | 1 | 60000 | 60000
|  |  | Total Cost of Engineering |  |  |  |  | 1170

## 12.2 Local Engr-Arch
LOCAL ENGINEERING
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | Soils & Environmental Eng |  |  |  |  | 1 | 15000 | 15000
2 | Civil Engineer |  |  |  |  | 1 | 30000 | 30000
3 | Mechanical Engineer |  |  |  |  | 1 | 30000 | 30000
4 | Electrical Engineer |  |  |  |  | 1 | 30000 | 30000
5 | Other |  |  |  |  | 0 | 0 | 0
|  |  | Total Cost of Local Engineering |  |  |  |  | 105

## 12.3 Engr Trav & per diem
ENGINEERING TVL AND PER DIEM
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Qty | Unit | Total
Nol | [5 empty] | Units | Cost | Cost
1 | [5 empty] | 0 | 0 | 0
2 | RT to Job Site |  |  |  |  | 10 | 3500 | 35000
3 | [5 empty] | 150 | 150 | 22500
4 | Days of Per Diem cost for Eng Days at Job Site |  |  |  |  | 90 | 180 | 16200
5 | [5 empty] | 0 | 100 | 0
6 | Auto Rental for Eng Days at Job Site |  |  |  |  | 120 | 120 | 14400
4 | Misc Travel Expentitures |  |  |  |  | 1 | 30000 | 30000
|  |  | Total Cost of Eng Tvl and Per Diem |  |  |  |  | 118.1

## 13.1 Proj Mgt Labor
PROJECT MANAGEMENT LABOR
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
160
Item |  | Description |  |  |  | No. | Cost | Total | hr/mo
Nol | [5 empty] | Mos | Per Mo | Cost
Project Mng't Home Office
1 | Project Mgr Months on Project |  |  |  |  | 8 | 15000 | 120000 | 1280
2 | Admin Mgr Months on Project |  |  |  |  | 8 | 7000 | 56000 | 1280
3 | Scheduler |  |  |  |  | 6 | 7000 | 42000 | 960
4 | Purchasing Agent |  |  |  |  | 2 | 7000 | 14000 | 320
5 | Expediter |  |  |  |  | 1 | 5000 | 5000 | 160
6 | Home Office Logistic Coordinator |  |  |  |  | 8 | 12000 | 96000 | 1280
Project at Job Site
7 | Secretary at Job Site |  |  |  |  | 8 | 6000 | 48000 | 1280
8 | Construction Mngr |  |  |  |  | 8 | 15000 | 120000 | 1280
9 | Contract Cost admin |  |  |  |  | 0 | 8000 | 0 | 0
10 | Mechanical Supervisor |  |  |  |  | 7 | 15000 | 105000 | 1120
11 | Electrical Supervisor |  |  |  |  | 7 | 15000 | 105000 | 1120
12 | Civil Supervisor |  |  |  |  | 6 | 15000 | 90000 | 960
13 | Clerks |  |  |  |  | 12 | 5000 | 60000 | 1920
14 | Warehousemen |  |  |  |  | 12 | 4000 | 48000 | 1920
15 | Draftsman |  |  |  |  | 6 | 9000 | 54000 | 960
16 | Security |  |  |  |  | 8 | 15000 | 120000 | 1280
17 | Safety |  |  |  |  | 8 | 12000 | 96000 | 1280
18 | QA/QC Mngr |  |  |  |  | 8 | 12000 | 96000 | 1280
|  |  |  | Total Proj Mgt Labor |  |  |  | 1275000 | 0
| US Electricians and Welders 6ea plus 6 ea 6 mos |  |  |  |  | 36 | 15000 | 540000 | 5760
19 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 8 | 15000 | 120000 | 1280
[8 empty] | 0 | 0
20 | Inspectors | [6 empty] | 0 | 0
| Civil - Structual __ ea ___ mos |  |  |  |  | 8 | 12000 | 96000 | 1280
| Mechanical __ ea ___ mos |  |  |  |  | 12 | 12000 | 144000 | 1920
| Electrical __ ea ___ mos |  |  |  |  | 12 | 12000 | 144000 | 1920
| Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 8 | 12000 | 96000 | 1280
0
21 | Training |  |  |  |  | 1 | 40000 | 40000
|  |  | Total Cost of Project Mgt Labor |  |  |  |  | 2455 | 33120

## 13.2 Proj MGT TVL Per
PROJECT MGT TVL AND PER DIEM
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | No. | Cost | Total
Nol | [5 empty] | Units | Per Unit | Cost
1 | [5 empty] | 0 | 0 | 0
2 | RT Fares to Job Site 12 people @ 5 trips |  |  |  |  | 78 | 3500 | 273000
3 | [5 empty] | 0 | 2200 | 0
4 | [5 empty] | 0 | 1000 | 0
5 | Months of Per Diem at Job site (10 men 8 mos) |  |  |  |  | 120 | 2500 | 300000
6 | Months of Pick up Trucks (6ea 12 mos) |  |  |  |  | 160 | 1200 | 192000
7 | Misc Expenditures |  |  |  |  | 1 | 250000 | 250000
8 | [5 empty] | 0 | 0 | 0
9 | [5 empty] | 0 | 0 | 0
10 | [5 empty] | 0 | 0 | 0
11 | [5 empty] | 0 | 0 | 0
12 | [5 empty] | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
0
0
0
0
0
|  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  |  |  | 1015

## 15.0 Sales Tax
SALES TAXES
(1,000's)
Project Name: |  | Corprolec 2ea Fr VII EA's Power Plant |  |  |  |  | Date: | 2008-09-26
Customer: |  | Corprolec |  |  |  |  | Quote No: | T-8041 - 2A
Location: |  | Venn |  |  |  |  | Est By: | WTS/JDP/LF
Bid Due Date: |  | 2008-09-26
Item |  | Description |  |  |  | Total | State | Total
Nol | [5 empty] | Cost | Tax | Taxes
1 | Major Mechanical Equipment |  |  |  |  | 8212 | 0.0825 | 677.49
2 | Major Electrical Equipment |  |  |  |  | 2982.1 | 0.0825 | 246.0232
3 | Substation Equipment |  |  |  |  | 3290 | 0.0825 | 271.425
4 | DCS Eqipment |  |  |  |  | 320 | 0.0825 | 26.4
5 | Instrument |  |  |  |  | 130 | 0.0825 | 10.725
|  |  | Total Cost of Plant Sales Taxes |  |  |  |  | 0