DISMANTLING, REMOVAL, INSTALLATION & COMMISSIONING

OF (2) GE FRAME 7EA GAS TURBINE GENERATORS

AT THE GENERAL RAFAEL URDANETA

TERMOELECTRIC POWER COMPLEX

(ENGLISH TRANSLATION)

- GENERAL SCOPE

The following terms of reference include the supply of all materials, parts, tooling, equipment and whatever other equipment or work even if they are mentioned here required for the disassembly, transportation, installation and startup of the (2) Frame 7EA Turbo-generators, GSU Transformer, the other auxiliary equipment and balance of plant equipment in Simple Cycle operation with a capacity of 170 MW with provision for the expansion to Combined Cycle.   The Units are currently installed near Memphis, Tennessee USA and will be installed at an available location south of the TermoZulia Plant located in La Cañada de Urdaneta located between Lake Maracaibo and the old road to La Cañada and approximately two (2) kilometers from the Bajo Grande Refinery owned by PDVSA.

The terms of reference include: Transportation from Houston to the Termozulia Plant, Assembly and Start-up of the Frame 7EA Turbogenerators, GSU Transformer, the auxiliary equipment and balance of plant.

This Specification includes the following in general:

- Supply of anchor bolts, sole plates, fixators, dowel pins, washers, nuts and other components required for the foundations.  These must be supplied to ENELVEN (15) days before the date of initiation.

- Supply of all power and control cabling required for the plant.  These materials must be available upon when the major equipment reaches the site.

- Transportation from the Port of Houston to the site at the Termozulia Plant.

- Insurance of the equipment during ocean and over land transportation and erection.

- All electrical and mechanical works required to install the units at the Termozulia Plant site.

- Conversion of the unit for operation on # 2 Diesel.

- Start-up the plant.

- Any other equipment or work that is required to transport, install and start up both units even if we have not covered these in this RFP.

- Parts required to install and start-up the units.

- Consumables required for initial operation.

The plant is to be designed with the expectation of conversion to Combined Cycle operation.

The contract must provide everything necessary to comply with the specifications attached to them but not limited to the successful implementation and acceptance of the above lines from THE CONTRACTING ENTITY, we understand that the contract only THE CONTRACTING ENTITY will provide activities, equipment, systems and infrastructure which are indicated in this specification.

  - EQUIPMENT & ACTIVITIES NOT INCLUDED IN THIS SCOPE

- Construction of Tanks and storage of Liquid Fuel and supply of liquid fuel to the perimeter of the plant.

- Supply of Water to the perimeter of the plant.

- Supply of Instrument Air to the perimeter of the plant.

- Site Preparation, Earth Moving and Foundations.

- Studies for: Short Circuit of the Transmission System, Environmental Impact.

- Conceptual and detailed engineering for the civil work of the plant.

- Electrical Interconnection from the GSU transformer to the 230KV substation.

- Roads, Lighting and Landscaping

- Storm Drains and Liquid Waste

- Pipelines and culverts

- Supply of the Frame 7EA Turbogenerators, GSU Transformers and other auxiliary equipment for Southaven

2.  SPECIFIC SCOPE

2.0  Transportation from the Port of Houston to the Termozulia Site as well as Installation and Start-up of the Frame 7EA Turbogenerators, the GSU transformers and other auxiliary equipment and balance of plant.

2.1  POINTS OF TERMINATION

The points of termination for all accessories, equipment, points of connection and / or interrupters are defined in the section.

2.1.1  Electrical & Instrumentation

- High Voltage Power termination point is at the high voltage bushings of the GSU Transformer.

- Instrument Air connection is at the flange on the instrument air supply pipeline for the entire plant.

- Points of connection for the Substation / Turbogenerator protection.

2.1.2  Fuel Systems

- Liquid Fuel connection point is at the flange of the Owner supplied day tank adjacent to the plant.

- Gas Fuel connection is at the Owner supplied gas pipeline at the boundary of the plant.

- Control and operation signals for the fuel systems are at the terminal panel in the plant.

2.1.3  Demineralized Water

(Water Injection, Fogging, Cooling, Compressor Wash)

- Connection to the Owner supplied Demin water pipeline of storage tank.

- Control and operation signals for the Demin water system is at the terminal panel in the plant.

2.1.4 Drainage System

- Connection flange or connection at plant boundary to the Owner supplied Transfer Pumps or Waste Transport Trucks.

2.1.5  Fire Water System

- Connection points to supply the equipment as required.  Owner supplies fire water pipeline to plant boundary.

2.1.6  Lubrication Oil System

- Flange connection at the plant boundary.

2.2  WORK PLAN

The Contractor will prepare and supply a Project Schedule which details all the activities that will be executed.  The Schedule will cover all activities from transport to the Port of Maracaibo until the completion of plant start-up.

The Contractor will prepare and provide a weekly report that updates the physical progress of the project including as a minimum the following:

- Master Timeline of planned vs. actual execution

- Resource Histogram of programmed vs. actual

- Sequence and timing of systems planned vs. actual

- Graphs showing planned progress vs. actual for systems and the project

- Graphs showing progress payments

- List of imported equipment and materials and their status

- Milestones for measuring the progress of each phase

- Project control meetings

- Tables showing trends and deviations

- Two and four week look ahead plans

- Daily plan of personnel and equipment for the work

- Reports to be detailed by activity

- Physical reprogramming

- Managing scope changes and potential claims

- Preparation of a historical dossier with photos and video of the most important events regarding the dismantling and removal of equipment

2.3  SECURITY OF THE WORK

The security of the construction area of this project and the construction of the facilities is the responsibility of the Contractor who shall coordinate security in the area with the Owner.

The contractor will build a temporary fence around the area destined for the installation of the gas turbines and associated equipment.

2.4  MATERIALS & CONSUMABLES

It is the responsibility of the Contractor to supply and replace in all phases of the project, all materials and consumables not limited to:  lubricating oil, transformer oil, CO2, ethylene glycol, grease, silica and any other consumables required.

The Owner will supply only water and fuel for testing and startup of the plant.

2.5  INDUSTRIAL HYGENE AND SECURITY

The Contractor is responsible for the security of each and everyone of its workers.  In order to accomplish this, it is the obligation of the Contractor to supply all protective equipment necessary to ensure at all times the prevention of accidents during the development of The Work.

In addition, the Contractor  will ensure security at the facilities that are part of the scope of work including the installation of warning signs, life lines, barricades, etc. in areas where the danger of accidents exist.

The Contractor shall have fixed and portable gas detection for explosives in the work areas near the natural gas supply for PDVSA or in areas where there is the possibility of the presence of gas.

The Contractor shall submit to the Owner a “Risk Assessment at Work” (ART) which will identify all existing risks in the Work which will require the need for using both commonly used and special protective equipment for the personnel.  This “ART” will be required before the start of the work.

The Contractor shall keep a record of all accidents and incidents occurring at the work site during the execution of its work and report these immediately to the Owner indicating the origin, implications, impacts and corrective measures taken to avoid their reoccurrence.

The Contractor shall submit a program of industrial health and safety including the activities to be developed during the execution of the work such as lectures, field inspections, equipment, tools, etc.  Tools may not be used with consumable materials that have the presence of asbestos.

The Contractor must maintain throughout the execution of the work, an Industrial Safety staff member certified by an institution registered under the Ministry of Education.

The Owner will conduct a Security Audit before the Contractor commences the Work.

The Contractor shall ensure that it meets all requirements of the Owner’s Environmental Health & Safety program related to the Work.  All new staff brought in by the Contractor shall receive an orientation on EH&S prior to stating work at the site.

The Contractor shall establish the working hours so as to accomplish its scope within the program established for the Work.

Personal protective equipment must comply with established security policies implemented in the Industrial Safety program of the Owner and based on Articles 06,19, 20 of the Organic Law of Prevention, Conditions and Labor Environment (LOPCYMAT) (Annex 1).

2.6  EQUIPMENT

All necessary equipment such as cranes, gantrics, lowboy, backhoes, forklifts, compressed air, electric welding machines, heat treatment, etc.. required during the relocation, installation and service must be supplied by the contractor.

The contractor shall deliver to Owner, certification for this equipment. 
The Contractor shall submit for approval by the Owner, the carrier to be used for the mobilization of the turbine units and their equipment.

  - QUALITY CONTROL

The Contractor must have a quality control program to indicate in tabular summary: components, equipment and civil works, mechanical and electrical, if any, to which they will carry out tests, tests to be performed objective of the test, under which rules governing the testing, acceptance criterion, the area of the component that you are testing stage and involved, taking as stages: removal, assembly, alignment and liquid fuel implementation.

The Contractor must submit well in advance the schedule of tests and procedures for conducting tests and the various components covered by this specification.

The factory acceptance tests must be endorsed by the inspectors or the relevant entity designated by the Owner who will verify compliance by signing a paper record of compliance as evidence.

The Quality Control Program should take into consideration for each of the systems, components, civil work, mechanical and electrical the terms of these specifications or as a default, the rules of PDVSA, COVENIN, National or International.

The Contractor’s quality control program must be approved by the Owner who may make comments or request changes or the inclusion of additional tests it may require.

2.8   WORKS, SERVICES & CIVIL CONSTRUCTION

The Contractor must build or bring in temporary construction facilities for assembly and construction of the gas turbine units and the balance of plant.  The facilities should have communication capabilities, electricity, basic services such as drinking water, service water, sewage storage/desposal, dining, lockers, portable toilets, etc.  The facility should also include physical space for up to (10) Owner’s inspectors.

The Contractor must provide potable and drinking water for its activities.  All waste generated must be disposed of at sites designated for that purpose by local, regional and national authorities with means of transport with proper permits for that purpose.

The Owner will supply temporary power to the plant boundary for Contractor’s temporary facilities and site electrical distribution.

All wooden crates and equipment containers received should be transferred and stored in an orderly manner at the site in an area indicated for this purpose by the Owner.

Permanent cleanup of the work area including clearing of a 40 meter wide peripheral band around the site will be the sole responsibility of the Contractor.  Final disposal of waste must be disposed of in areas designated by local authorities and transported by proper means and with proper permits.

Any required waste water service during the construction process is the responsibility of the Contractor with disposal be made at sites designated by local authorities for that purpose and with proper permits.  This also includes the approval by the Owner of any affluent discharge at the Termozulia site.

2.9   ACTIVITIES TO BE IMPLEMENTED

The Contractor shall provide the hardware to mount the major equipment to their foundations (Turbogenerators, Exhaust Stacks and GSU Transformer).  This hardware includes:  anchor bolts, sole plates, fixators, dowel pins, washers and nuts, and grouting.  These components should be provided (15) days after the signed notice to proceed.

2.9.1  The Contractor will prepare an area for the storage of the equipment prior to installation in its foundations.  All of the accessories and balance of plant equipment will be supplied by the Contractor excluding the civil works.

2.9.2  The Contractor will supply all necessary power and control cable in accordance with the technical specifications and quality standards of the manufacturer.

2.9.3  The Contractor will verify and confirm based on the manufacturer’s certified drawings, the location in the foundations of the Turbogenerator the following:  anchor bolts, sole plates, fixators and location of stub ups for piping connections and electrical conduits prior to construction of the foundations.

2.9.4 The Contractor will mobilize and transport from the Port of Maracaibo to the Termozulia Plant the (2) Frame 7EA gas turbine generators, the GSU Transformer with its auxiliary equipment and the balance of plant equipment.

2.9.5  The Contractor is responsible for the supply and installation of the power and control cabling and connections in accordance with the manufacturer’s technical specifications taking into consideration the changes in location of the equipment from their original layout.

2.9.6   The Contractor is responsible for the installation of all of the equipment associated with the Units Serial Nos. 297631 and 297632 and their associated balance of plant equipment.

The Contractor will execute all the activities necessary to preserve the equipment during the installation phase until it is put into service.

The Contractor will guarantee the integrity of the equipment and its accessories.  Any damaged component must be repaired or replaced to the satisfaction of the Owner.

The disposition of the equipment will be defined by the Owner.

The installation of the equipment should be in strict accordance with the standard procedures of the manufacturer.

The Contractor must install and complete the power and control connections of all the equipment.  Following the installation, the Contractor must conduct both static tests of the connections and energized tests in the presence of the Owner or its designee.

The Contractor must submit to the Owner, the following reports not limited to:

- Dorsier of the Assembly

- Allignment Data of the rotating equipment

- Results of the Non-destructive Tests (NDE, Rx, and other)

2.9.7  All structures must be coated with paint and materials and colors in accordance with the established standards of the Owner.

2.9.8  Conversion of the units for operation with liquid fuel (# 2 Diesel).  The Contractor is responsible for the design, supply and installation of the equipment and accessories necessary for the conversion for operation with liquid fuel must be in accordance with the original equipment manufacturer’s standards.

The Contractor must supply and install the control software for operation with liquid fuel.  All cost relating to assuring the integrity of the software purchased by the Owner or supplied by the Contractor shall be borne by the Contractor.

The equipment supplied for the liquid fuel conversion without limitation will include:  pumps, piping, valves, filters, injectors, atomizing air compressor, motors, controls, and others.

The Contractor must supply in less than (60) days from the anticipated initiation of the installation phase of the Turbogenerators, the operating perameters for the liquid fuel to be supplied by the Owner to the Termination Point as defined in Clause 2.1.2. so the Owner can guarantee the sufficient supply at that point.

Additionally, the Contractor must supply within (60) days of the anticipated initiation of the installation phase of the Turbogenerators, the requirements of the Owner so he can insure the on time provision of adequate fuel supply, foundations, pipelines and infrastructure so the Contractor can install the liquid fuel equipment outside the gas turbine compartments.

The Owner will only design and construct the civil infrastructure necessary to mount the equipment and structures outside the gas turbine compartments.  The installation of any equipment inside the compartments is the responsibility of the Contractor.

The Contractor is must supply and connect all the equipment associated with the liquid fuel conversion inside the points of termination of the plant.

2.9.9   Start Up and Commissioning

The Contractor must provide the Owner in advance a schedule of activities to be run during the startup and commissioning of the plant.  During the startup and commissioning, daily meetings will be held to discuss and define the activities which will talk place the following day.

The Contractor shall furnish all tools, spare parts, materials and consumables required for startup and commissioning of the gas turbine generators and the balance of plant equipment.

The gas turbine generators should be able to operate on # 2 Diesel as a primary fuel and natural gas as an alternative fuel.  The Contractor must ensure that the control system is configured to accomplish this.

The Contractor shall be responsible to energize, isolate and put into service all equipment belonging to the gas turbine generating equipment during the testing and commissioning of the plant.  It will also be responsible for flushing all systems within the work scope.

The Contractor shall deliver to the Owner a summary of all the final adjustments made to the gas turbines and auxiliary equipment.

The startup and commissioning tests must be performed in strict accordance with the standard procedures of the original manufacturer of the gas turbine generators.

The Contractor, prior to testing of the equipment should provide a work plan that includes technical expertise, equipment for measuring and recording data, test protocol and acceptance parameters.  The parameters should include but not limited to:  vibration, operating temperatures and pressures, fuel consumption, voltage & power output, electrical insulation, etc.  The Contractor must also have personnel available to make adjustments and corrections during testing.

The Contractor shall perform performance tests in accordance with the manufacturer’s specifications to record power and heat rate utilizing liquid fuel.

The Contractor shall deliver to the Owner the following reports not limited to:

Approved test protocols

Data sheets summarizing all equipment tested and calibrations

Vibration reports for all rotating equipment greater than 10 HP.

Noise level data

Performance test reports

2.9.10  Supply of Consumables for Initial Operation

The Contractor shall supply a recommended critical spare parts list for ENELVEN to select from which will includes at least the following:

Forty (40) sets of liquid fuel filters

Two (2) sets of liquid fuel nozzle parts

Six (6) sets of liquid fuel nozzle gaskets

Two (2) sets of liquid fuel check valves

Two (2) liquid fuel control servo-valves

Two (2) flame detectors

Four (4) igniters

Four (4) igniter cables

One (1) set of combustion air filters

One (1) set of generator air filters

One (1) control system power supply

Two (2) control system discrete input cards

Two (2) control system digital output cards

Two (2) control system thermocouple cards