| CLIENT: | BIE REF. / REPORT No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bariven S.A. c/o PDVSA Services BV President Kennedylaan 19 2517 JK The Hague The Netherlands | 4519C.02 |  |  |  |  |  |  |  |  |  |  | PAGE 1 OF 3 |  |  |  |  |  |  |
|  | CLIENT P.O. No.: |  |  |  | VISIT No.: |  |  |  |  |  |  | NEXT SCHED. VISIT: |  |  |  |  |  |  |
|  | 5100077213 |  |  |  | RM-01 |  |  |  |  |  |  | TBA |  |  |  |  |  |  |
| VENDOR: | W.O. / REQ No.: |  |  |  | INSPECTOR: |  |  |  |  |  |  | BASE: |  |  |  |  |  |  |
| Derwick Associates MMG Tower Piso 16 Calle 53, Urb, Panama | 2232 |  |  |  | Ric Middleton |  |  |  |  |  |  | Houston, Texas |  |  |  |  |  |  |
|  | VENDOR REF. No.: |  |  |  | INSPECTION DATE(S): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 14 January 2010 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-VENDORS: |  | LOCATION: |  |  |  |  |  |  |  |  | SUB-VENDOR REF. No.: |  |  |  |  |  |  |  |
| Wood Group Pratt & Whitney |  | Sedalia, Missouri |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |
| SUB-SUB-VENDORS: |  | LOCATION: |  |  |  |  |  |  | SUB-SUB-VENDOR REF. No.: |  |  |  |  |  |  |  |  |  |
| Morris Export Services |  | Houston, Texas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CLIENT P.O. BRIEF MATERIAL DESCRIPTION: |  |  | I-1 | 5.5 |  | Hrs |  | I-3 | 2 | Hrs |  |  |  | I-4 | 116 KMS |  | I-5 | $0 |
| Turbo Generator Sets |  |  | INSPECTION AT: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Sub-Sub-Vendor (Morris Export Services) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-ORDER – BRIEF MATERIAL DESCRIPTION: |  |  | ORDER STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1-62500 KVA, 3000A, 12000V, 60HZ Electric Generator EM |  |  | In Process |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| P.O. ITEM | P.O. QTY. | QTY ACC. | QTY REJ. | NARRATIVE | QP STAGE |
| --- | --- | --- | --- | --- | --- |
| 4 | 1 | 0 | 0 | 1-62500 KVA, 3000A, 12000V, 60HZ Electric Generator with Brushless Excitation EM Serial Number 173228201 |  |

INSPECTION VISIT OF 14 JANUARY 2010: SUMMARY: The following personnel were in attendance at Morris Export Crating for today’s inspection: Thomas Moran – Marketing Manager – Wood Group Pratt & Whitney Tom Young – Director, International Services – UTC Overseas Inc. Ricardo Middleton – TPI – Representing PDVSA BV The generator was previously reported to be from PG&E’s Hunter Point Station in California where it was used for a total of 4800 hours since installation in the mid 1970’s. The service was reported to be only peaking and over 50% of the run hours were attributed to periodic testing for verification of readiness for service. The generator was reported to be the only generated installed at this single gas turbine plant. Visual inspection of the generator was performed to determine the condition of the equipment and to observe the results of painting of the external casing, which was performed after the previous initial inspection. The condition of the unit was “as witnessed” during the previous inspection and the painting was performed in a workman-like fashion, to the satisfaction of the inspector. Heaters were installed and in operation to maintain the temperature of the generator. The generator casting was warm to the touch. Fiberglass insulation was applied over ventilation openings to prevent the entrance of dust into the generator casing.

Internal wiring for controls and metering, internal fans, auxiliary lighting, piping for internal lube oil, and main conductors were all brought out and accessible from outside of the generator and the exciter.

SPECIFICATIONS AND DRAWINGS:

Generator specifications were not provided with exception to information available on the Nameplate. No additional specifications were made available.

MATERIALS:

One – 3-phase, 62500 KVA, 12,000V, 3000A, 60HZ Electric Generator with Brushless Excitation with externally accessible connections.

EM Manufacturing Company Serial No. 173228201

VISUAL AND DIMENSIONAL EXAMINATION:

No dimensional specifications were made available.

FUNCTIONAL AND PERFORMANCE TESTS:

No testing of the units was performed during the inspection.

Inspector cannot comment on operability of this generator.

MARKING AND PACKING:

The unit was not prepared for shipping and no shipping marks were noted.

DOCUMENTATION:

Inspection Report by Leppert-Nutmeg Inc., dated 19th February 2009, for Twin Pak Generator was reviewed and endorsed as such.

The report included a narrative of inspection, repair and testing activity.  Failure during initial “high voltage” testing of the generator was referred to the 12 o’clock position on the stator where insulation damage was visually observed and repaired, but was not referred to a particular phase. The test report indicated that a High Potential Test was not performed.

INSPECTION RELEASE / NON-CONFORMANCE NOTE:

The equipment is acceptable as described and as inspected.  The equipment can be released when authorized by the client.

ATTACHMENTS:

Digital Photographs

Inspection Report for Twin Pak Generator (With Digital photographs) (Repair Contractor)

EM Generator Exciter End                          EM Generator Non-Exciter End

Unit Name Plate                                    Unit Serial Numbers

- END OF REPORT -