EDC Margarita Island 2x7EA Gas Turbine Scope of Work

Performance of TIL 1346 – 7EA Stage 17 Rotating Compressor Blades

Based on GE TIL 1346, the replacement of the 17th stage rotating blades is not required until the first major inspection and at each subsequent major inspection (if water injection is utilized). Therefore ProEnergy does not recommend replacement of the 17th stage rotating blades prior to putting the unit into service.

However, the cost to replace the 17th stage rotating blades is $278,000.00 per unit. This price includes labor, supervision, technical direction, tools and equipment, and consumables to perform the work. This price is based on the assumption that the blades will be replaced without removing the rotor from the unit.

The price above does not include a set of 17th stage rotating blades. A new set of replacement 17th stage rotating blades (403CB alloy, uncoated) can be purchased from ProEnergy for $50,000.00 plus shipping and import duties. This set of compressor blades is equivalent to GE Part Number 199E7421P001 and will fulfill the requirement of TIL 1346.

Commissioning of the 7EA gas turbine generator, auxiliaries, and Balance of Plant Equipment

Below are the rates for management and technical specialists to commission and start up the 2 x 7EA gas turbine power plant in Margarita Island, Venezuela. This scope includes all systems of the the turbine generator, auxiliary equipment, balance of plant equipment and systems including fuel, water, air, fire protection, waste oil / water, and control systems. The duration required to commission and start up 2 x 7EA dual fuel gas turbine generators and standard BOP equipment is approximately 18 weeks and includes office preparation and overlap with construction activities. The scope of work includes filling and flushing systems; lubricating and testing pumps, fans, and motors; check out and testing of electrical systems; calibration and verification of instrumentation; operational and functional checks;  and operating, testing, and turn over of each system of the plant. This budgetary estimate also includes two weeks of operator training and all the documentation and data for equipment commissioning and testing.

The number of personnel can be reduced or increased based on the scope of work to be performed and time allotted for start-up. However the personnel below is representative of a standard commissioning and start-up team.

Position						Rate

Start-Up Manager (1)					90.00 / hr

BOP Electrical Commissioning Engineer (1)		80.00 / hr

BOP Electrical Commissioning Tech (2)			73.00 / hr

BOP Mechanical Commissioning Engineer (1)		75.00 / hr

BOP Mechanical Commissioning Tech (2)		68.00 / hr

Gas Turbine Controls TA (2)				165.00 / hr

Gas Turbine Mechanical TA (1)				150.00 / hr

Gas Turbine Electrical & Generator TA (1)		165.00 / hr

I&E Technician (2)					73.00 / hr

Turn over Coordinator (1)				68.00 / hr

DCS Engineer (1)					90.00 / hr

DCS Tech (1)						75.00 / hr

Man-hour estimates are included in the budget estimate.

Budgetary Estimate

Assumptions:

- Quote is a budgetary estimate is +/- 20% because the details of the plant are not known.

- Operators and shift supervisors to be provided by plant owner or by ProEnergy at T&M rates

- Gas Turbines are dual fuel (gas and #2 diesel)

- Craftsmen supplied by installation contractor or by ProEnergy at T&M rates

Insert Budget estimate breakdown.

Mark V Control System Uprate

ProEnergy has evaluated the Mark VI –E upgrade proposed for the Margaritia units. ProEnergy believes that this PLC distributed type system requires increased maintenance than would a Mark VI or equivalent control system. ProEnergy base this on history of the system and the fact that they the PLC’s utilized with the Mark VI-E are placed in environments (hot, dirty, and oily) that cause early failure. The PLC’s in the system are redundant but fail more frequently than expected. Failure of these PLC’s would temporarily cause the system to lose redundancy. Therefore ProEnergy recommend a traditional Mark VI or equivalent type system to control the gas turbine generator. If required, this control system can also control balance of plant equipment.

ProEnergy propose to build a Mark VI equivalent control system with an Allen Bradley platform. The price to supply this system is $XXX,XXX per unit. This price does not include shipping or customs fees.

The control system will be implemented at the site during the installation of the turbine generator. Additional costs for implementation will be minimal if ProEnergy perform the start-up and commissioning of the unit. Also, the dual fuel modification software and I/O will be included with the system.

If the customer is interested, the new control system can be built to include BOP system controls. Therefore eliminating the need for a DCS system.

Spare Parts for the 7EA Dual Fuel Conversion

The spare parts quoted below include recommended spare parts for the systems added for the Dual Fuel Conversion. The type and quantity of spare parts was based on having assemblies to change out quickly while the defective components are being repaired. For example a spare fuel oil pump and minor repair kit is recommended to keep in stock.

The spare parts for the Turbine Control System cannot be determined until the control system is determined.  However a budgetary estimate for these spares is $100,000.00.

| Liquid Fuel system |  | Qty | Price | Extended |
| --- | --- | --- | --- | --- |
|  | Fuel Filters (accessory base) | 24 | $112 | $2,679.60 |
|  | Main Fuel Pump | 1 | $95,219 | $95,218.60 |
|  | Main Fuel Pump (minor repair kit) | 1 | $8,036 | $8,035.90 |
|  | Flow Divider | 1 | $25,155 | $25,154.60 |
|  | Isolation Valve | 1 | $63,008 | $63,008.30 |
|  | Liquid Fuel Check Valve | 10 | $503 | $5,031.50 |
|  | Gauge Panel - Pressure switch | 2 | $1,015 | $2,030.00 |
|  | Pressure Switch | 1 | $964 | $964.25 |
|  | Gauge Panel – Gauge | 1 | $429 | $429.20 |
|  | Parker Valve | 1 | $1,399 | $1,399.05 |
|  | Pump Clutch | 1 | $14,645 | $14,645.00 |
| Water injection system |  |  |  |  |
|  | Water Injection Filters | 12 | $154 | $1,844.40 |
|  | Injection pump / motor assy | 1 | $24,418 | $24,417.64 |
|  | Water Injection Check Valve | 10 | $641 | $6,409.00 |
|  | Water Injection Stop Valve | 1 | $3,058 | $3,057.76 |
|  | Variable Frequency Drive | 1 | $6,569 | $6,568.50 |
| Atomizing Air System |  |  |  |  |
|  | Air Filter | 4 | $279 | $1,117.66 |
|  | Booster Compressor | 1 | $13,472 | $13,471.95 |
|  | Booster Compressor – Motor | 1 | $2,373 | $2,372.85 |
|  | Booster Compressor – Belt | 2 | $92 | $184.50 |
|  | Main Atomizing Air Compressor | 1 | $41,498 | $41,497.55 |
|  | Main Atomizing Air Compressor - Quill Shaft | 1 | $1,740 | $1,740.00 |
| Purge Air System |  |  |  |  |
|  | 3-way purge valve assy | 10 | $10,083 | $100,833.00 |
|  | Red Hat Solenoid Valve | 4 | $1,372 | $5,489.70 |
|  | Pressure transducer - Purge protection panel | 1 | $2,926 | $2,926.10 |
| Combustion System |  |  |  |  |
|  | Primary Fuel Nozzles | 10 | $56,534 | $565,340.50 |
|  | Secondary Fuel Nozzles | 10 | $21,598 | $215,977.50 |

These prices do not include shipping or customs fees.