Bases de Diseño de Sistema de Conversion Dual
AGM-02-0204-ESP-P-0004
409-2956-DFM-BASE

| Rev. | Fecha | Breve Descripción del Cambio | Total Pág. | Elab. por INELMECA | Rev. por INELMECA | Aprob. por EL CLIENTE |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 27/06/2011 | EMISIÓN FINAL | 27 | XX | XX | J.M.T. |
| A | 07/04/2011 | EMISIÓN PARA COMENTARIOS DE EL CLIENTE | 20 | XX | XX | J.M.T. |

CONTENIDO

INTRODUCTION	4

1.	PURPOSE	5

2.	SCOPE	5

3.	LOCATION	5

3.1.	Área y ubicación	6

4.	REFERENCES	7

5.	ENVIRONMENTAL AND METEOROLOGICAL CONDITIONS	8

6.	CODES AND STANDARDS	9

7.	DUAL FUEL MODIFICATION GENERAL ASPECTS	9

8.	MODIFICATION OF EXISTING TURBINE SYSTEMS	10

9.	Additional turbine SYSTEMS REQUIRED	10

10.	ADDITIONAL BALANCE OF PLANT REQUIRED	10

11.	PROCESS DESIGN BASIS:	11

11.1.	GENERAL	11

11.2.	SPECIFIC PROCESS DESIGN BASIS	11

11.2.1.	MODIFICATION OF EXISTING Turbine SYSTEMS	11

11.2.2.	Additional turbine SYSTEMS REQUIRED	13

11.2.3.	ADDITIONAL BALANCE OF PLANT REQUIRED	14

12.	general features for dual modifications package´s major equipments and skids	16

12.1.	Demineralized Water Forwarding skid	16

12.2.	Water Injection System skid	17

12.3.	Liquid Fuel Forwarding System	18

12.4.	Liquid Fuel Management Spool	19

13.	design consideration	20

13.1.	Electrical Systems	20

13.2.	Mechanical Scope	23

13.3.	Civil Interface	23

13.4.	Instrumentation	24

13.5.	ENVIRONMENTAL ASPECTS	24

14.	SYSTEMS INTEGRATION AND INTERCONECTION POINTS	25

15.	TITULO GENERAL 1	25

15.1.	TITULO GENERAL 2	26

15.1.1.	TITULO GENERAL 3	26

ANEXO 1.-	TITULO ANEXO 1	27

INTRODUCTION

Derwick has developed a Dual Fuel Modification Package to be installed on GE 7EA Gas Turbines originally built by the OEM with “Gas Only” configuration. This modification, when applied to a “Gas Only” unit, will allow it to start and operate on natural gas or No 2 distillate fuel.  The Dual Fuel Modification Package was developed through evaluations of several existing GE 7EA dual fuel units. Derwick developed systems for this package that provide similar functionality and are comprised of equipment that has been proven in the same application.

Derwick has developed these systems to fit into the existing turbine and accessory packages so that they will not interfere with existing equipment or future modifications. Derwick has performed engineering evaluations for new equipment that have not been proven in this application.

Derwick used industry standards and general practices to fabricate and assemble equipment for the dual fuel modification. A list of codes and standards utilized on the project are defined below in the text.

EDC has supplied drawings and documentation to Derwick specifically for the units that will be modified. These documents included all drawings, specifications, and documentation for the equipment that was issued by the Original Equipment Manufacturer (OEM) and their sub vendors.  These drawings were evaluated and modified to reflect the duel fuel modification that will be applied to the units.

The turbine unit serial numbers that will be modified to dual fuel are 298034 and 298035 manufactured by General Electric.

A detailed project scope for the work has been defined; refer to drawing AGM-02-0204-MED-G-0002, Functional Description.

- PURPOSE

The purpose of this document is to establish the design basis for the modification of two GE MS 7001EA gas turbines from a “gas only” configuration to dual fuel (gas and No. 2 distillate). The modification will include a water injection system for NOx abatement while the unit is operating on distillate fuel.

- SCOPE

This document covers the basis for design, assumptions made, and standards used to develop, fabricate and install the modification.

- LOCATION

La Planta de Generación Juan Bautista Arismendi estará ubicada en la zona de El Guamache, municipio Tubores (ver Figura 1 y Figura 2), al lado oeste de la planta de Distribución de combustible El Guamache de PDVSA.

Figura 1. Ubicación de la Nueva Planta de Generación Juan Bautista Arismendi

Fig. 2. Parcela de Ubicación de Nueva Planta de Generación Juan Bautista Arismendi

  - Área y ubicación

La parcela ocupará un área aproximada de 50 hectáreas, la cual forma un polígono de cuatro (04) lados, definidos por los siguientes puntos de coordenadas UTM - REGVEN:

|  | Vértices de Linderos |  |
| --- | --- | --- |
| Punto | Norte | Este |
| 220A | 1.203.129,416 | 386.707,723 |
| 220B | 1.203.060,674 | 387.201,966 |
| 221A | 1.202.267,719 | 387.261,708 |
| 221B | 1.202.232,067 | 386.775,330 |

Elevación Sobre El Nivel Del Mar (m.s.n.m.):	5 m.

- REFERENCES

The drawings and documents used as references to develop and support the technical content of this document are:

| AGM-02-0204-MED-G-0002 | Functional Description |
| --- | --- |
| AGM-02-0204-PLA-G-0057 | Plot Plan |
| AGM-02-0204-PLA-P-0009 | Process Flow Diagram |
| AGM-02-0204-FOP-P-0002 | POF Description System Ops. |
| AGM-02-0204-PLA-G-0060 | Flow and Process Specifications |
| AGM-02-0204-ESP-P-0055 | Liquid Fuel Specification for GE Industrial Turbines |
| AGM-02-0204-ESP-P-0056 | Water Specification for GE Industrial Turbines |

- ENVIRONMENTAL AND METEOROLOGICAL CONDITIONS

On table 1, are shown parameters and values related to environmental and meteorological conditions used at reference for the selected site at Margarita Island.

Tabla 1: Condiciones Ambientales del Área de Influencia del Proyecto

| Parámetro | Valor |
| --- | --- |
| Temperatura media: | 27,0 ºC |
| Temperatura máxima: | 36,5 ºC |
| Temperatura mínima: | 22,5 ºC |
| Punto de rocío medio: | 18,0 ºC |
| Presión atmosférica media a nivel del mar: | 1,013 bar |
| Pluviosidad media anual: | 399 mm |
| Pluviosidad anual Península de Macanao: | 300-500 mm |
| Humedad relativa media: | 74 % |
| Velocidad media del viento: | 13,9 km/h |
| Velocidad máxima sostenida del viento: | 99,0 km/h |
| Dirección predominante de viento: | E - NE |

- CODES and STANDARDS

The codes and standards listed below will be used during the design, fabrication and or installation of the dual fuel modification.

| Codes and Standards |  |
| --- | --- |
| IEEE | Institue of Electrical and Electronic Engineers |
| UL | Underwriters Labratories (electrical components) |
| ASME | American Society of Mecanical Engineers – B31.1 (piping fabrication) |
| NEC | National Electric Code |
| NEMA | National Electrical Manufacturer’s Association |
| ANSI | American National Standards Institute |

- DUAL FUEL MODIFICATION GENERAL ASPECTS:

The Dual Modification Package can be broken out into three sections:

- Modification of existing Turbine systems.

- Additional systems that will be added to the Turbine.

- Additional balance of plant equipment that will need to be support for dual fuel operations.

Each one of these sections will be described below.

- MODIFICATION OF EXISTING Turbine SYSTEMS

The GE MS 7001EA that will be installed and modified for dual fuel were built by the Original Equipment Manufacturer (OEM) configured as “Gas Only” with DLN1 Technology.

Below is a list of existing systems on the Turbine Generator that will be modified to incorporate the dual fuel modification.

- Lube oil system

- Hydraulic Oil System

- Trip Oil System

- Cooling Water System

- Cooling and Sealing Air System

- Gas Fuel System (Skid)

- Combustion System

- Turbine Control System

- Additional TURBINE SYSTEMS REQUIRED

Additional systems will be required to provide the dual fuel capability to the generation unit

Below is a list of new systems that will be added to the turbine generator to configure the unit for dual fuel operation.

- Liquid Fuel System

- Atomizing Air System

- Purge Air System

- Water Injection System

- ADDITIONAL BALANCE OF PLANT REQUIRED

The Dual Fuel Modification Package will also require that new equipment be added to the balance of plant to support the unit for dual fuel operation.

The additional equipment required and its function will be mentioned as follows:

- Demineralized Water Forwarding Skid (near demineralized water storage tank)

- Water Injection System Skid (near to unit)

- Liquid Fuel Forwarding System Skid (near treated No 2 distillate storage tank)

- Liquid Fuel Management Spool (near to unit)

The new equipment added, basic process conditions, and flow streams are shown on the drawing AGM-02-0204-PLA-P-0009 Process Flow Diagram.

- PROCESS DESIGN BASIS:

  - GENERAL

The dual fuel modification package was developed through evaluations of several existing GE 7EA dual fuel units. Derwick developed systems for this package that provide similar functionality and are comprised of equipment that has been proven in the same application. For these cases, no engineering calculations will be provided.

Derwick has developed and / or modified these systems to fit into the existing turbine and accessory packages so that they will not interfere with existing equipment or future modifications.

Derwick has performed engineering evaluations for new equipment that have not been proven in this application. Derwick used industry standards and general practices to fabricate and assemble equipment for the dual fuel modification. A list of codes and standards utilized on the project are defined below in the text.

  - SPECIFIC PROCESS DESIGN BASIS

The process design basis, premises and assumptions used to perform the engineering design for the Dual Fuel Modification Package was established as follows and using the same package´s breakdown mentioned before.

    - MODIFICATION OF EXISTING TURBINE SYSTEMS

Below is a list of existing systems on the Turbine Generator that will be modified to incorporate the dual fuel modification. The referenced drawing is the revised one that include the aspects and details of the dual fuel modification.

- Lube oil system  – Refer to Drawing AGM-02-0204-PLA-P-0061 Lube Oil P&ID. (DTI Aceite de Lubricación).

- Hydraulic Oil System  (no change to original drawing issued for unit).

- Trip Oil System – Refer to Drawing AGM-02-0204-PLA-P-0050 Trip Oil P&ID (DTI Aceite de Disparo).

- Cooling Water System – Refer to Drawing AGM-02-0204-PLA-P-0051 Cooling Water P&ID (DTI Agua de enfriamiento).

- Cooling and Sealing Air System – Refer to Drawing AGM-02-0204-PLA-P-0049 Cooling and Sealing Air P&ID (DTI Aire de Enfriamiento y Sellado).

- Gas Fuel System (Skid) – Refer to Drawing AGM-02-0204-PLA-P-0052 Fuel Gas P&ID ( DTI Gas Combustible).

- Combustion System – Refer to Drawing AGM-02-0204-PLA-M-0013 & -0009 Dual Fuel Nozzle Assembly – Secondary and Dual Fuel Nozzle Assembly – Primary (Ensamblaje de Boquillas de Combustible Dual - Secundarias y  Ensamblaje de Boquillas de Combustible Dual – Primarias).

- Turbine Control System – Refer to Drawing AGM-02-0204-PLA-I-0003 Control System Modifications (Modificaciones Sistema de Control).

      - combustion system

The combustion system will require modification to accommodate dual fuel capabilities and water injection (NOx abatement method) when liquid fuel is used for combustion.

The modified fuel nozzles will be modified and then tested to the following specification. These specifications were developed by DERWICK specifically from original Dual Fuel Nozzles:

Table 1: Flow Specifications for Primary Fuel Nozzles (End Covers)

|  | Atomizing Air (in2) (see note 1) | Gas Fuel (in2) (see note 1) | Water (lbs/hr) (see note 2) | Liquid Fuel (lbs/hr) (see note 2) |
| --- | --- | --- | --- | --- |
| Maximum | 0.1224 | 0.3468 | 4549.2 | 1847.22 |
| Nominal | 0.1200 | 0.3400 | 4460.0 | 1811.00 |
| Minimum | 0.1176 | 0.3332 | 4370.8 | 1774.78 |

Table 2: Flow Specifications for Secondary Fuel Nozzles

|  | Secondary Gas (in2) (see note 1) | Tertiary Gas (in2) (see note 1) | Water (lbs/hr) (see note 2) | Liquid Fuel (lbs/hr) (see note 2) |
| --- | --- | --- | --- | --- |
| Maximum | 0.1520 | 0.2805 | 1592.0 | 1747.0 |
| Nominal | 0.1490 | 0.2750 | 1561.0 | 1713.0 |
| Minimum | 0.1460 | 0.2695 | 1530.0 | 1679.0 |

Note 1) Flow test performed with fluid at 1.25PR

Note 2) Flow test performed with fluid at 100 psig

    - Additional Turbine SYSTEMS REQUIRED

Below is a list of additional systems that will added to the turbine generator to configure the unit for dual fuel operation.

- Liquid Fuel System  – Refer to Drawing AGM-02-0204-PLA-P-0048 Liquid Fuel System P&ID (DTI Sistema de Combustible Líquido).

- Atomizing Air System – Refer to Drawing AGM-02-0204-PLA-P-0053 Atomizing Air P&ID (DTI Atomización de Aire).

- Purge Air System – Refer to Drawing AGM-02-0204-PLA-P-0054 Fuel Purge P&ID (DTI Purga de Combustible).

- Water Injection System – Refer to Drawing AGM-02-0204-PLA-P-0047 Demin Water Forwarding / Injection System.(Suministro e Inyección de Agua Desmineralizada).

    - ADDITIONAL BALANCE OF PLANT REQUIRED

The process design basis for the new equipment required for Dual Fuel Modification Package has been stated as follows:

- Demineralized Water Forwarding Skid

- Water Injection Skid

- Liquid Fuel Forwarding Skid

- Liquid Fuel Management Spool

      - demineralized water forwarding skid

The demineralized water forwarding skid will forward demineralized water from the treated demineralized water tank to the water injection skid adjacent to the turbine generator. The demineralized water provided should meet or exceed the specifications recommended by the OEM. This specification is included in Reference Drawing AGM-02-0204-ESP-P-0056.

The process conditions, refer to drawing AGM-02-0204-PLA-P-0009. The pump and flow elements were engineered based on piping and plant information.

The skid is designed with a back pressure regulating valve that will maintain a specific pressure on the feed line to the water injection skid if the above process conditions are met. This will be achieved by returning any additional water back to the storage tank. As water flow to the water injection skid increases, the flow in the return line to the tank will decrease.

The flow streams, equipment set up and basic process flow conditions are shown on the drawing AGM-02-0204-PLA-P-0009 Diagrama de Flujo de Procesos. The piping and instrument drawing (P&ID) AGM-02-0204-PLA-P-0047 DTI Suministro e inyección de agua desmineralizada will show the control and automation required to make this system work properly.

The control philosophy and operation for the demineralized water forwarding and injection system will be stated on the document  AGM-02-0204-FOP-P-0002 Filosofía de Operación y Control.

The technical requirement, specifications, sizing and selection of the pumps to be installed in the skid are described on documents  AGM-02-0204-ESP-0001 Especificaciones técnicas – Patín de Suminstro de Agua Desmineralizada, AGM-02-0204-HDE-G-0001 Hojas de Datos de Equipos e Instrumentos y AGM-02-0204-CAL-M-0001 Memoria de Cálculo para Mecánica y Procesos.

      - Water Injection System Skid

The water injection skid will receive demineralized water from the demineralized water forwarding pumps. This skid will boost the water pressure, final filter the water, and control water flow to the fuel nozzles on the turbine base. The water flow rate is controlled by a variable speed drive controller connected to the motor with flow meter feedback signals. The turbine control system contains the software which calculates an output signal to the variable speed drive controller based on feedback from the water flow meter.

To obtain demineralized water injection at the combustion chamber for NOx abatement, the process conditions on drawing AGM-02-0204-PLA-P-0009 Flow and Process, must be met.

      - Liquid Fuel Forwarding System Skid

The liquid fuel forwarding skid will forward Liquid Fuel from the treated fuel tank to the fuel metering spool adjacent to the turbine generator.

The process conditions at the treated liquid fuel tank outlet required for the pump suction and the discharge parameters to the liquid fuel metering spool adjacent to the turbine generator are shown on drawing AGM-02-0204-PLA-P-0009, Flow and Process.

The liquid fuel forwarding skid is designed with a back pressure regulating valve that will maintain a specific pressure on the feed line to the Liquid Fuel Management Spool by returning Liquid Fuel to the storage tank. As the flow to the turbine increases, the flow in the bypass to the tank will decrease.

The flow streams, flow control equipment, and basic process flow conditions are shown on the drawing AGM-02-0204-PLA-P-0009 Diagrama de Flujo de Procesos. The piping and instrument drawing (P&ID) AGM-02-0204-PLA-P-0048 DTI Suministro de Combustible Líquido will show the control and automation required to make this system work properly.

The control philosophy and operation for the liquid fuel forwarding system will be stated on the document AGM-02-0204-FOP-P-0002 Filosofía de Operación y Control.

The technical requirement, specifications, sizing and selection of the pumps to be installed in the skid are described on documents  AGM-02-0204-ESP-0002 Especificaciones técnicas – Patín de Suministro de Agua Desmineralizada, AGM-02-0204-HDE-G-0001 Hojas de Datos de Equipos e Instrumentos y AGM-02-0204-CAL-M-0001 Memoria de Cálculo para Mecánica y Procesos.

      - Liquid Fuel Management Spool

The liquid fuel management spool will provide secondary protection for the turbine, secondary pressure control, and primary fuel flow metering.

The process conditions and parameters required at the liquid fuel management spool input to accomplish proper liquid fuel pressure, flow and temperature conditions at the turbine generator are shown on drawing AGM-02-0204-PLA-P-0009, Flow and Process.

The flow streams, control equipment, and basic process flow conditions are shown on the drawing AGM-02-0204-PLA-P-0009 Diagrama de Flujo de Procesos. The piping and instrument drawing (P&ID) AGM-02-0204-PLA-P-0048 DTI Sistema de Combustible Líquido will show the control and automation required to make this system work properly.

The control philosophy and operation for the Liquid Fuel Management Spool system will be stated on the document  AGM-02-0204-FOP-P-0002 Filosofía de Operación y Control.

The technical requirement, specifications, sizing and selection of instruments, devices to be installed in the Liquid Fuel Management Spool are described on documents  AGM-02-0204-HDE-G-0001 Hojas de Datos de Equipos e Instrumentos and AGM-02-0204-CAL-M-0001 Memoria de Cálculo para Mecánica y Procesos.

- general features for dual modifications package´s major equipments and skids

  - Demineralized Water Forwarding skid

This skid will forward demineralized water from the treated demineralized water tank to the water injection skid adjacent to the turbine generator.

The skid will have the following features:

- Two 100% pump and motor sets

- Back pressure regulating valve that will maintain a specific pressure on the feed line to the water injection skid by returning water back to the storage tank

- Pressure transmitter on the output header that will provide a trigger for the second pump to start when the pressure drops below a specified level.

- NEMA 4 rated junction boxes, conduit, and instrumentation

- Separate Termination Boxes for power supply to the motors and for skid instrumentation

- Skid base painted with epoxy “shark grip” paint to protect the surface from aggressive demineralized water and to make the base slip proof

- Butterfly valves on both sides of the pump in order to isolate it from the system

- Ball valve at the inlet to the skid for a positive shut off

- Pump and motor sets manufactured by Flow Serve

- Power supply to motors terminated in NEMA 4 junction box for interconnection to cables from customer supplied MCC.

- Instrumentation terminated in NEMA 4 junction box for interconnection to cables to control system

- Gauge Panel for local pressure indication

- Open skid design with 1” containment around base and drain to capture liquids

Reference Drawings:

- Assembly Drawing – Demin Water Forwarding: 	AGM-02-0204-PLA-M-0037

- General Arrangement – Demin Water Forwarding:	AGM-02-0204-PLA-M-0038

- Electrical – Demin Water Forwarding:		AGM-02-0204-PLA-E-0040

- Interconnection Points: 				AGM-02-0204-ESP-G-0061

  - Water Injection System skid

This skid will receive demineralized water from the demineralized water forwarding pumps. The skids will boost the water pressure, final filter it, control flow to the fuel nozzles on the turbine base.

The skid will have the following features:

- Enclosed climate controlled skid with acoustically insulated interior

- High pressure multi-stage centrifugal pump with variable speed drive

- High pressure duplex filter with transfer valve

- Solenoid stop valve on high pressure side of the pump that is controlled by the gas turbine control system

- Ball valves on inlet and exit of skid for positive shut off

- Flow meter for feedback to turbine control system

- Skid floor is painted with epoxy “shark grip” paint to protect the surface from aggressive demineralized water and to make the base slip proof

- Skid base has a two drains to collect liquid

- Pressure transmitters for feedback to turbine control system

- Step down transformer for 480/220/110 supply for skid

- Interior lights and electrical outlet

- NEMA 4 rated enclosures and conduit

Reference Drawings:

- Mechanical – Water Injection: 			AGM-02-0204-PLA-M-0044

- General Arrangement – Water Injection:		AGM-02-0204-PLA-M-0041

- Electrical – Water Injection:				AGM-02-0204-PLA-E-0043

- Interconnection Points: 				AGM-02-0204-ESP-G-0061

  - Liquid Fuel Forwarding System

This skid will forward Liquid Fuel from the treated fuel tank to the fuel metering spool adjacent to the turbine generator.

The skid will have the following features:

- Two 100% pump and motor sets

- Back pressure regulating valve that will maintain a specific pressure on the feed line to the water injection skid by returning water back to the storage tank

- Pressure transmitter on the output header that will provide a trigger for the second pump to start when the pressure drops below a specified level.

- NEMA 4 rated junction boxes, conduit, and instrumentation

- Separate Termination Boxes for power supply to the motors and for skid instrumentation

- Skid base painted with epoxy “shark grip” paint to protect the surface from aggressive demineralized water and to make the base slip proof

- “Fire Safe” butterfly valves on both sides of the pump in order to isolate it from the system

- “Fire Safe” Ball valve at the inlet to the skid for a positive shut off

- Pump and motor sets manufactured by Flow Serve

- Power supply to motors terminated in NEMA 4 junction box for interconnection to cables from MCC.

- Instrumentation terminated in NEMA 4 junction box for interconnection to cables to control system

- Gauge Panel for local pressure indication

- Open skid design with 1” containment around base and drain to capture liquids

- Duplex strainer on suction header to the pumps

- Pump seals utilize API flush plan 11

Reference Drawings:

- Assembly – Liquid Fuel Forwarding: 		AGM-02-0204-PLA-M-0033

- General Arrangement – Liquid Fuel Forwarding:	AGM-02-0204-PLA-M-0034

- Electrical – Liquid Fuel Forwarding:			AGM-02-0204-PLA-E-0036

- Interconnection Points: 				AGM-02-0204-ESP-G-0061

  - Liquid Fuel Management Spool

The liquid fuel management spool will provide secondary protection for the turbine, secondary pressure control, and fuel flow metering.

Below are several features of this equipment.

- Liquid fuel solenoid stop valve with manual operator that is controlled by the turbine control system

- Positive displacement flow meter capable of 99.9% accuracy between 85-150 gpm with transmitter for feedback to turbine control system.

- Pressure regulating valve

- “Fire Safe” butterfly valves to isolate the flow meter and bypass flow

Reference Drawings:

- Fuel Management Spool Mechanical Arrangement:	AGM-02-0204-PLA-M-0075

- design consideration

  - Electrical Systems

The electrical scope of work on the dual fuel project is relatively small. The only electrical modification to the unit is the addition of an atomizing air booster compressor motor breaker / starter. Because there are no spares available in the PECC, Derwick will supply a breaker / starter that will be installed in the PECC. The design calculations for this breaker will be provided in the electrical calculations document (reference drawing AGM-02-0204-MED-E-0001). The breaker / starter for the atomizing air booster compressor motor will be controlled by the turbine control system. The software and the wiring to control the breaker will be part of Derwick’s scope of work.

For the fuel forwarding and demineralized water forwarding pump motors, breaker and breaker control hardware will need to be provided by the customer that will start and stop the motors as required. The software controls and contact inputs and outputs for these breakers will be provided in the turbine control system.

The fuel forwarding and demineralized water forwarding skids are equipped with a pressure switch on the outlet header of the pump that will close on a low pressure event. The signal from this pressure switch will be connected to the turbine control system. Control logic in the turbine control system will send a start signal to the MCC breaker for the standby pump motor to close.  In order for this scheme to work, the breakers / motor starters should be configured similar to the schematic below.

Figure 1:  Schematic for motor starters of liquid fuel and demineralized water forwarding pump motors

The breaker / breaker controls for the demineralized water forwarding and liquid fuel forwarding are

the responsibility of the customer. It is estimated that NEMA 2 size breakers will be sufficient for these applications, however customer to verify. Below in Figure 2 is a general schematic for the pump breaker power and controls circuits.

Figure 2: Power and Control Schematic for Forwarding Pump Skids (Demineralized Water and Distillate Fuel)

The Interconnection Wiring Drawing will outline all of the connections required for the dual fuel modification including electrical. Refer to Interconnection Point Drawing AGM-02-0204-PLA-G-0061.

The unit specific Cable List issued by GE for the unit will be modified to include the additional

cables required to implement the dual fuel modification. The Cable List Drawing will be issued as a Product of Engineering. (Refer to Drawing AGM-02-0204-PLA-E-0006)

The additional cables and wires will connect the field devices to the turbine control panel and other customer supplied equipment. The unit specific Interconnection Diagram and Turbine Connection Diagram issued by GE will be modified to include the additional field devices, connection points in the field, and the termination location in the control panel. The Interconnection Diagram and Turbine Connection Diagram will be issued as a Product of Engineering. (Refer to Drawing AGM-02-0204-PLA-E-0058 for the Revised Interconnection Diagram and AGM-02-0204-PLA-E-007 for the Revised Turbine Connection Diagram).

  - Mechanical Scope

Piping, tubing, valves, fittings, and equipment will be installed per industry standards and practices. The piping on all systems is fabricated per ASME B31.1. All welders performing welds on the piping and supports have current welding certifications that match the scope of work being performed.

Piping provided on for the modification have been cleaned and packaged for shipment. Prior to installation, the piping will be blown down to confirm no foreign material has contaminated the piping spools. After the piping has been fit up to the unit, all systems will be opened up and flushed to remove any contamination introduced during field fabrication.

The equipment will be installed per the vendor or manufactures literature. Rotating pumps and valves will be installed in a strain free condition. Pumps and motors will be aligned according to the vendor specifications for the pumps and coupling manufacturers. All installation details will be provided to the customer.

Seismic requirements were not considered during the development of the dual fuel modification package. This decision was made based on the equipment to be provided would be installed directly on the accessory and turbine base. The forwarding skids and water injection skids did not require such evaluation and were being installed on Customer provided foundations.

  - Civil Interface

The majority of the dual fuel modification will occur on the accessory and turbine bases. However there are several civil interfaces that need to be considered. The liquid fuel forwarding, demineralized water forwarding, and water injection skids will require foundations to be placed. The customer’s scope of work is to design and install these foundations.

The general arrangement drawings of the skids outline the skid dimensions, anchor bolt hole locations, and weights. The skids mentioned above will not experience any dynamic loads and can be anchored to the foundation with anchor bolts that are drilled and set in place with epoxy.

Reference Drawings:

Liquid Fuel Forwarding Skid		AGM-02-0204-PLA-M-0034

Demin Water Forwarding Skid	AGM-02-0204-PLA-M-0038

Water Injection Skid			AGM-02-0204-PLA-M-0041

  - Instrumentation AND CONTROLS

The Device Summary originally supplied with the unit has been modified to include devices added for the dual fuel modification.  The modified device summary (drawing AGM-02-0204-PLA-I-0046) has all of the devices identified with settings and specifications.

Additional junction boxes pull boxes, and conduit installed will be minimum of NEMA 4 rating. The conduit from the devices to junction boxes will be the rigid galvanized type. Flexible conduit and Seal Tite connections will be used at the device to tie into the rigid conduit. Several existing junction boxes on the turbine and accessory bases will be utilized.

Wire / cable utilized for the dual fuel modification will be to GE specifications and will have a minimum temperature rating of 90 deg C.

Several instruments that will be added on the accessory base will tie directly into existing conduit runs as per typical dual fuel units. Any additional conduit that will be installed will not interfere with existing equipment or future modifications. The cable installed will be per industry standards and terminated in existing junction boxes. The original equipment drawings will be modified to reflect the additional terminations and cables. Wires will be terminated using crimp style lugs and will be numbered according to interconnection drawings identified in the Engineering Products.

Instruments and devices will be calibrated during the pre commissioning phase and according to the Device Summary Drawing identified above.

An instrument gauge panel inside of the accessory package will be modified to include additional gauges and pressure switches associated with the dual fuel modification. Refer to Drawing AGM-02-0204-PLA-M-0024.

Modifications to the turbine control system will be implemented to support dual fuel operations similar to a standard GE 7EA turbine generator. These modifications will ensure that the turbine control system is comprehensive and will allow the unit to be started, synchronized, loaded, unloaded, shut down, with fuel transfer functions with integration to BOP and DCS systems as required. See AGM-02-0204-PLA-I-0003 Control System Modifications (Modificaciones Sistema de Control). Note: any integration systems (fiber optic) or hardwiring to be provided by customer.

  - ENVIRONMENTAL ASPECTS

There are several key interfaces associated with the dual fuel modification that provide protection for the environment. Below is a summary of these interfaces that should be considered for the plant design.

- The Fuel Forwarding Skids have an extended lip above the surface of the base and a base drain to capture any fuel leaks or spills. The base drain should be tied into the plant oily waste drain system to avoid any soil contamination

- The Demineralized Water Forwarding Skids also have skid containment with a base drain in order to capture demineralized water that can corrode carbon steel and concrete. The base drain should be tied into the plant waste water system.

- The Water Injection Skid is designed with a base drain and should also be tied into the plant waste water system.

- The False Start Drain System includes drains at three points on the turbine. These drains should be tied into the plant waste water and oily water system to capture waste water during water wash events, and to the oily waste drain for false fire events to capture waste fuel. (Refer to Drawing AGM-02-0204-PLA-M-0021).

- The accessory base has a fuel drain sump to capture any liquid fuel drained from points in the system including fuel filters, relief valve blow down, and low point drains. This drain sump should be tied into the plant waste oil system.

Specific locations of these drain points are identified on the skid general arrangement drawings and on the Package Piping Connection Drawing AGM-02-0204-PLA-M-0003 and -0004.

- SYSTEMS INTEGRATION AND INTERCONECTION POINTS

The Dual Fuel Modification Package will require specific integration or interconnection points with the generation unit systems itself, control system and PJBA Balance Of Plant.  Drawing AGM-02-0204-ESP-G-0061 Interconnection Points will provide a complete list of drawings for interface points.

- TITULO GENERAL 1

Texto GENERAL 1

- Caso 1

- Caso 2

- Caso 3

- Viñeta GENERAL 1

- Viñeta Indentada 1

- Viñeta Indentada 2

  - TITULO GENERAL 2

Texto GENERAL 1

- Caso 1

- Caso 2

- Caso 3

- Viñeta GENERAL 1

- Viñeta Indentada 1

- Viñeta Indentada 2

    - TITULO GENERAL 3

Texto GENERAL 1

- Caso 1

- Caso 2

- Caso 3

- Viñeta GENERAL 1

- Viñeta Indentada 1

- Viñeta Indentada 2

      - Titulo General 4

Texto GENERAL 1

- Caso 1

- Caso 2

- Caso 3

- Viñeta GENERAL 1

- Viñeta Indentada 1

- Viñeta Indentada 2

- TITULO ANEXO 1