Technical Specifications – Liquid Fuel Forwarding

Drawings and Schematics

P&ID:  AGM-02-0204-PLA-P-0035

Mechanical Outline Drawing:  AGM-02-0204-PLA-M-0034

Electrical Outline Drawing: AGM-02-0204-PLA-M-0036

Process Specifications:

Fluid – Distillate Fuel (see GE specification GEI-41047)

Fluid Specification:

|  | Skid Inlet |  | Skid Outlet |  |
| --- | --- | --- | --- | --- |
|  | Maximum | Minimum | Maximum | Minimum |
| Pressure (psig) | 25.0 | 0.5 | 150.0 | 55.0 |
| Temperature (deg F) | 150.0 | 40.0 | 150.0 | 40.0 |
| Flow (gpm) | 150.0 | 15.0 | 150.0 | 15.0 |

Electrical Control Center

| 480VAC, 3 phase, 60Hz | Pump Motors |
| --- | --- |
| 125 VDC | Instrument Switches |
| 24 VDC | 4-20 ma Flow and Pressure Transmitters |

Piping Specification

Manufactured to B31.1

Pump & Motor Specification

Two redundant (100%) ANSI pumps

Continuous Duty Motor

Other

- Open Skid

- Electrical NEMA 4 rated

- Non-hazardous rated

- Recirculation back to the tank via backpressure regulating valve

Calculations for Pump / Motor Specifications:

hL = f x L/D x V2

Where:

hL = Head loss (ft)

L = Length (ft)

D = Diameter

F = Friction Factor

V = Average Velocity (fps)

g = Acceleration of gravity (ft/sec2)

NR = (VDr)/m

Where:

NR = Reynolds Number

r = Density (lb / ft3)

m = Dynamic Viscosity (lb-sec/ft2)

RR = D/e

Where:

RR = Relative Roughness

e = Roughness

hfl = K * V2/2g

K = Friction coefficient

NPSHA = hatmo + hele – hf –hvap

hatmo = atmospheric head

hele =head due to elevation

hf = friction losses

hvap = vapor pressure of fluid

=Q = AV

Where:

Q = Flow rate (ft3/sec)

A= Average  cross sectional area (ft2)

Calculation of velocity in 4” suction assuming maximum flow rate:  150 gpm

(150 gpm  /  7.48 ft3/gpm)  =  [p x (4.03/12)2]/4 x V

V = 226.35 ft / min   or  3.77 ft / sec

2.436cp = 2.0895 x 10-5 [lb-sec/ft2/cp]	m=5.088-5 lb-sec/ft2

0.87 x 8.33 lb / gal x 7.48 gal/ft3 = 54.208 lb/ft3 OR 1.6848 slugs/ft3

Assuming liquid fuel specific gravity = 0.87

Reynolds Number Calculation:

NR = [3.77ft / sec x 4 in/12 x 1.6848 Slugs/ft3] /5.088 x 10-5 lb-sec/ft3

NR = 24,274

RR = (4/12)/1.5x10-4 = 2,222  Moody’s Diagram

Head Loss Calculation:

Moody’s friction factor for 4” schedule 40 carbon steel pipe f=0.023

hLf = 0.023 x [100 ft/(4/12)] x [(3.8 ft/sec)2 / (2 x 32.2 ft / sec2)]

hLf = 1.547 ft diesel / 100 ft   1.346 ft H20

Approximate pipe run = 260 feet

hLf = 260 ft/ 100ft  x 1.346 ft H20 / 100 ft = 3.5 ft H20

Losses in Fittings

K

(2)		4” Ball Valve			0.06 ea

(4)		4” reg 90 ell			0.225 ea

(1) 		4” nozzle at tank		0.5 ea

Total K = 1.52

hfl =1.52 * 3.832 ft/s / (2*32.2 ft/s2)

hLl = 0.346ft Diesel  0.301 ft H20

hL = hLf + hLl

hL = 3.5 ft H20  + 0.301 ft H20

hL = 3.8 ft H20

Liquid Fuel Forwarding – Skid Suction Losses

K

(1)		4” tee branch flow 			0.7

(1)		4” butterfly valve			1.5

(1)		4” 90 ell				0.3

(1)		3” butterfly valve			1.5

(1)		4”x3” reducer 				0.25

(1)		basket strainer				1.1

K= 5.35

hLl skid = 5.35 * 3.832 feet/sec / (2*32.2 ft/s2)

hLl skid = 1.22 ft Diesel   1.06 ft H20

NPSHA

Skid Elevation – 5.05m + Inlet elevation – 0.25m = 5.3m

Tank Elevation – 7.22m

Head due to elevation – 7.22m-5.3m = 1.92m  6.297 ft diesel  5.48 ft H20

NPSHA = 14.1 psia/.433psi/ft + 5.48 ft H20 – 4.86 ft H20 – 0.01psia/.433psi/ft

NPSHA = 33.16 ft H20

Calculation of velocity in 3” discharge assuming maximum flow rate:  150 gpm

(150 gpm  /  7.48 ft3/gpm)  =  [p x (3/12)2]/4 x V

V = 397.34 ft / min   or  6.62 ft / sec

2.436cp = 2.0895 x 10-5 [lb-sec/ft2/cp]	m=5.088-5 lb-sec/ft2

0.87 x 8.33 lb / gal x 7.48 gal/ft3 = 54.208 lb/ft3 OR 1.6848 slugs/ft3

Assuming liquid fuel specific gravity = 0.87

Reynolds Number Calculation:

NR = [6.62ft / sec x 3 in/12 x 1.6848 Slugs/ft3] /5.088 x 10-5 lb-sec/ft3

NR = 55,569

RR = (3/12)/1.5x10-4 = 1690  Moody’s Diagram

Head Loss Calculation:

Moody’s friction factor for 3” schedule 40 carbon steel pipe f=0.023

hLf = 0.023 x [100 ft/(3/12)] x [(6.62 ft/sec)2 / (2 x 32.2 ft / sec2)]

hLf = 6.26 ft diesel / 100 ft   5.45 ft H20

Approximate pipe run = 1260 feet

hLf = 260 ft/ 100ft  x 5.45 ft H20 / 100 ft = 68.67 ft H20

Losses in Fittings

K

(2)		3” Ball Valve			0.07 ea

(12)		3” reg 90 ell			0.35 ea

(1) 		2” check valve			2 ea

(1)		3” butterfly 			3 ea

(2) 		reducers			.05 ea

Total K = 9.44

hfl =9.44 * 6.622 ft/s / (2*32.2 ft/s2)

hLl = 0.642ft Diesel  0.585 ft H20

hL = hLf + hLl

hL = 68.67 ft H20  + 5.85 ft H20

hL = 74.25 ft H20

Calculation for total losses:

Turbine Elevation: 7.44M + .25m

Liquid Fuel Elevation:  5.3M

Difference in Elevation: 2.39M  7.839 ft diesel  6.82 ft H20

Pressure required at Unit: 70 psi

+ 161.66 ft H20 – Pressure at unit

+ 6.82 ft H20 - Elevation

+74.25 ft H20 – Friction losses

-33.16 ft H20 – NPSHA

Required differential – 209.57 ft H20  90.74psi

Design Pressure: 80.8 x 1.125 = 91 psi

Documentation from Pump / Motor Supplier