Technical Specifications – Liquid Fuel Forwarding

Drawings and Schematics

P&ID:  AGM-02-0204-PLA-P-0035

Mechanical Outline Drawing:  AGM-02-0204-PLA-M-0034

Electrical Outline Drawing: AGM-02-0204-PLA-M-0036

Process Specifications:

Fluid – Distillate Fuel (see GE specification GEI-41047)

Fluid Specification:

|  | Skid Inlet |  | Skid Outlet |  |
| --- | --- | --- | --- | --- |
|  | Maximum | Minimum | Maximum | Minimum |
| Pressure (psig) | 25.0 | 2.0 | 150.0 | 55.0 |
| Temperature (deg F) | 150.0 | 40.0 | 150.0 | 40.0 |
| Flow (gpm) | 150.0 | 15.0 | 150.0 | 15.0 |

Electrical Control Center

| 480VAC, 3 phase, 60Hz | Pump Motors |
| --- | --- |
| 125 VDC | Instrument Switches |
| 24 VDC | 4-20 ma Flow and Pressure Transmitters |

Piping Specification

Manufactured to B31.1

Pump & Motor Specification

Two redundant (100%) ANSI pumps

Continuous Duty Motor

Other

- Open Skid

- Electrical NEMA 4 rated

- Non-hazardous rated

- Recirculation back to the tank via backpressure regulating valve

Calculations for Pump / Motor Specifications:

hL = f x L/D x V2

Where:

hL = Head loss (ft)

L = Length (ft)

D = Diameter

F = Friction Factor

V = Average Velocity (fps)

g = Acceleration of gravity (ft/sec2)

NR = (VDr)/m

Where:

NR = Reynolds Number

r = Density (lb / ft3)

m = Dynamic Viscosity (lb-sec/ft2)

RR = D/e

Where:

RR = Relative Roughness

e = Roughness

Q = AV

Where:

Q = Flow rate (ft3/sec)

Calculation of velocity assuming maximum flow rate:  150 gpm

(150 gpm  /  7.48 ft3-sec/gpm)  =  [p x (4.03/12)2]/4 x V

V = 226.35 ft / min   or  3.77 ft / sec

2.436cp = 2.0895 x 10-5 [lb-sec/ft2/cp]	m=5.088-5 lb-sec/ft2

0.87 x 8.33 lb / gal x 7.48 gal/ft3 = 54.208 lb/ft3 OR 1.6848 slugs/ft3

Assuming liquid fuel specific gravity = 0.87

Reynolds Number Calculation:

NR = [3.77ft / sec x 4.03 in/12 x 1.6848 Slugs/ft3] /5.088 x 10-5 lb-sec/ft3

NR = 41,924

RR = (4/12)/1.5x10-4 = 2,222

Head Loss Calculation:

Moody’s friction factor for 4” schedule 40 carbon steel pipe f=0.023

hL = 0.023 x [100 ft/(4/12)] x [(3.77 ft/sec)2 / (2 x 32.2 ft / sec2)]

hL = 1.523 ft H2O / 100 ft

hL = .659 psi / 100 ft

Approximate pipe run = 1100 feet

1100 ft/ 100ft  x 0.659 psi / 100 ft = 7.25 psi

Pressure Drop for Twelve Pipe Elbows

5.9 ft x 12 = 70.8/100 x .659 psi/100 ft = 0.4665 psi

Calculation for total losses:

Turbine Elevation: 7.44M

Liquid Fuel Elevation:  5.3M

Difference in Elevation: 2.14M

2.14M x 3.28 ft/M x .433 psi/ft = 3.04 psi

Pressure required at Unit: 70 psi

+ 7.25 psi for piping losses

+ 0.47 psi for piping elbow losses

+3.04 psi for elevation losses

Minimum Pressure at forwarding pump outlet = 80.8 psi

Design Pressure: 80.8 x 1.125 = 91 psi

Documentation from Pump / Motor Supplier