## Slide 1: Stacks Report LM6000
GENERAL NOTES
1. DESIGN CRITERIA
ACOUSTIC:
- Exhaust System: 85 DBA - 3FT FROM EQUIPMENT, 5FT ABOVE GRADE
65 DBA - 400 FEET FOR ONE UNIT IN OPERATION
MECHANICAL:
- Exhaust System: EXHAUST INTERNAL DESIGN PRESSURE
DESIGN PRESSURE DUCT +18"/-2" W.C.
DESIGN PRESSURE STACK +12"/-2" W.C.
OPERATING PRESSURE ALL +8"/-2" W.C
STRUCTURAL:
- SEE DRAWING A-9656-001 SHEET 3
FLOW CONDITIONS:
- MAX FLOW RATE 269 LBM/S AT 848°F
- MAX EXHAUST TEMP - 1,000°F
2. COMPONENTS / CONSTRUCTION
EXPANSION JOINT :
- 304 STAINLESS STEEL HOT-SIDE FRAME, BACKING BARS AND FLOW LINER
- CHEMFAB 1000BF BELT WITH FIBER GLASS INSULATION AND WIRE-FLEXTRA
BACKING CLOTH
- CARBON STEEL COLD SIDE FrAME PAINTED.
STACK BASE, ELBOW & STACK BREECHING:
- 3/8" THICK ASTM A36 CARBON STEEL CASING
- 4" DIA. 304L SS DRAIN PIPE C/W CAP
- 6” THICK 8 LB/CU. FT. DENSITY CERAMIC FIBRE LINING INSULATION
- 12 GA ASTM 240 TYPE 409 STAINLESS STEEL LINING SHEETS
- OVERLAP OF LINING SHEETS IN DIRECTION OF GAS FLOW @ HORIZONTAL
DUCTS AND IN DIRECTION OF RAIN FLOW @ VERTICAL STACK
- 24" x 24" CLEAR OPENING ACCESS DOOR.
10/19/2010
ProEnergy International

## Slide 2: Stacks Report LM6000
SILENCER:
- 1/4" THICK ASTM A36 CARBON STEEL CASING
- 2” THICK 8 LB/CU. FT. DENSITY CERAMIC FIBRE LINING INSULATION
- 26 GA 409SS SEPTUM LINER
- 4” THICK 8 LB/CU. FT. DENSITY BASALT WOOL LINING INSULATION
- GLASS SILK CLOTH AND 304 SS MESH RETAINER
- 12 GA ASTM A240 TYPE 409 STAINLESS STEEL LINING SHEETS
(PERFORATED AT BAFFLE LOCATION ONLY)
SILENCER SPLITTER CONSTRUCTION :
- 12 GA ASTM A240 TYPE 409 STAINLESS STEEL SILENCING SPLITTER
PERFORATED FACING SHEETS
- 12 GA ASTM A240 TYPE 409 STAINLESS STEEL SILENCING SPLITTER FRAMES
- BASALT WOOL WRAPPED WITH GLASS SILK CLOTH AND COVERED WITH
304 STAINLESS STEEL MESH ON GAS FACES
PERSONNEL PROTECTION SCREEN :
- 1 1/2-13F EXPANDED METAL, GALVANIZED.
- 3/8"-16 UNC ZN PL STAND-OFFS (8 1/2" LG APPROX.) FIELD WELDED TO CASING
(24" SQ. CENTERS)
HARDWARE :
- FLANGE CONNECTIONS: 3/4" DIA. ASTM A325 HOT DIP GALVANIZED BOLT SETS
C/W TWO WASHERS
3. FINISH
EXTERNAL ONLY SURFACES OF SYSTEM:
- CLEAN TO SSPC SP10
- ONE COAT DIMETCOTE 9 INORGANIC ZINC PRIMER
ONE UNIT REQUIRED FOR P.O.# PS4701
ONE UNIT REQUIRED FOR P.O.# PS4703
ONE UNIT REQUIRED FOR P.O.#
10/19/2010
ProEnergy International

## Slide 3: Stacks Report LM6000
10/19/2010
ProEnergy International

## Slide 4: Stacks Report LM6000
10/19/2010
ProEnergy International

## Slide 5: Stacks Report LM6000
10/19/2010
ProEnergy International