## SOS
Scope of Supply and Purchaser's Responsibilities
FT8-3 MOBILEPAC W/I POWER ISLAND
BRUSH GENERATOR
| DUAL FUEL WATER INJECTION |  |  | Qty: | 3
Line No. |  |  |  | Quantity | Design | Supply | Erection
| Item |  | Description |  |  |  |  | Notes
2 | I. | POWER TRAILER
4
6 |  | 1 | GAS TURBINE PACKAGE | 3 | P | P | C
8 |  |  | Gas Generator (GG8-3 Core Engine)
14 |  |  | Power Turbine
18 |  |  | Diffuser
20 |  |  | Collector Box
22 |  |  | Exhaust transition
24 |  |  | Fabricated gas turbine base and mount assembly
26 |  |  | Coupling connecting power turbine and generator
28 |  |  | Hydraulic starting motor
30 |  |  | Ignition system
32 |  |  | Off-line compressor internal water wash system. |  |  |  |  | Pipe, nozzle, valve internal to Power Trailer included.. One (1) Water wash skid included for the project.
44 |  |  | Lube oil system |  |  |  |  | Combined GG & PT
46 |  |  | * Single oil-to-air cooler
48 |  |  | * Motor driven pumps |  |  |  |  | One AC; One DC
50 |  |  | * Stainless Steel Piping |  | P | P | C
54 |  |  | Fuel supply system |  | P | P | C | Skid is prime painted
56 |  |  | * Fuel gas strainer |  | P | P | C
58 |  |  | * Gas fuel fire valve |  | P | P | C
60 |  |  | * Liquid fuel fire valve
62 |  |  | * Fuel Gas/Liquid Fuel flowmeter/totalizer
64 |  |  | * Last Chance Filter
66 |  |  | Buffered air system
68 |  |  | * Single air-to-air cooler
70 |  |  | * Instrumentation for temperature control
71 |  |  | * One AC motor driven pump
72 |  |  | Water injection NOx control system |  |  |  |  | Skid is prime painted
74 |  |  | * One AC motor driven pump
76 |  |  | * Single air-to-air cooler
78 |  |  | Gas Turbine Enclosure
79 |  |  | * Secondary cooling air system with louvers
81 |  |  | * Secondary cooling air inlet silencer
82 |  |  | * Vents and drains |  |  |  |  | Customer to provide waste drain tank at each site for each unit. Freeze protection for tank and hoses from Power Trailer to tank are in customer scope.
84 |  |  | * Interior AC/DC lighting
86 |  |  | * CO2 Fire Suppression System |  |  |  |  | CO2 Bottles supplied by PWPS. CO2 and Nitrogen precharge supplied by Customer at jobsite. Bottle rack is external to power trailer.
88 |  |  | * Sound attenuation to meet 95 dB(A) Average |  |  |  |  | Average at 3 feet (one meter)
90 |  |  | * Three point jacking and leveling system |  |  |  |  | Customer to provide level and compacted site with soil of at least 191,521 Pa. (4000 lbs) per square foot compressive strength.
92 |  |  | Two-stage inlet air filter with weather protection |  |  |  |  | 1st stage prefilter, 2nd stage high-efficiency media. Prime painted
100 |  |  | Inlet silencing |  |  |  |  | One 1.2 m (4 ft.) inlet section included. Prime painted
106 |  |  | Exhaust Stack |  |  |  |  | Top of exhaust stack 10.36 m (30ft) above grade; transition and two exhaust silencing sections included. Prime painted only.
108 |  |  | * Quick Disconnect Electrical Interface
110
114
116 |  | 2 | GENERATOR PACKAGE | 3 | P | P | C
118 |  |  | Brush Open Ventilated Air Cooled Synchronous Generator or equivalent |  |  |  |  | Brush 62-170/ER with electric heater installed
124 |  |  | Brushless Exciter Assembly |  |  |  |  | With pilot exciter
126 |  |  | Stator Heaters
128 |  |  | Neutral ground transformer/resistor
130 |  |  | Current transformers |  |  |  |  | Quantity 4 per package
132 |  |  | Stator RTD’s |  |  |  |  | Quantity 6 with 6 spares per package
134 |  |  | Vibration probes |  |  |  |  | Proximity
136 |  |  | Bearing drain RTD’s |  |  |  |  | One per bearing
138 |  |  | Bearing metal RTD’s |  |  |  |  | One per bearing
140 |  |  | Hot and cold air RTD’s
142 |  |  | Rotor ground detection
144 |  |  | Generator Lube oil System |  |  |  |  | Air cooled
146 |  |  | * Single Stage Filter
148 |  |  | * Oil pumps |  |  |  |  | One Rotor Driven; One DC
149 |  |  | * Air/Oil heat exchanger with fan
150 |  |  | * Stainless steel piping downstream of filters
154 |  |  | Enclosure |  |  |  |  | Finish Painted aluminum enclosure
158 |  |  | * Inlet air filter
160 |  |  | * Inlet and exhaust silencing
162 |  |  | * Interior AC/DC lighting
164 |  |  | * Sound attenuation to 95 dB(A) Average |  |  |  |  | Average at 3 feet (one meter)
166 |  |  | * Fire detection system
170 |  |  | * Quick Disconnect Electrical Interface
172
174 | II. | CONTROL TRAILER |  | 3 | P | P | C | Prewired and checked
176 |  | 1. | Control Enclosure |  |  |  |  | Finish Painted Enclosure
178 |  |  | * HVAC
180 |  |  | * Fluorescent lighting
182 |  |  | * DC emergency lighting
184 |  |  | * AC power outlets
186 |  |  | * Smoke detection
190 |  |  | Operator control cabinet
192 |  |  | * Starting and operating controls |  |  |  |  | Manual and automatic
194 |  |  | * Speed indication
196 |  |  | * Voltmeters and frequency meters |  |  |  |  | Bus and generator
198 |  |  | * Ammeter
200 |  |  | * Wattmeter
202 |  |  | * VAR meter
204 |  |  | * Power Factor Meter
206 |  |  | * Synchroscope and lamps
208 |  |  | Monitoring cabinet
210 |  |  | * HMI Interface (CRT, keyboard and software for operator interface) |  |  |  |  | Citect ICE.
212 |  |  | * Printer
214 |  |  | Instrument Cabinet
216 |  |  | * Micro automatic voltage regulator |  |  |  |  | Auto follower and trip to standby
218 |  |  | * Digital synchronizer
220 |  |  | * Vibration monitor |  |  |  |  | Gas turbine and generator
222 |  |  | * Fire protection system power supplies
224 |  |  | * Static inverter
226 |  |  | Unit control cabinet
228 |  |  | * Control system for automatic starting, running, loading, unloading and shutdown of the unit.
230 |  |  | * Timer Panel
232 |  |  | * Expansion chassis
240 |  |  | Generator protective relay panel
242 |  |  | * Generator protective relays |  |  |  |  | One Beckwith 4325A. Transformer protection by Customer.
244 |  |  | * Lockout relays
246 |  |  | * Watt hour meter
248 |  |  | Motor Control Center
250 |  |  | * AC and DC distribution panels
252 |  |  | * Motor starters
254 |  |  | * Distribution transformer
256 |  |  | * Breakers as required
258 |  |  | * Manual transfer switch
262 |  |  | Master terminal cabinet
264 |  |  | * Field termination blocks
266 |  |  | * Power supplies
268 |  |  | Rack mounted sealed lead acid cell batteries |  |  |  |  | 24 VDC and 125 VDC
270 |  |  | Battery chargers |  |  |  |  | One 24VDC; One 125VDC
272 |  |  | Switchgear module 15 kV Class
274 |  |  | * Metalclad switchgear compartment |  |  |  |  | Mounted in control enclosure
276 |  |  | * Circuit breaker |  |  |  |  | 2000 Amp/ 750 MVA, 15kV class Totally enclosed, 15kV class, 2000 Amp
286 |  |  | * Lightning arresters and surge capacitors
288 |  |  | * Current transformers and potential transformer
290 |  |  | * CTG Auxiliary transformer
292 |  |  | FM200 Fire Suppression
303 |  | 2 | HYDRAULIC STARTING PACKAGE | 3 | P | P | C | Trailer mounted with enclosure including fire detection (No fire suppression)
306 | III. | FIELD INSTALLATION HARDWARE |  |  | P | P | C
310 |  |  | Interconnecting piping and hoses for: Hydraulic Start, CO2, Fuel |  | P | P | C | Between PWPS supplied aux skids, Power Trailer, and Control Trailer
318 |  |  | Interconnecting Quick Disconnect electrical cables for power and signal. |  | P | P |  | Between PWPS supplied aux skids, Power Trailer, and Control Trailer. HV cables from generator to switchgear included.
320 |  |  | Access Stairs and platforms for Power Trailer and Control Trailer |  | P | P |  | Std supply provides for 3 access points per trailer which can be configured per customer requirements at site.
322 |  |  | Piping intefaces |  | P | P |  | Maiting flanges on all Customer piping interfaces is by others
324 |  |  | Special Maintenance Tools |  | P | P |  | One set for the site
326 | IV. | PWPS SUPPLIED SERVICES AND RESPONSIBILITIES
|  | 1 | PROJECT MANAGEMENT, CONSTRUCTION AND COMMISSIONING SUPPORT |  |  | P
328 |  |  | PWPS Project Manager assigned to project to manage project execution single point contact for customer. |  |  | P
330 |  |  | Technical Representatives to advise Customer Supervisory Personnel during initial equipment erection, checkout, commissioning, and testing. |  |  | P
332 |  |  | Instruction Manuals and Plant Documentation provided: Construction Manual, Commissioning Manual & Sign-off Sheets, Picture Book, PWPS Drawing Package, Vendor Manuals & Drawings, FT8 Maintenance Manual, FT8 Illustrated Parts Catalog, FT8 Service Bulletins, MOBILEPAC Operating Instructions, Bill of Material, As Built Drawings. |  |  | P |  | Provided in CD or alternate electronic format for PWPS Supply. One (1) hard copy of O&M Manual in English is included.
334 |  |  | PWPS training “Power Plant Operators Course” |  |  | P |  | Training description can be found in the PWPS Customer Training Document version 21-0802. Travel and lodging for customer's personnel not included.
|  | 2 | PERFORMANCE TESTING SUPPORT
336 |  |  | Thermal Performance Testing |  |  | P | C | Customer to provide all personnel and equipment required for emissions testing.
338
340 | V. | OWNER SUPPLIED SERVICES AND RESPONSIBILITIES | [5 empty] | Owner is responsible for compliance with PWPS' operating, installation, and maintenance instructions. Warranty is contingent upon compliance.
344 |  | 1 | PROJECT AND SITE DEVELOPMENT |  | C | C | C | Owner is responsible for all areas of site development and are not limited to the items listed in this document.
346 |  |  | Adequate Title and Interest, Permanent Facility Permits, Construction Permits and Licensing |  |  | C |  | To permit the installation of such units and their operation for at least the period contemplated by the contract. Provide PWPS representatives unrestricted access at all times as may be reasonably necessary in the performance of their duties.
350 |  |  | Foundations for all Equipment |  | C | C | C | Site prep, leveling and compaction to meet at least 191,521 Pa (4000 lbs per square foot) compressive strength.
351 |  |  | Equipment Mounting |  | C | C | C | Customer responsible for hardware to secure PWPS supplied Stairs/Platforms & Ancillary Skids (CAB, Fuel Metering Skids, CO2 Enclosure, Cable Trays).
354 |  |  | Provision of Secure Field Office adequate for 3-5 PWPS field personnel. Furnished with electricity, Heating and Air Conditioning, Drinking Water, Desks, Chairs, Parking Area, Lockers and others which are necessary for Field Works, Services & Sanitary Facilities of Office Personnel. |  | C | C | C
355 |  |  | SAFETY PROVISION, Provide a safe working environment that meets or exceeds all applicable local, regional, national, and international safety standards and regulations. |  | C | C | C | The purpose of this provision is to emphasize the importance of site safety and insure safe working conditions for all personnel. PWPS and our sub-contractors/suppliers will only be able to provide support under safe site conditions.
356 |  |  | Provision of First Aid and Medical Services - OSHA Approved |  | C | C | C
358 |  |  | Provisions of Local Communication Facilities |  | C | C | C | Telephone (local and long distance) with international direct dialing and fax machine. This should be a minimum of 3 lines in the PWPS field office. A separate dedicated phone line shall be provided to each turbine control system in the control house.
360 |  |  | Temporary Construction Staging & Secure Inventory Area |  |  | C
362 |  |  | Access Road(s), Interior Roads, and Parking Areas |  | C | C | C | All-weather and unobstructed
364 |  |  | Transmission System |  | C | C | C | Including interconnection to PWPS supplied equipment.
366
368 |  | 2 | ENGINEERING AND CONSTRUCTION
370 |  |  | Site Engineering |  |  | C
372 |  |  | All Supervision and Craft Labor for complete off-loading, Inventory, Inventory control, Storage, Erection, Installation, Checkout, Testing, and Start-up of all non-PWPS supplied equipment and material. |  |  | C |  | Customer is responsible for scheduling all works on site and directing all craft.
374 |  |  | Maintaining and Guarding all Facilities, Equipment, and Materials during construction |  |  | C |  | Including security fence
376 |  |  | Site Organization During Construction |  |  | C |  | Including Resident Field Construction Manager.
378 |  |  | Emissions and Acoustic Testing |  |  | C
380 |  |  | Worker's Compensation, Employer's Liability, or any other Local Insurance Required |  |  | C P |  | Each party will cover its personnel.
382 |  |  | Consumable Material for Erection Works |  |  | C |  | As required
384 |  |  | Construction Equipment, Tools and Aids |  |  | C |  | For PWPS Supplied equipment.
386 |  |  | Required Tests Prior to Startup: Including but not limited to: |  |  | C
388 |  |  | * Resistance ratio and polarity tests |  |  | C |  | For PWPS Supplied equipment.
390 |  |  | * All high voltage dielectric tests * Field check and calibration * Protective Relay Calibration |  |  | C |  | For PWPS Supplied equipment.
392 |  |  | Phasing and Synchronizing the Generator to Purchaser’s system |  |  | C P |  | Interface between Genset & Grid.
394
396 |  | 3 | INTERFACE REQUIREMENTS AND RESPONSIBILITIES
398 |  |  | Site Facilities Motor Control Centers |  |  | C |  | Customer to provide power, potable water, fuel, service air.
399 |  |  | Natural Gas for Start-up, Testing and Operation 475 psig (33 bar), Approximately 4700 scfm (2.2 m3/sec) per gas turbine |  | C | C | C | Interface Point: Flange on PWPS Power Island. Per PWPS Natural Gas Fuel Specification FR-2. Fuel to be tested by a certified lab and the results provided to PWPS prior to start-up.
406 |  |  | Liquid Fuel for Start-up Testing, and Operation 30-75 psig (2.0-5.1 bar), Approximately 36 gpm (136 l/min) per gas turbine |  |  | C |  | Interface Point: Flange on fuel storage tank. Per PWPS Liquid Fuel Specification FR-1. Fuel to be tested by a certified lab and the results provided to PWPS prior to start-up.
400 |  |  | Injection Water for NOx Control 35-75 psig (2.4-5.2bar), Approximately 37 gpm (115 liters/min) per gas turbine |  |  | C |  | Interface Point: Flange on PWPS Power Island. Per PWPS Specification AR-1. Water to be tested by a certified lab and the results provided to PWPS prior to start-up.
401 |  |  | Potable Water for Gas Turbine Off-line Water Wash 30-105 psig (2.1- 7.3 bar) min., Approximately 300 gallons (1150 liters) per gas turbine water wash at 35 gpm (133 liters/m) |  |  | C |  | Interface Point: Flange on PWPS Power Island. Per PWPS Potable Water Quality Specification
402 |  |  | Control System Interface / Grid Signals |  |  | C P |  | PWPS and Customer to coordinate I/O interface between PWPS supplied equipment and Customer supplied equipment.
413 |  |  | Vent and Drain. Maximum flow on Oily Waste drain is 35 GPM for water wash. Total waste water per wash is 300 gal. |  |  | C |  | Interface Point: Flange connection+I163+I145 on drain pipe on underside of PWPS Power Trailer.
416 |  |  | High Voltage Power |  |  | C |  | Interface Point: Switchgear terminals on the control trailers.
419 |  |  | Alternate Electrical Power Supply 255 kW per Power Island, 380V, 50 Hz, 3 phase for lighting, heating and intermittent auxiliaries |  |  | C |  | Interface Point: Manual transfer switch on control trailer.
422 |  |  | Electrical ground grid interconnections. Grounding pads are provided by PWPS on each trailer and aux skid. |  |  | C |  | Customer to provide adequate ground grid and cable, lug, etc. required to make interconnection. Ref. Drawing 0719-123-E300D, Grounding, Field Electrical.
423
424 |  | 4 | OTHER RESPONSIBILITIES |  | C | C | C | The following list of items is provided for your convenience and gives examples of the types of equipment and/or services that are outside the PWPS Scope of work, and if required, are the sole responsibility of the Owner.
426 |  |  | Site Survey/Plot Plan
428 |  |  | Excavation for Foundations, Pipes, Roads, Cabling & Grounding Grid
430 |  |  | Site Leveling
432 |  |  | Backfill
434 |  |  | Finish Grading
438 |  |  | Surface Drainage to and including any Collection Pond
440 |  |  | Oily Water Separator
442 |  |  | Sanitary Waste Disposal
444 |  |  | Plant Fire Protection Systems-Hydrants Panels and Extinguishers |  |  |  |  | Including Fire Protection during construction
446 |  |  | Plant Lighting
448 |  |  | Intra-communication system
450 |  |  | Site Fencing and Gates
452 |  |  | Construction Water
454 |  |  | Builder's All Risk Insurance (BAR)
480