# TYPICAL SCOPE OF SUPPLY LM6000

## Basic Scope Description

### Gas Turbine

General Electric gas turbine model LM6000 is a two-shaft/two-spool engine consisting of a five-stage low pressure compressor, a fourteen-stage high pressure compressor, a two-stage high pressure turbine, and a five-stage low pressure turbine.  The engine is equipped with a stainless steel mesh screen in the inlet air stream for "last chance" protection against foreign object damage.  The engine is shock mounted and shipped in position, with the exception of the coupling spacer, which is removed and shipped in a separate container

### Generator

Air cooled, 2-pole generator operating at 13.8 kV, 60 Hz.  Generator is capable of handling customer power requirement throughout a wide ambient temperature range. The generator includes a brushless excitation system with permanent magnet generator.  Neutral and line side cubicles are included.

### Unit Enclosure

The package is supplied with weatherproof, acoustic enclosures.  The enclosures are designed to achieve noise abatement to an average of 85 dB(A) at 3 ft. (1.0 m) away and 5 ft. (1.5 m) above grade during full load operations.  The enclosures are completely assembled and mounted over the equipment prior to testing and shipment.  Both turbine and generator compartments are fully ventilated with redundant fans (one running, one stand-by).  Explosion-proof lighting is provided in both compartments.

### Gas Turbine / Generator Base plate

The package is supplied with the support structures for the gas turbine generator set consisting of a two-piece skid assembly, which is sectioned between the gas turbine and the generator.  The full depth, bolted section is designed to provide the full structural properties of the wide flange I-beams.  Full depth cross members are utilized to provide for a rigid design that is suitable for installation in earthquake areas (IBC2000) as well as providing a convenient structure for transportation.

### Air Inlet System

The package is supplied with a modular, multi-stage filtration system consisting of inlet screens, a prefilter and a final barrier filter.  All air for ventilation systems is filtered to the same level as turbine combustion air.  An anti-ice, an evaporative cooling, a combustion air heating or a chilling system is available as an option.  Filtered air is silenced before entering the turbine plenum.  This design results in a compact arrangement and eliminates the need for customer supplied inlet ducting when the standard design is utilized.  Internal lighting of the filter house is provided to facilitate inspection and service.  Package is also supplied with platforms and ladders to service the inlet filter.

### Turbine Exhaust

The package is supplied with a circular, axial exhaust outlet with connection flange to facilitate in-line mounting of an HRSG or simple cycle exhaust stack.

### Fuel System

The package is supplied with a natural gas fuel system that utilizes an electronically controlled fuel-metering valve.  For full-load operation, the gaseous fuel must be supplied to the base plate at 675 psig±20 (4,654 ±138 kPag).  Gas fuel must meet General Electric specification MID-TD-0000-1 (See Section Error: Reference source not found).

### Lube Oil Systems

The package is supplied with two separate lube oil systems: one synthetic for the gas turbine and one mineral for the generator.  The oil reservoirs and piping are all stainless steel, and the lube oil system valves have stainless steel trim.  The turbine coolers, oil reservoir, and filters are mounted on the auxiliary equipment module.  The mineral lube coolers, reservoir and filters are located on the main skid base plate.  The auxiliary equipment module provides simplified piping connections and reduces customer's installation time and costs.  Customer must supply cooling water to the shell and tube coolers.  Turbine lube oil must meet MID-TD-0000-6 (See Section Error: Reference source not found).

### Electro-Hydraulic Start System

The package is supplied with an electric motor driven hydraulic pump assembly, filters, cooler and controls, mounted on the auxiliary equipment module.  A hydraulic motor is also mounted on the gas turbine accessory gearbox.  Hydraulic hoses are furnished to connect the auxiliary equipment module and the main base plate.

### Fire Protection System

The package is supplied with a factory installed fire protection system complete with optical flame detection, hydrocarbon sensing and thermal detectors, piping and nozzles in both the generator and the turbine compartments.  The fire protection system includes cylinders containing CO2 mounted on a separate skid.  A 24 V DC battery and charger to power the fire protection system is also included.  All alarms and shutdowns are annunciated at the turbine control panel (TCP).  An alarm sounds at the turbine if the gas detectors detect high gas levels, or if the system is preparing to release the CO2.  When the system is activated, the package shuts down, and the primary CO2 cylinders are discharged into the turbine and generator compartments via multiple nozzles, and the ventilation dampers automatically close.  After a time delay and if required, the reserve supply of CO2 is discharged.

### Digital Control System

The package is supplied with a free-standing control panel suitable for mounting in an indoor, non-hazardous area.  The control system features an integrated Woodward MicroNet Plus turbine control system, vibration monitor, digital meter, digital generator protective relay module and an HMI (human machine interface) display of key discrete and analog data.  The operator selects HMI displays with convenient touch screen control.  Alarm and shutdown events are displayed on the HMI automatically.  An Ethernet TCP/IP EGD or RS485 Modbus Port is provided to transmit unit conditions (status, pressures, temperature, etc.) to the customer's distributed control system.  Power for the control panel is provided by a dedicated 24V DC battery system with dual 100% capacity chargers, which are shipped separately for installation by others.

### Generator Protective Relays

The package is supplied with a microprocessor-based generator protective relay module, mounted in the TCP.  The protective relay system includes functions necessary for protection of the generator.

### Soak Wash System

The package is supplied with a turbine cleaning system, which allows customers to clean the compressor section of the turbine during full power operation. The same system reservoir and piping are utilized for off-line soak washing.  Auxiliary skid connections are provided for customer supplied purified water at a maximum of 50 psig (345 kPag) and air at 100 – 120 psig (689 – 827 kPag).  Customer is required to provide water meeting MID-TD-0000-4 (See Section Error: Reference source not found), detergent meeting MID-TD-0000-5 (See Section Error: Reference source not found), and air filtered to ISA S7.3 standards.

### Component Testing and Package Test

Every new gas turbine is performance tested under load in a GE Test Cell, using procedures developed for flight turbine reliability.  The generator is tested to ANSI C50.14 or IEC 34.3 standards at its factory of manufacture.

All gas turbine generator sets receive a static test including:

- Switch State (N.O. or N.C., actuation, wiring, and set point)

- Temperature element output, and wiring

- Transmitter range, output, and wiring

- Solenoid operation

- Control valve torque motor, excitation, and return signal

- Fire system continuity, and device actuation

- System flushing verification

- Tubing integrity

### Drawings, Data and Manuals

The package is supplied with a customer drawing package that includes general arrangement drawings, flow and instrument diagrams, electrical one-line drawings and interconnection plan drawings.  Additional electrical schematic diagrams and logic drawings are provided for record.  See Error: Reference source not found for a detailed typical list and typical drawing delivery.

Maintenance manuals are provided and are printed in English.  The manuals cover operating concepts for power generating equipment, guides to troubleshooting, basic information on components, and equipment within the turbine generator set.

### Improvements and Changes

It is understood that the Seller has the right to make changes in product design and add improvements to products or services at any time without incurring any obligations to install the same on or in connection with the Equipment or Services provided hereunder.

## Optional Equipment and Services Checklist and Descriptions

(I) Included	(S) Quoted Separately

### Factory Options

|  | Error: Reference source not found | Error: Reference source not found |
| --- | --- | --- |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |
|  | Error: Reference source not found | Error: Reference source not found |