| CLIENT: | BIE REF. / REPORT No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bariven S.A. c/o PDVSA Services BV President Kennedylaan 19 2517 JK The Hague The Netherlands | 4519A.02 |  |  |  |  |  |  |  |  |  |  | PAGE 1 OF 3 |  |  |  |  |  |  |
|  | CLIENT P.O. No.: |  |  |  | VISIT No.: |  |  |  |  |  |  | NEXT SCHED. VISIT: |  |  |  |  |  |  |
|  | 5100077213 |  |  |  | GB-02 |  |  |  |  |  |  | None |  |  |  |  |  |  |
| VENDOR: | W.O. / REQ No.: |  |  |  | INSPECTOR: |  |  |  |  |  |  | BASE: |  |  |  |  |  |  |
| Derwick Associates MMG Tower, Piso 16 Calle 53, Urb. PANAMA | 2232 |  |  |  | Garry Bryan |  |  |  |  |  |  | St. Louis, Missouri |  |  |  |  |  |  |
|  | VENDOR REF. No.: |  |  |  | INSPECTION DATE(S): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 13 January 2010 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-VENDORS: |  | LOCATION: |  |  |  |  |  |  |  |  | SUB-VENDOR REF. No.: |  |  |  |  |  |  |  |
| ProEnergy |  | Sedalia, Missouri |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CLIENT P.O. BRIEF MATERIAL DESCRIPTION: |  |  | I-1 | 14 |  | Hrs |  | I-3 | 8 | Hrs |  |  |  | I-4 | 620 KMS |  | I-5 | $0 |
|  |  |  | INSPECTION AT: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Sub-Vendor (ProEnergy – Sedalia, Missouri) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-ORDER – BRIEF MATERIAL DESCRIPTION: |  |  | ORDER STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| LM2500 Generator Package w/o Turbine |  |  | In process |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| P.O. ITEM | P.O. QTY. | QTY ACC. | QTY REJ. | NARRATIVE | QP STAGE |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 0 | 0 | LM2500 Generator Package w/o Turbine |  |

INSPECTION VISIT OF 13 JANUARY 2010: SUMMARY: The purpose of this visit was to perform a final visual inspection of the refurbished equipment (without turbine), review available documentation, obtain the Packing List and determine final export packaging plans. The following personnel participated: Joaquin Mavares – Director of International Sales – ProEnergy Garry Bryan – Inspector – BIE Joaquin Mavares is now the ProEnergy contact for inspection notifications: Phone: 660-829-5100 Mobile: 713-992-1790 SPECIFICATIONS AND DRAWINGS: All of the specifications, O&M manuals and drawings from the previous owner’s installation were available and were reviewed by the inspector.

MATERIALS:

All materials are now complete.

VISUAL AND DIMENSIONAL EXAMINATION:

- The re-furbishing “like new” has been completed for the LM2500 unit, which was built in 1993.  This unit had previously been in continuous operation and was dismantled and all parts (except the turbine) brought to the ProEnergy site.  All new interior piping and wiring was installed and a new single electrical control board provided for all control functions.  This package now is modelled after the current GE package design.  All walls have been stripped down and new insulation/paint provided.  The unit appears to be in “like new” condition.  The enclosure was packaged and being stored in the Vendor’s yard.  (See attached photographs.)  Overall dimensions had been checked and confirmed on the previous visit.

- Testing of the refurbished turbine was completed at another site and the Vendor indicated that test reports had been provided to the owner.  The inspector did not address any turbine related issues during this inspection.

- The generator was being stored in the shop area under controlled conditions (dry and 65°F to 70°F).  All other items were being stored in the Vendor’s yard.

- Serial number for the generator was recorded as GEC 2S553435/01/580K

- The Vendor provided the following serial numbers for the turbines:

  - For LM2500:	691.098 (1993)

- Photographs were taken of all available items on the packages.  These photos are attached and labelled.

- Packing List for LM2500 and photographs of the contents of each box were provided to the inspector and are attached to this report.

MARKING AND PACKING:

All equipment related to the LM2500 which could be boxed is completely packaged and stored in the yard for export in accordance with the Packing List which was provided and attached to this report.  See photos attached.  The Vendor also provided detailed photos of the contents of each box, and identified by the Vendor’s PES Tag Number. These are cross-referenced in the Packing List for easy identification.

The Vendor advised that they operate a certified onsite export packaging facility. White shrink-wrap type covering has been utilized, and appears acceptable. All miscellaneous steel is properly marked and banded for export.  The Generator was being stored in the main building under controlled conditions (dry and 65°F to 70°F).

DOCUMENTATION:

All available documentation from the previous Owner, including drawings, specifications, O&M manuals, and other data was reviewed by the inspector.  A master index of this documentation was provided by the Vendor, and is attached.  All items classified by an “L” were available in hard copy and the originals stamped and endorsed by the inspector.  Items classified by an “I” were available only in electronic format.  These were also all reviewed by the inspector via the Vendor’s on-line documentation system, and found to be acceptable.

Vendor indicated that the documentation would continue to be updated when the final package orientation is determined and as the EPC contract is executed with actual site requirements.  All final documentation will also be provided in electronic format at the completion of the Project.

INSPECTION RELEASE / NON-CONFORMANCE NOTE:

The inspector did not issue a Release Note.  However, this equipment may now be released for final packaging arrangements and shipping.  Vendor’s understanding is that his responsibility at this time is to provide the packaged equipment Ex-works.

ATTACHMENTS:

- Packing list, formatted by (1) Box number and (2) PES Tag number (Excel file)

- Digital Photos by PES Tag number showing the contents of each box.

- Master Index of documentation on the LM2500 (pdf file).

- Selected inspector’s digital photographs of packaged equipment in the yard and of the Generator being stored in the main shop area.

- END OF REPORT -