June 8, 2010

Allen Hill

Centrax Trent 60

Subject:  Centrax Trent 60 Inspection

The engines are located at the Centrax location in Exeter, England.  The 4 engines, serial numbers 055, 056, 057 and 058 are in excellent condition and stored in a controlled enclosure.  Each engine is incased in a vinyl enclosure with a device to condition the air and control the humidity.   See picture A.  Each engine is configured for 50Hz operation and will need to be reconfigured for 60Hz and tested.  Centrax mentioned that it will be completed at Rolls Royce and tested once complete.  Each engine is configured for dual fuel with water injection only.  The engines or packages are not ISI configured.  Each engine has gone through a preservation procedure once a month per Rolls Royce procedure and Centrax has the documents to account for this.

Engine Enclosure Monitor

Each engine is sealed

LPC, VIGV and VBV system

Left side of engine with IP and HP bleed valves and fuel system.

There are two water injection skids and two liquid fuel forwarding skids built as of today.    Centrax is in process of building the remaining skid at this time.  See pictures below.

Water injection skid

Liquid Fuel

The Turbine and Generator enclosures are stored at a warehouse in Staint-Ouen France.  The warehouse in a climate controlled building with low humidity.  Each section of the turbine and generator enclosure is shrink wrapped and the other ship loose items are plastic wrapped and sealed.  The generator heaters are in operation and there are heaters installed in the generator and turbine enclosures to ensure dryness.  The control panels have moisture control devices installed along with monitors to monitor temperature and humidity.  The turbine, generator and all ship loose will need to be crated to meet international shipping guidelines.

Gen Sets.

Gen Sets.

Ship Loose

Ship Loose

Ship Loose

Generator Data Plate

The turbine exhaust, ship loose and rear supports.

Heater mounted on diffuser support.

Turbine inlet with support installed

Fuel system

Bleed air piping and forward engine support.

Turbine lube oil filters

Hydraulic start system

Control cabinet

Control Cabinet.  Rolls Royce FT55 control system.

Control cabinet monitor.  22 c temperature and 42% humidity

Allen Hill

ProEnergy Services Technical Advisor.