ENGINEERING SPECIFICATIONS FORLA INGENIERÍA PROCURAAND CONSTRUCTION OF NEW UNITS OF THERMOELECTRIAL GENERATION INLA PLANTA LUISACÁCERES OF ARISMENDI

EDC0301-02-G-D-001

| REV. | DATE | BRIEF DESCRIPTION OF THE CHANGE | TOTAL P. | ELAB. BY INELMECA | REV. BY INELMECA | APROB. BY THE CLIENT |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 27/10/08 | FINAL EMISSION | 134 | LIMITED LIABILITY COMPANY. | M.M. | J.S. |

CONTENT TABLE

1.	OBJECTIVE 10

2.	DEFINITIONS 10

3.	APPLICABLE CODES AND NORMS 12

3.1.	LOCATION OF EQUIPMENT AND FACILITIES 13

3.2.	ROTATING EQUIPMENT 14

3.3.	PIPES AND ACCESSORIES 15

3.4.	COATING OF PIPES 18

3.5.	PAINTING 19

3.6.	INSPECTION AND TESTS OF EQUIPMENT 20

3.7.	INSPECTION AND TESTS OF CRANES AND EQUIPMENT OF HOISTING 20

3.8.	INSTRUMENTATION AND CONTROL 20

3.9.	ELECTRICITY 21

3.10.	CIVILIAN 24

3.11.	VENEZUELAN ENVIRONMENTAL LEGISLATION 27

3.12.	STATUTORY LAW OF WORK 30

3.13.	STATUTORY LAW OF PREVENTION, CONDITIONS AND ENVIRONMENT OF WORK 30

3.14.	REGULATION OF THE CONDITIONS OF HYGIENE AND SECURITY IN WORK 30

3.15.	OBLIGATIONS CONTAINED IN NORMS ON HYGIENE 31

3.16.	SYSTEM OF UNITS OF MEASUREMENT 31

3.17.	SECURING OF QUALITY 31

4.	GENERAL CONDITIONS 32

5.	INFORMATION OF the SITE and location of parcel 33

5.1.	INFORMATION METEREOLÓGICA 34

5.2.	SEISMIC CONDITIONS 35

6.	TEMPORARY FACILITIES AND SERVICES FOR WORK 35

7.	MODALITY OF HIRING 36

8.	IT REACHES OF WORK 37

8.1.	STUDIES OF CHARACTERIZATION AND ENVIRONMENTAL IMPACT 37

8.1.1.	TOPOGRAPHICAL SURVEY 37

8.1.2.	GEOTECHNICAL STUDY 38

8.1.3.	STUDY OF ENVIRONMENTAL IMPACT (EIA) 38

8.2. basic engineering and OF detail 39

8.3.	GENERAL CIVIL WORKS 40

8.3.1.	PRELIMINARY OPERATIONS 42

8.3.2.	FOUNDATIONS FOR MECHANICAL OR ELECTRICAL EQUIPMENT 42

8.3.3.	Quarter OF BOARDS 43

8.3.4.	TANQUILLAS 43

8.3.5.	LARGE STONE BENCHES OF POWER, COMMUNICATION AND CONTROL 43

8.3.6.	DEMOLITIONS 44

8.3.7.	RECONSTRUCTIONS AND/OR EXTENSIONS 44

8.4.	PACKAGE OF GENERATION 44

8.4.1.	INSPECTION, INSURANCES AND GUARANTEES OF TURBOGENERATORS TO GAS 44

8.4.2.	TRANSPORT, INSTALLATION AND INTERCONNECTION OF TURBOGENERATORS TO GAS 46

8.4.3.	TRANSFORMING TRANSPORT AND INSTALLATION OF POWER 13.8 kV/115KV 46

8.5.	CONNECTIONS TO EXISTING SYSTEMS 47

8.5.1.	CONNECTION TO THE SUPPLY APPARATUS OF FUEL 47

8.5.2.	CONNECTION TO THE WATER SYSTEM ON WATCH 47

8.5.3.	CONNECTION TO THE WATER SYSTEM DESMINERALIZADA 47

8.5.4.	CONNECTION TO THE SYSTEM AGAINST FIRE 48

8.5.5.	CONNECTION TO THE TREATMENT SYSTEM AND DISPOSITION OF INDUSTRIAL EFFLUENTS 48

8.5.6.	CONNECTION TO THE COMPRESSED AIR SYSTEMS 49

8.6.	ELECTRICAL SYSTEM AND CONTROL 49

8.6.1.	SYSTEM OF DAMPING OF ELECTRICAL DISTURBANCES 49

8.6.2.	CONNECTION TO CONTROL ROOM 49

8.6.3.	FACILITIES FOR ELECTRICAL EQUIPMENT 49

8.6.4.	SYSTEMS OF EARTHING 50

8.6.5.	SYSTEM OF FEEDING AND DELIVERY OF ENERGY DC OF THE GENERATION UNITS:	51

8.6.6.	SYSTEM OF ELECTRICAL PROTECTIONS 51

8.6.7.	EXTERNAL LIGHTING SYSTEM 51

8.6.8 integration of signals to the DISTRIBUTED CONTROL SYSTEM 51

8.6.9.	INTEGRATION OF SIGNALS TO THE DETECTION SYSTEM AND FIRE ALARM 52

8.6.10.	Integration TO the SYSTEM OF SHUTDOWN OF PLANT 56

9.	SPARE PARTS 58

10.	SPECIAL TOOLS 58

11.	TRAINING 58

12.	PLANES APPROVED FOR CONSTRUCTION 59

13.	PLANES “LIKE CONSTRUCTED” 59

14.	SUPPORT TO TRIES 59

15.	ENGINEERING OF FIELD 59

16.	SPECIFICATIONS FOR TRY 60

16.1.	ACCEPTANCE TESTS IN MAKE 61

16.2.	TRANSPORT AND STORAGE OF MATERIALS AND EQUIPMENT OF WORK 62

17.	SPECIFICATIONS FOR CONSTRUCTION 63

17.1.	MACHINERIES AND TOOLS OF CONSTRUCTION.

INTRODUCTION

As a result of the studies realized byla C.A Electricidadof Caracas jointly with SENECA, with the purpose of to guarantee the reliable and safe provision of electrical energy to the Margarita island, it has been decided to extend the capacity of electrical Generation inla Plantaexisting Luisa Cáceres de Arismendi located in the Marine municipality to the south-east of the Margarita island to increase his capacity of generation in 67,8 MW (ISO) additional.

The installation of three (3) turbogeneradoras units General Electric, model LM2500 is predicted, working to Simple Cycle and patients with liquid fuel, a capacity ISO of 22.6 MW each.

The present document has as intention to establish the bases for the execution of all the activities that assure the developmentla Ingeniería Básicaand Detail, Tries of equipment and materials of the work, inspection, transport to the site, assembly and construction, training of the personnel, start, tests and beginning of the new units until its NORMAL OPERATION, fulfilling all the norms of quality, established security, hygiene and atmosphere in the present state-of-the-art, in these specifications and the laws ofla República Bolivarianaof Venezuela.

In this sense preparation is had these specifications that contain general information of the project, reaches of engineering to develop, specifications of tries of materials, equipment and systems, reach and specifications of construction, inspection of equipment in makes and/or field, quality control of execution and requirements of documentation, manuals of operation and maintenance, books of the project, everything according to the Norms and indicated Applicable Codes in the Criteria of Design.

Also one includes information on the requirements in the matter of security, hygiene and atmosphere, of planning and programming, methodology of measurement of the global progress of Engineering, Tries, Inspection and Assembly of the WORK, guarantees, spare parts and the plan of training suggested for the professional personnel, technical operators and breadwinners of the PLANT.

- OBJECTIVE

To establish the engineering specifications that allow the installation ofthree (03) new unitsof electrical generation in the Margarita island inla Plantaexisting Luisa Cáceres de Arismendi, by means of the development of basic engineering and of detail, tries, inspection, transport to the site, construction, training, tests, starting and beginning (IPC), until the normal operation of the mentioned turbogeneradoras units GE, model LM2500 with a capacity ISO of 22.6 MW each, working to Simple Cycle operated with liquid fuel, as well as necessary infrastructure works for the correct operation of the units and its connection and integration toLA PLANTA, leaving all the forecasts a future for the operation with gas.

- DEFINITIONS

- LA OBRA: One talks about the development of basic engineering and of detail, it tries, construction, inspection, transport to the site, tests, training, starting and beginning until the NORMAL OPERATION, of the three (03) new turbogeneradoras units GE, model LM2500 with a capacity ISO of 22.6 MW each, working to Simple Cycle and the adaptation of the BALANCE OF PLANT required for his operation.

- LA PLANTA: One talks about tola Plantaexisting Luisa Cáceres de Arismendi with his set of systems, physical and industrial facilities, constituted lands, equipment, materials and accessories which are going to be integrated toLA OBRAas a result of the completación of the corresponding works.

- LA AMPLIACIÓN; One talks about to the extension of the capacity of generation ofLA PLANTAconformed by the set of systems, physical facilities and industrial, equipment, materials and accessories that are constituted and are integrated to the same as a result of the completación of corresponding works a LA OBRA.

- THE COMPANY: It is used to define tola C.A. ELECTRICIDADOF CARACAS, being that contract and pays a LA CONTRATISTA.

- THE CONTRACTOR: She is the legal person who the COMPANY has contracted the execution of the works.

- THE SUPPLIER: One talks about the companies, companies, manufacturers, all of them approved byLA COMPAÑÍA, providers of services or equipment that participates jointly with the CONTRACTOR in the process of licitation for the services that involve the equipment or specified system, as well as to who the CONTRACTOR grants the national or concerned contract for provision of equipment and materials to him.

- THE ENGINEER OF THE PROPRIETOR: She is the legal person engaged by the COMPANY he represents so that it and he supervises during the execution of the works. The revision of engineering and the supervision ofLA OBRAwill be on behalf of the ENGINEER OF the PROPRIETOR who will receive the information of all the studies developed by the CONTRACTOR, for the construction of the foundations and infrastructure, provision of the rest of the equipment noncontemplated inla IP, the total installation of the equipment, the tests and the beginning.

- THE CONTRACT: One talks about the signed legal document entersLA COMPAÑÍAand the CONTRACTOR, integrated by all the Annexes, procedures and other collections, in which the conditions and terms settle down under which it will be due to execute LA OBRA.

- POWER ISLAND (IP): It consists of the equipment of generation of electrical energy that is constituted by the units connected disturb-gas and its auxiliary equipment. All the equipment ofla Islaof Power will be provided byLA COMPAÑÍA, and installed and tried by the CONTRACTOR under the supervision of the ENGINEER OF the PROPRIETOR.

- CONNECTIONS OF PLANT BALANCE: It consists of the connections to all the existing systems, roads, constructions and works required for the correct operation of la IP.

- MECHANICAL COMPLETACION: One talks about to that the WORK has been designed and constructed in agreement with the last edition of the engineering planes, present state of the art, specifications, instructions, codes, and applicable regulations. It is understood that in this stage all the activities of “PRECOMMISSIONING” have concluded, that is to say, those previous ones to PREARRANQUE.

- PRECOMMISSIONING: Activities refer to all those and tests realized by CONTRACTOR, previous to COMMISSIONING (PREARRANQUE) that allows to guarantee toLA COMPAÑÍAthat the MECHANICAL COMPLETACION has been obtained, in accordance with the reach of the WORK, the terms and other conditions of the CONTRACT.

- COMMISSIONING (PREARRANQUE): One talks about to all those preparatory activities realized by the CONTRACTOR, as of the date of the MECHANICAL COMPLETACION and previous to the STARTING and BEGINNING until the commercial operation ofLA AMPLIACIÓN, in accordance with the reach of the WORK, the terms and other conditions of the CONTRACT.

- STARTING: one talks about to the previous stage to the NORMAL OPERATION ofLA AMPLIACIÓN, whenLA COMPAÑÍAwith attendance of the CONTRACTOR, realizes the activities of feeding of raw materials and adjustments and intonation of LA AMPLIACIÓN.

- NORMAL OPERATION: One talks about at the moment at whichLA AMPLIACIÓNit has operated by a minimum period of thirty and two (32) days consecutive, to total capacity, generating the waited for products, according to the guaranteed numbers.

- TESTS OF GOOD OPERATION: One talks about the tests that will have to execute the CONTRACTOR, to verify the suitable operation and operation ofLA AMPLIACIÓNequipment and other facilities designed and/or constructed by the CONTRACTOR, according to the present norm, state-of-the-art, specification, plane, code, norm and better practice of engineering than allow to guarantee the correct implantation of the WORK and according to the conditions stipulated in the CONTRACT.

- CAPACITY TESTS: One talks about the levels of capacity, recovery and quality of products that will have to process the equipment and integral systems of the WORK and other components ofLA AMPLIACIÓN, with a predetermined consumption of raw materials and industrial services and according to the conditions stipulated in the CONTRACT.

- TRUSTWORTHINESS TESTS: One talks about to the probability in that an equipment or system it realizes his anticipated function, without incidents, by a period of specified time and under indicated conditions industrialists and according to the conditions stipulated in the CONTRACT.

- PROVISIONAL ACCEPTANCE: Document signed byLA COMPAÑÍAand the CONTRACTOR like certainty of which the TESTS OF GOOD OPERATION and TESTS OF CAPACITY have been fulfilled to satisfaction and by means of whichLA COMPAÑÍAreceives the WORK in provisional form during a period of guarantee of twenty-four (24) months.

- GUARANTEES: One talks about to the period between the date of the company/signature of the Act of PROVISIONAL ACCEPTANCE and the date of the company/signature of the Act of DEFINITIVE ACCEPTANCE of the WORK executed by the CONTRACTOR.

- DEFINITIVE ACCEPTANCE: One talks about the act by means of whichLA COMPAÑÍAit completely receives the totality of the WORK of the CONTRACTOR, after to have turned the period of GUARANTEE of twenty-four (24) months, after the company/signature of the Act of PROVISIONAL ACCEPTANCE and all the other obligations on the part of the CONTRACTOR, according to the established thing in the CONTRACT.

- APPLICABLE CODES AND NORMS

The CONTRACTOR will become attached itself to the applicable norms, codes and regulations, as well as to local, national and international laws, of way to obtain the best quality level of the product, trustworthiness and security during the design, the construction and operation of all the facilities contemplated for the execution of the WORK.

LA COMPAÑÍAthe right is reserved to ask for to the CONTRACTOR the applicable certification of the fulfillment of the codes, norms, regulations and laws in the design and construction of the facilities contemplated for the execution of the WORK.

Unless the opposite specifies itself, the CONTRACTOR will use the last edition of codes and norms. When several codes, norms, regulations differ to each other, it will be applied the most demanding criterion from the point of view of operational trustworthiness, security, hygiene and atmosphere.

  - LOCATION OF EQUIPMENT AND FACILITIES

| American Petroleum Institute |  |
| --- | --- |
| API RP 750 | Management of Process Hazards |
| API RP 752 | Management of Hazards Associated with Location of Process Plant Buildings |
| Venezuelan commission of Industrial Norms (COBENIN): |  |
| COBENIN 200 | National Electrical code |
| COBENIN 1565 | Maximum levels of Permissible Noise in Work areas. |
| COBENIN 2239 | Inflammable and Combustible materials, Storage and Manipulation. Part I. Liquid. |
| COBENIN 694-82 | Safety measures to follow inla Ventaand Chlorine Transport |
| COBENIN 695-82 | Safety measures to follow by the Users of Chlorine Containers |
| National Fire Protection Association: |  |
| NFPA 30 | Flammable and Combustible Liquids Code |
| NFPA 70 | National Electrical Code |

  - ROTATING EQUIPMENT

| American Petroleum Institute: |  |
| --- | --- |
| API 610 | Centrifugal for Pumps Petroleum, Petrochemical and Natural Gas You train |
| API 613 | Special Purpose Gear for Units Petroleum, Chemical and Gas Industry Services |
| API 614 | Lubrication, Shaft-sealing, and Control Systems and for Auxiliaries Petroleum, Chemical and Gas Industry Services |
| API 616 | Gas for Turbines the Petroleum, Chemical and Gas Industry Services |
| API 617 | Axial and Centrifugal Compressors and for Expander-compressors Petroleum, Chemical and Gas Industry Services |
| API 671 | Special Purpose for Couplings Petroleum, Chemical and Gas Industry Services |
| API 675 | Positive Displacement Pumps - Controlled Volume |
| API 682 | Pumps - Shaft for Sealing Systems Centrifugal and Rotary Pumps |
| American National Standards Institute |  |
| ANSI/ASME B73.1M | For Specification Horizontal End Suction Centrifugal for Pumps Chemical Process |
| ANSI/ASME B73.2M | Vertical for Specification In-line Centrifugal for Pumps Chemical Process |
| ANSI/ASME B16.5 | Pipe Flanges and Flanged Fittings |
| ANSI/HI - M100 | Hydraulic Institute Standards |
| Venezuelan commission of Industrial Norms (COBENIN): |  |
| COBENIN 2453 | Centrifugal pumps for use in systems of fire extinguishing |
| National Fire Protection Association: |  |
| NFPA 20 | For standard the Installation of Stationary for Pumps Fire Protection |

  - PIPES AND ACCESSORIES

| American Society of Mechanical Engineers (ASME)/ANSI |  |
| --- | --- |
| ANSI/ASME B 1.1 | Unified Inch Screw Threads |
| ANSI/ASME B 2.1 | Pipe Threads (Except Dry Seal) |
| ANSI/ASME B16.10 | Block and Check Valves |
| ANSI/ASME B16.11 | Forged Steel Fittings, Socket Welding and Threaded |
| ANSI/ASME B16.21 | Non metallic Flat Gasket for Pipe Flanges |
| ANSI/ASME B16.25 | Butt Welding Ends |
| ANSI/ASME B16.34 | Steel Valves, Flanged And Butt welding Ends |
| ANSI/ASME B16.47 | Large Diameter Steel 26 Flanges NPS " Through NPS 60” |
| ANSI/ASME B16.5 | Pipe Flanges and Flanged Fittings |
| ANSI/ASME B18.2 | Square and Hex Bolts & Nuts |
| ANSI/ASME B 31.1 | Power Piping |
| ANSI/ASME B 31.3 | Process Piping |
| ANSI/ASME B 31.4 | Liquid for Transportation Systems Hydrocarbons, Liquid Petroleum Gas, Anhydrous Ammonia and Alcohols |
| ANSI/ASME B 31.8 | Gas Transmission and Distribution Piping Systems |
| ANSI/ASME B 36.10 | Welded and Seamless Wrought Steel Pipe |
| ANSI/ASME B 36.19 | Stainless Steel Pipe |
| American Petroleum Institute: |  |
| API 5L | Line Pipe Specifications |
| API 570 | Inspecting Piping Certification |
| API 600 | Steel Gate Valves - Flanged and Butt-Welding Ends |
| API 601 | Metallic Gaskets for Refinery Piping |
| API 602 | Compact Steel Valves |
| API 605 | Large Diameter Coal Steel Flanges |
| API 1110 | Pressure Testing of liquid Petroleum Pipelines |
| API 1104 | Welding of Pipelines and Related Facilities |
| Manufacturers Standarization Society |  |
| MSS-SP-44 | Steel Pipe Line Flanges |
| MSS-SP-25 | Standard Marking for System Valves, Fittings, Flanges and Unions |
| International Organization for Standardization (ISO) |  |
| ISO 15348 | ISO 15348 |
| American for Society Testing and Materials (ASTM) |  |
| ASTM TO 105 | Coal Steel for Forgings Piping Components |
| ASTM TO 106 | Seamless Coal Steel for Pipe High Temperature Services |
| 193 ASTM TO | Alloy Steel & S. Steel Bolting for Materials High Temp Service |
| ASTM A194 | Coal and Alloy Steel Nuts and Volts in High Pressure and High Temperature Service |
| ASTM TO 307 | Coal Steel Externally and Internally Threaded STD Fasteners |
| ASTM TO 53 | Welded and Seamless Steel Pipe |
| ASTM AND 10 | For test Brinell Hardness of Metallic Materials |
| ASTM AND 110 | For test Indentation Hardness of metallic Materials by Portable Hardness Testers |
| American Welding Society |  |
| AWS TO 5.1 | For Specification Coal Steel Covered Arc Welding Electrodes. |
| AWS TO 5.4 | For Specification Corrosion - Resisting Chromium and Chromium- Nickel Steel Covered Welding Electrodes. |
| AWS TO 5.5 | Specification for Low Alloy Steel Covered Arc Welding Electrodes. |

  - COATING OF PIPES

| American for Society Testing and Materials (ASTM) |  |
| --- | --- |
| ASTM D 49 | Dielectric Breakdown Voltage and Dielectric Strengths of solid Electrical Insulating Materials AT Commercial Power Frequencies |
| ASTM D 570 | Standard Test for Methods Water Absorption of Plastics |
| ASTM D 638 | Tensile Properties of Plastics |
| ASTM D 792 | Standard Test for Methods Specific Gravity (Relative Density) and for Density Plastics by Displacement |
| ASTM D 1000 | Pressure-Sensitive Adhesive Coating Tape for Used Electrical Insulation |
| ASTM D 1002 | Strength Properties of Adhesives in Shear by Loading Tension |
| ASTM D 1044 | Resistance of Plastic to Surface Abrasion |
| ASTM D 1921 | Standard for Test Particle Size (Sieve Analysis) of Plastics Materials |
| ASTM D 2370 | Elongation and Tensile Strength of Free Films of Paint, Varnish, Lacquer, and Related Products with to Tensile Testing Apparatus |
| ASTM D 3363 | Standard for Methods Test Hardness Film by Pencil Test |
| ASTM D 4217 | Standard for Method Test Gel Time of Thermosetting Coating Powder |
| ASTM D 5162 | Standard for Practice Discontinuity (holiday) Testing of nonconductive Protective Coating on Metallic Substrates |
| ASTM AND 96 | Standard Test for Methods Water Transmission Steam of Materials |
| ASTM G 6 | Resistance abrasion of Coatings Pipeline |
| ASTM G 8 | Cathodic Disbonding of Coatings Pipeline |
| ASTM G 14 | Impact Resistance of Coatings Pipeline |
| ASTM G 17 | Test for Method Penetration Resistance of Pipeline |
| American Society for Testing and Materials |  |
| AWWAC - 213 | For standard Fusion Epoxy inner for Coating and outer of Steel Water Pipelines |
| Canadian Standard Asociation |  |
| CAN/CSA - Z245.20 | Canadian Standard Association. External Fusion Bond Epoxi Coated Steel Pipe |

  - PAINTING

| Structural Steel Painting Council |  |
| --- | --- |
| SSPC SP2 | Hand Cleaning |
| SSPC SP3 | Power Tool Cleaning |
| SSPC SP5 | Blast Cleaning tp “White” Metal |
| SSPC SP10 | Blast Cleaning to “Near White” Metal |

  - INSPECTION AND TESTSOF EQUIPMENT

| American Society of Nondestructive Testing (ASNT) |  |
| --- | --- |
| SNT-TC-1A | Recommended Practice |
| American Society of Mechanical Engineers (ASME) |  |
| ASME PTC 46-1987 | Overall Plant Performance |
| ASME PTC 22-1997 | Performance Code Test on Gas Turbines |

  - INSPECTION AND TESTS OF CRANES AND EQUIPMENT OF HOISTING

| ANSI/ASME B30 | Safety for Standard cableways, cranes, derricks, hoist hooks, jacks and slings |
| --- | --- |
| ISO 9927 | Crane - lnspections |
| SAE J765 | Test of load stability. |

  - INSTRUMENTATION AND CONTROL

| CODELECTRA | National Electrical code |
| --- | --- |
| AGA | American Gas Association |
| NFPA | National Fire Protection Association, NFPA-70, 59A |
| ISA | Instrument Society ofAmerica, SP-5.1, RP-12.1 |
| API | American Petroleum Institute |
| SEALLING | National Electronic Manufacturer Association, CS-3 |
| ANSI | American National Standard Mechanical Engineers |
| ASME | American Standard Mechanical Engineers |
| IEEE | Institute of Electrical and Electronics Engineers |
| ASTM | American for Society Material Testing and |

  - ELECTRICITY

| Norms COBENIN 200 |  |
| --- | --- |
| COBENIN 200-99 | National Electrical code. |
| Norms of CADAFE |  |
|  | General norms for Projects of Lines of communication kV and 230 to 115 kV of CADAFE. |
|  | General norms for Projects of Substations of kV and 230 Transmission to 115 kV of CADAFE |
| Process Industry Practices Electrical |  |
| PIP ELSSG11 | Design and Fabrication of Electrical Power Center. |
| PIP ELSMC13 | Low-Voltage Circuit Motor Breaker Centers Control. |
| American National institute of Norms (ANSI): |  |
| ANSI C19.3 | Industrial General Apparatus Control |
| ANSI C19.6 | Industrial Apparatus Control, Control Circuit Devices and Assemblies |
| ANSI C37 | Breakers, Switchgear, Substations Relays and fuses. |
| ANSI C48-1 | Tensions Standardized for Systems and Equipment of Power. |
| ANSI C57.109 | Special Purpose for Couplings Petroleum, Chemical and Gas Industry Services |
| ANSI C57.13 | Requirements for Instrument Transformer |
| Institute of Electronic Electrical engineers and (IEEE) |  |
| IEEE, STD 141-1993 | IEEE Recommended for Practice for Distribution Industrial Plants. |
| IEEE STD 142-1991 | IEEE Recommended for Practice Grounding of Industrialist and Commercial Power Systems. |
| IEEE STD 446-1987 | IEEE Recommended for Practice Emergency and Standby Power Industrial for System and Commercial Applications. |
| IEEE STD 1100-1992 | IEEE Recommended for Practice Powering and Grounding Sensitive Electronic Equipment. |
| National association of Electrical Manufacturers (SEALLING) |  |
| SEALLING SG-4 | Power Circuit Breakers. |
| SEALLING SG-5 | Power Switchgear Assemblies. |
| SEALLING ICS-2 | Standards for Industrial Control, Devices Controllers and Assemblies. |
| Norms IEC (International Electrotechnical Commission). |  |
| IEC 34-1 | Recommendations for Rotating Electrical Machinery. |
| IEC 51 | Direct Acting Indicating Analogue Electrical Measuring Instruments and their accessories |
| IEC 185 | Current Transformers |
| IEC 186 | Voltage Transformers |
| IEC 269-1 | Low-voltage fuses. General requirements. |
| IEC 439-1 | Low Voltage Switchgear & Control to gear Assemblies. |
| IEC 521 | Class 0,5, 1 and 2 Alternating-Current Watt-hour Meters |
| IEC 529 | Degrees of protection provided by enclosures (IP Code). |
| IEC 664-1 | Insulation for Coordination Equipment within Low-Voltage Systems. Part 1.: Principles, Requirements and Tests. |
| IEC 688 | Electrical Measuring for Transducers Converting A.CIEC 947-2 Low-Voltage Switchgear and Control to gear. Part 2: Circuit-Breakers. |
| IEC 947-3 | Low-Voltage Switchgear and Control to gear. Part 3: Switches, Disconnections, Switch-Disconnections and Fuse-Combination Units. |
| IEC 947-4-1 | Low-Voltage Switchgear and Control to gear. Part 4: Contactors and Motor. Section One: Electromechanical Contactors and Motor. |
| IEC 60076 | Power Transformers |
| IEC 60137 | For Bushing Alternating Voltages stupefies 1000V. |
| IEC 60354 | Loading Guide Oil-inmersed Power Transformers |
| IEC 60551 | Measuring of Transformers and Reactors Sound Levels |
| IEC 60296 | Mineral Unsed Insulating Oils Transformers and Switchgear |
| IEC 60298 | MV and LVCubicle Switchboards |
| IEC 60076 | Power Transformers |
| IEC 60137 | For Bushing Alternating Voltages stupefies 1000V. |
| Association of Engineers of Cables Revestidos (ICEA) |  |
| Norm is 1.2-1974 | Seismic Testing of Motor Centers Control. |

  - CIVILIAN

| American Petroleum Institute |  |
| --- | --- |
| API RP 570 | Management of Process Hazards |
| API RP 752 | Management of Hazards Associated with Location of Process Plant Buildings. |
| ACI 318 | American Concrete Institute. |
| AISC | American Institute of Steel Construction |
| API | American Petroleum Institute |
| AWS | American Welding Society |
| ANSI | American National Standards Institute |
| ASTM | American Society of Testing and Materials |
| ASCE | American Society of Civil Engineers |
| UBC | Uniform BuildingCode |
| AASHTO | American Association of State Highwayand Transportation Officials |
| Venezuelan commission of Industrial Norms (COBENIN): |  |
| COBENIN 2002 | Criteria and Minimum Actions for the Project of Constructions |
| COBENIN 2003 | Action of the Wind on the Constructions |
| COBENIN 1756 | Sismorresistentes constructions |
| COBENIN 1753 | Structures of Concrete Armed for Constructions - Analysis and Design |
| COBENIN 1618 | Steels for Constructions, Project, Manufacture and Construction |
| COBENIN 2000 | Part I “Highways” |
| COBENIN 2000 | Part II “Buildings” |
| COBENIN 2000 | Part III “Hydraulic Works |
| COBENIN 1565 | Maximum levels of Permissible Noise in Work areas |
| COBENIN 2239 | Inflammable and Combustible materials. Storage and Manipulation. Part I Liquids |
| COBENIN 356 | Used Chemical additives in Concreto. Specifications |
| COBENIN 633 | Concrete Premezclado. Requirements |
| COBENIN 277 | Specifications for the Acceptance or Aggregate Rejection for Concrete |
| COBENIN 28 | Specifications for Portland Cement |
| COBENIN 316 | Specifications of Steel Bars with Projections for use like Structural Reinforcement |
| COBENIN 1022 | It enmeshes of Wire Electrosoldado Steel |
| COBENIN 344 | Method of Concrete Sampling of Fresh |
| COBENIN 338 | Method for the Elaboration, Cured and Test of Cylindrical Test tubes of Concrete |
| COBENIN 339 | Concrete. Method for the Measurement of Establishment with the cone of Abrams. |
| COBENIN 3400 | Waterproofing of Constructions |
| COBENIN 1755 | Code of Practices Standardized for the Manufacture and Construction of Steels. |
| COBENIN 656 | Pipes for Served Water Systems nonPressurized, Ventilation and Rainwater |
| COBENIN 633 | Concrete Premezclado. Requirements. |
| COBENIN 334 | Tubes of Concrete. Test of Three Edges. |
| COBENIN 333 | Tubes of Concrete without Arming for Use in Systems of Sewage system without Pressure |
| COBENIN 1704 | Manufacture of Cones and Ring of Concrete for Mouth of visit in the System of Sewage system. |
| COBENIN 1705 | Meetings for Pipes of Concrete for use in Systems of Sewage system Using Empacaduras de Goma |
| MINDUR-1985 | Manual for the Project of Structures of Concrete Armed for Constructions”. |
| MOP-1967 | Manual of Drainage |
| MTC-1983 | Road drainage |
| INOS-1989 | Norms for the Project of Aqueducts and Sewage systems |
| INOS-1979 | Urban drainage |
| Official newspaper Nº 4.044. - 08/09/88 | Project Construction, Repair, the Reformation and Mantenimiento de Edificaciones”. |

  - VENEZUELAN ENVIRONMENTAL LEGISLATION

| General atmosphere |  |
| --- | --- |
| Official newspaper Nº 31.004. - 06/06/76 | Statutory law of the Atmosphere |
| Official newspaper Nº 4.358. - 03/01/92 | Penal law of the Atmosphere |
| Official newspaper Nº 4.358. - 25/04/96 | Norms on Environmental Evaluation of Activities Susceptible To degrade the Atmosphere. Decree 1.257 |
| Official newspaper Nº 5.079. - 19/07/96 | Norms on Collections for the Environmental Evaluation of Programs and Projects of Miners and Exploration and Hydrocarbon Production, Resolution 56 |
| Official newspaper Nº 4.358. - 03/01/92 | Urban drainage |
| Official newspaper Nº 4.044. - 08/09/88 | Project Construction, Repair, the Reformation and Mantenimiento de Edificaciones. |
| Environmental quality |  |
| Air |  |
| - 196/05/95 | Norms on quality of the Air and Control ofla Contaminación Atmosféricas, Decree Nº 638 |
| - 04/09/98 | Norms on Emissions of Movable Sources, Decree 2.673 |
| Official newspaper Nº 36.594. - 02/12/98 | Norms Regarding Certification of Originating Emissions of Movable Sources, Resolution 334 |
| Official newspaper Nº 37.217. - 12/06/01 | Regulation of the Air, Decree no. 1.235 |
| Official newspaper Nº 37.217. - 12/06/01 | Approving law ofla Enmiendaof the Protocol of Montreal, regarding the Exhausting Substances ofla Capaof Ozone. |
| Water |  |
| Official newspaper Nº 5.021. - 18/12/95 | Liquid normsla Clasificaciónfor and the Decree, Quality control of the Water Bodies and Spills or Effluents no. 883 |
| Official newspaper Nº 5.568. - 31/12/01 | Statutory law stopsla Prestaciónof the Services of Potable Water and Cleaning |
| Official newspaper Nº 36.298. - 24/09/97 | Sanitary norms for the Location, Construction, Protection, Operation and maintenance of Perforated Wells Destined for the Potable Decree, Water supply no. 691 |
| NonDangerous remainders |  |
| Official newspaper Nº 4.418. - 27/04/92 | Norms for Manejo de Desechos of origin Domestic servant, Commercial and Industrial or of any other Nature nonDangerous, Decree no. 2.216 |
| Official newspaper Nº. 35.229. - 09/06/93 | National system of Recycling, Treatment and Final Disposition of Industrial Residues, Decree no. 2.961 |
| Noise |  |
| Official newspaper Nº 4.418. - 27/04/92 | Norms on Control ofla Contaminación Generadaby the Noise, Decree no. 2.217 |
| Norms regardingla Ejecuciónof Works |  |
| Official newspaper Nº. 35.206. - 07/05/3 | Norms on Earthwork and Environmental Conservation, Decree no. 2.212. |
| Official newspaper Nº. 4.418. - 27/04/92 | Environmental norms forla Aperturaof Goads and Construction of Access roads, Decree no. 2.226 |
| Official newspaper Nº. 4.418. - 27/04/92 | Norms To regulate the Activities Able To bring about Changes of Flow, Obstruction of Channels and Problems of Sedimentation, Decree no. 2.226 |
| Natural resources |  |
| Resources Forest-Vegetation and Hídricos |  |
| Official newspaper Nº. 997. - 08/01/96 | Forest law of Grounds and Water |
| Official newspaper Nº. 27.981. - 09/03/66 | Edition of Forest Law of Grounds and Waters, No.078 Resolution |
| Official newspaper Nº. 27.565. - 10/10/64 | Partial Water andla Ley ForestalGround regulation, Decree no. 156 |
| Official newspaper Nº. 2.022. - 28/04/97 | The Partial Reformation of the Regulation of Forest Law of Grounds and Waters, Decree no. 2.117 |
| Official newspaper Nº. 34.273. - 01/08/89 | National Ground advice, Decree no. 369 |
| Official newspaper Nº. 34.808. - 27/09/91 | The Partial Reformation of the Regulation of Forest Law of Grounds and Waters exceedsla Repoblación Forestalin Loggings, Decree no. 1.657 |
| Official newspaper Nº 3.182. - 19/05/83 | Procedural norms of the Partial Water andla Ley ForestalGround Regulation, Resolution no. 491 |
| Official newspaper Nº 36.013. - 10/02/97 | Norms onla Regulaciónand the Control of the Advantage of the Hydric Resources and the Hydrographic River basins. Resolution no. 1.400. |

  - STATUTORY LAW OF THE WORK

| Official newspaper Nº 5.152. - 19/06/67 | To govern the Situations and Legal Relations Derived from the Work like Social Fact. |
| --- | --- |

  - STATUTORY LAW OF PREVENTION, CONDITIONS AND ENVIRONMENT OF WORK

| Official newspaper Nº 3.850. - 18/06/86 | Statutory law of Prevention, Conditions and Environment of Work. To guarantee the Workers, Permanent and Occasional, Conditions of Security, Health and Well-being, in an Atmosphere of Suitable and Propitious Work for the Exercise of its Physical and Mental Faculties |
| --- | --- |

  - REGULATION OF THE CONDITIONS OF HYGIENE AND SECURITY IN THE WORK

| Official newspaper Nº 1.899. - 26/08/76 | To establish Norms on Conditions of Hygiene and Industrial Security, Obligatory Fulfillment for Employers and Workers. |
| --- | --- |
| - 31/01/07 | Partial regulation ofla Ley Orgánicaof Prevention, Conditions and Environment of Work |

  - OBLIGATIONS CONTAINED IN NORMS ON HYGIENE

| Official newspaper Nº 36.395. - 13/03/98 | Resolution M.S.A.S Not 18. “Sanitary Norms On Quality of the Potable Water” |
| --- | --- |

  - SYSTEM OF UNITS OF MEASUREMENT

| Official newspaper Nº 2.823. - 14/07/81 | System of Units of edidas of the Legal System Venezuelan International System of Units (IF) |
| --- | --- |
| Venezuelan commission of Industrial Norms (COBENIN): |  |
| 288-93 | (ISO 1000-92) System of Units of measurement and Recommendations for Uso of its Multiples and other Units (1ra. Revision) |

  - SECURING OF LA CALIDAD

| Venezuelan commission of Industrial Norms (COBENIN): |  |
| --- | --- |
| COVENIN-ISO 9000:2000 | Of Vocabulary and systemsla Calidad. FundamentosManagement |
| COVENIN-ISO 9001:2000 | Systems of Management of the Quality. Requirements |
| COVENIN-ISO 9004:2000 | Systems of Management ofla Calidad. Directricesforla Mejoraof the Performance. |

- GENERAL CONDITIONS

- The applied criteria for design, manufacture, inspection and test that they will be due to apply to all the systems, materials, equipment and accessories including in Alcance of the WORK, will have to correspond to safe, proven practices and with successful experience, established on the base of the codes, norms and specifications indicated in Numeral 3. Proven designs will only be accepted previously.

- The strict fulfillment with the engineering specifications does not release to the CONTRACTOR of its responsibility to use methods safe, proven and based on good practices of engineering and construction. Therefore, the CONTRACTOR will be forced to repair, to modify or to replace, without additional cost forLA COMPAÑÍA, any defective component, with deficient engineering, inspected, installed and/or inadequately nonappropriate for the specific application and described conditions of operation in his particular specifications or documents of reference.

- The CONTRACTOR will be able to suggest criteria or procedures alternative, different from the indicated ones in the particular and general specifications, that according to their experience are in an improvement from quality and/or reduction from costs or time from delivery. The alternatives technical and will be economically justified for approval on the part of LA COMPAÑÍA.

- The CONTRACTOR in the preparation of his supply will have to include all the necessary technical requirements that they allow to guarantee technical integrity, trustworthiness, availability, mantenibilidad, security, hygiene and atmosphere of all the facilities including within the IPC, even though specifically have not been indicated in these engineering specifications.

- The CONTRACTOR is in the obligation to certify the fulfillment with all the specifications and to present/display a list of exceptions, there are if them, for revision and approval on the part ofLA COMPAÑÍA. Todasthe exceptions they will have economically to be listed and to be justified technically and. If any exception to these specifications is not clarified on the part of the CONTRACTOR before the company/signature of the CONTRACT, it will be considered that the contracted reach of execution will fulfill the same. Therefore, any omission of this nature on the part of the CONTRACTOR will not justify additional costs forLA COMPAÑÍAand will force the CONTRACTOR to satisfy all the engineering specifications exactly.

- The precedence between documents Data sheets, Specifications and Norms will be the following one:

- The Contract

- These specifications

- Particular specifications

- General specifications

- International and National norms of reference

- In a possible conflict associated to the previous precedence, the CONTRACTOR will have to immediately notifyLA COMPAÑÍAand asking for a clarifying one before presenting/displaying his Supply. The CONTRACTOR will have to receive the solution assumed byLA COMPAÑÍAin writing and as soon as possible.

- The general and particular diagrams, planes and engineering specifications are in agreement and they are mutually complemented, to verify discrepancies between mentioned documents,LA COMPAÑÍAwill define the one that prevails and the CONTRACTOR will be forced to accept it without it generates a cost additional stops LA COMPAÑÍA.

- Where they stipulate themselves, registered or manufacturing marks or names, or in the Planes or the engineering specifications are due to understand that such mention is made like reference to define the quality or norm of quality of the material required byLA COMPAÑÍAbut that the CONTRACTOR will be able to present/display other products for the approval of the ENGINEER OF the PROPRIETOR, whenever these are of equal or better quality and fulfill the specifications and the indicated norms, all this without a modification to the Unit costs and/or the Total Amount of the CONTRACT is originated.

- INFORMATION OF the SITEand location of la parcela

LA PLANTAit is located in the South-east of the Margarita island in the Marine Municipality. In the figures 6.1y 6,2 is the location of the same and the parcel selected withinLA PLANTAfor the installation of the new units, which occupies an area approximated of1.600 m2forming a polygon of four (04) sides.

Figure 6.1. Location ofla Planta LuisaCáceres de Arismendi

Figure 6.2. Parcel of location of the New Turbogeneradoras Units

  - INFORMATION METEREOLÓGICA

The meteorological conditionses of the zone and the area of established influence of the project as design base is defined by the official sources authorized andorganisms and as minimum they are defined:

- Room temperature average

- Room temperature maximum average

- Room temperature minimum average

- Relative humidity average

- Relative humidity maximum average

- Relative humidity minimum average

- Maximum wind speed of design

- Predominant direction of the wind

- Annual average precipitation total

  - SEISMIC CONDITIONS

For all referring to the analysis and the sismorresistente design the norms COBENIN - FUNVISIS 1756-2001 will be followed. For the zone where it is locatedLA PLANTA, they apply the following main parameters:

- Seismic zoning:                    5

- Level of Design: ND3

- Horizontal acceleration:                 0,30 g

- Vertical acceleration:                     0,20 g

- TEMPORARY FACILITIES AND SERVICES STOP LA OBRA

It will be responsibility of the CONTRACTOR to execute all provisional works and facilities necessary to obtain the good performance ofLA OBRA, including without being limited it, the deposits, clothes, the lighting system, the electrical force, the toilets/baths, the white waters, the waters on watch, the black waters and any other service that according to the CONTRACTOR considers necessary so that the construction activities are executed fulfilling the norms and existing governmental decrees in the matter of industrial hygiene and atmosphere.

LA COMPAÑÍAone reserves the right to inspect directly or through third parties, the physical state and the provisional conditions of operation of all the facilities, works, the machineries, the equipment, the vehicles and the tools of work provided by the CONTRACTOR for the execution of LA OBRA.

LA COMPAÑÍAit will not replace any construction, service or temporary installation.

The CONTRACTOR will be the unique responsible being by the preparation, the construction, the operation, the maintenance of the work and storage areas, the services, the offices, the factories, the sanitary facilities and the other provisory works that can be needed for the executionLA OBRA, including particular studies, works and services for the transport, the storage, the conservation, the manipulation, the repair, the desensamblaje, the protection, the disassembling and the disembarkation of ordinary or special transports, of the equipment heavy, and voluminous.

The CONTRACTOR will have, as she leaves from the reach, to provide, to install, to maintain and to remove all the necessary provisional facilities for the complete and satisfactory execution of the WORK. The type of facilities, the dates of installation and retirement, as well as the site of location in the place of the WORK, must be put under the revision and approval ofLA COMPAÑÍA.  Acontinuation the temporary facilities and facilities are indicated that, like minimum, will have to be provided by the CONTRACTOR:

For the power supply of the load a reliable system is required that guarantees the continuity of the service of electrical energy as well as the quality of the provided energy (smaller variations of tension to 5% and smaller variations of frequency of 2%).

The CONTRACTOR will have to undertake all the works necessary to replace the demand indicated for temporary facilities during the construction ofLA AMPLIACIÓNand/or installing his own temporary generation; the costs associated by the use of the service will be responsibility of the CONTRACTOR.

The CONTRACTOR will have to carry out the final cleaning ofLA OBRA, as well as the demolition and the removal of civil works and electrical provisional weathers and/or, assuring that the area it is totally free of necessary and incidental residues, rubbish, wastes, materials, equipment for the final cleaning and the repair from all the defects of construction and damages to the existing facilities, as well as cleaning, transport, and boat of any remainder, weeds, trunks of wood, drums, papers and leftover construction equipment, existing in the occupied area.

- HIRING MODALITY

The WORK object of this licitation will be contracted under the modality of GLOBAL SUM during the use of the CONTRACT.  The CONTRACTOR will have to supply: PORTION in U.S. Dollars, by the consumptions, materials, services (transport among others), insurances and manpower of foreign origin and PORTION in Bolivars, by the component of materials, equipment, services (transport among others) and manpower of national origin. The fixed and firm prices that settle down in the previous paragraphs, will have to include each and every one of the costs and administrative expenses, as well as estipendio of the CONTRACTOR to execute the WORK.

The games corresponding to Spare parts, Special Tools and technical and professional Training, will have to be supplied by the CONTRACTOR under the modality of Unitary Prices.

All the payments to the CONTRACTOR will be based according to the indicated thing on Numerals 23.2.1., 23.2.2., 23.2.3., 23.2.4 and 23.2.5 of these specifications.

The monetary units to which the supply will be due to refer will be: strong Bolivar for the originating and/or acquired goods and services inla República Bolivarianaof Venezuela and the Dollar of the United States of North America (US$) like currency of reference for the acquired or contracted goods and services abroad.

Specifically he is agreed thatLA COMPAÑÍAwill not accept any type of claim based on the variation, alteration or modification of the exchange parity between currencies. LA COMPAÑÍA the execution of the WORK in the currencies will pay in which the Supply has been presented/displayed.

The modification in the prices originally quoted, will only be admitted, when the same obey to Decrees and Governmental Laws, that according toLA COMPAÑÍAindeed affect the hiring.

- IT REACHES OF LA OBRA

The reach includes the development ofla Ingeniería Básicaand of Detail, It tries, Inspection and Transport to the site, Construction, Precommissioning, Commissioning, Tests of Good Starting and Beginning, of the systems and facilities necessary to obtain the construction and putting in NORMAL OPERATION of three (03) units of generation of electrical energy of approximately 22.6 MW (ISO) each with turbines to gas of simple cycle, last technology, simple, combustible axis dual (Gas and Oil Distillate Nº 2), with low emission of NOx. All the costs corresponding to nationalization, taxes, insurances and guarantees demanded in these specifications comprise of the reach of the WORK and will have to be including by the CONTRACTOR in the amount of their Supply. The generated net power will be given to the system of transmission in 115 kV of EDC, by means of the connection of the elevating transforming generator ELTs of 13.8 power kV/115kV in LA PLANTA.

The CONTRACTOR will be responsible to execute the assembly, installation and/or construction of all those parts and/or components, as well as of the execution of all the works that were necessary, in order to guarantee the complete operativity ofLA AMPLIACIÓN, contemplating without being limited it the mechanical, civil, electrical completación and of instrumentation of all the systems and processes described in these specifications.

The CONTRACTOR will have to review the information provided byLA COMPAÑÍAand together developing with the documentation and planes of construction elaborated by the SUPPLIER,la Ingeniería Básicaand of necessary Detail for the installation and assembly of the set of systems, equipment and materials that conform LA AMPLIACIÓN.

The equipment and systems that next are indicated conformLA AMPLIACIÓNand constitute the reach of global of the WORK.

  - STUDIES OF CHARACTERIZATION AND ENVIRONMENTAL IMPACT

The CONTRACTOR will execute the studies of characterization and Environmental impact whose global reach is transformed in the following main activities:

    - TOPOGRAPHICAL SURVEY

The CONTRACTOR will realize the topographical survey of the sector where the generators will be placed and will elaborate the corresponding planes. Once concluded, the CONTRACTOR will have to warn in a maximum term of 8 days the ENGINEER OF the PROPRIETOR.

For electronic equipment like the System of Posición Global (GPS), the data of the rise will be due to print in leaves so large letter and Compact disc, according to is required, which will have to contain the data base taken in field, and the printed coordinates of the points in X, and Z, type txt numerically classifying each one of the CD, as well as leaves so large letter with all the information and observations that have been taken from the instrument.

In addition, one will be due to establish a horizontal control and another simultaneous vertical or following the instrument that is used for the accomplishment of the works of field, the tolerances for the GPS' precision s must consider in the Horizontal of 5mm ± 0.0000001 in the Vertical 10mm ± 0.0000002, that are the permissible maximum errors in common conditions for the accomplishment of these works.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 1,1 of the Nº.1 Annex of these specifications.

    - GEOTECHNICAL STUDY

The CONTRACTOR will make the Ground Study and will provide an evaluation of the nature of the subsoil and the geotechnical properties of the materials in the area, where it will be locatedLA AMPLIACIÓN, consequently will be able to be obtained the lifting capacity of grounds, to be determined the solution of foundation of the different structures to install and to be established the related necessary parameters to the earthwork, excavation and organization of terrain. And others.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 1,2 of the Nº.1 Annex of these specifications.

    - STUDY OF ENVIRONMENTAL IMPACT (EIA)

The CONTRACTOR will be responsible to realize the Study of Impacto Ambiental (EIA) which is a requirement indispensable settled down by the Ministry of the Popular Power for Ambiente (MINAMB) for all the projects of works and services that are executed in the national territory like previous step for the obtaining ofla Autorizaciónof Occupation of the Territory, Authorization forla Afectaciónof Recursos Naturales (AARN) and Authorization of Construction. Inla AARNthe MINAMB it establishes the conditions under which the affectation of the atmosphere will be developed during the stages of execution ofLA OBRA, adjusting in addition, to the program of measures and conditions established in the approved environmental evaluations. The results of this study, as well as of the measures and/or recommendations emitted inla AARN, to diminish or to mitigate the environmental impact in the phases of design, construction, operation and maintenance ofLA AMPLIACIÓN, comprise of documents to provide byLA COMPAÑÍAand will have to be of strict fulfillment on the part of the CONTRACTOR.

  - basic engineering and OF detail

With base in the information available provided byLA COMPAÑÍA, the CONTRACTOR will have to review the information and to develop the tasks, the activities and described essential products in the list indicated in the Annex 2 for each one of the disciplines, which is of orientative character, not limited. It will be responsibility of the CONTRACTOR to not yet elaborate all those planes and/or documents that are necessary for the completación ofLA OBRA, being the same including in the indicated listing.

It will be responsibility of the CONTRACTOR to notify toLA COMPAÑÍA, in diligent form and opportune, about any discrepancy, deficiency, omission or doubt, that they could arise during the execution of this phase ofLA OBRA. Asuch aimLA COMPAÑÍAwill have to authorize to the CONTRACTOR the possible changes and/or inclusions that will be to carry out.

The CONTRACTOR will present/display for his revision and approval the descriptive memory, memories of calculation, documents and planes of the project in the formats provided thereforeLA COMPAÑÍAin physicist like in digitalis.

The documents must be sufficiently clear, identifying design hypothesis, you formulate and equations used, qualities of the materials and any other requirement according to stipulate the School to it of Engineers of Venezuela.

If a commercial program is used it must provide the results so that they can easily be interpreted by the reviewer of the document.

Croquis, quarterings of the numbered reinforcement and any other instrument will be included that the revision of the project allows. Each system will be placed in the memory separately.

The planes will have sufficiently to be detailed and will have you cut, to views, numbered plants, quarterings, metric bills of material and calculations.

Separated planes for each one of the points indicated in this document will be executed, the planes would give to dubbings in plastic lining so large letter in white folder of three hoops with title page clearly identified. The documents will give in paper bond bases 20 so large letter on white folder three hoops with title page clearly identified.

All the documents and planes will have to be signed by a reliable associated professional.

The CONTRACTOR will have to realize all the here predicted activities for the definition and the most complete and exhaustive design than assures the construction and the satisfactory operation of all the functional sets of the WORK, having to include itself in principle, without being limited them, those that are indicated next:

The reach of works indicated in this document will not limit the CONTRACTOR of the fulfillment of the development of engineering in complete form and to satisfaction ofLA COMPAÑÍAproposing, recommending and improving aspects of which in his opinion it will result in the quality of the end item without this causes an additional cost stops LA COMPAÑÍA.

The new turbogeneradoras units will be installed with the characteristic of being completely apt to be handled from the existing Control center and this one will have the capacity to control the load and shutdown of remote form and will have to operate reliably and to be able to start from conditions of shutdown in cold, lukewarm and warms up. The starting, the operations in site and its safekeeping will be coordinated by a group of local operators according to the instructions of the Control center. With the provision of systems and equipment the CONTRACTOR will have to provide the minimum spare parts recommended by the manufacturer to object to at least guarantee the suitable operation of the components that integrate the System at issue, during the first five (05) years of operation.

The CONTRACTOR will have to provide to four (04) copies of the Manual of Operation and maintenance of each one of the Components that form part of each one of the Systems applicable to the Units of Generation, Table of Adjustments, Planes of Wiring, final Disposition of the Equipment and any other integral document of the implanted system.

The CONTRACTOR will have to provide all the materials, equipment, components, parts, pieces, manpower and tools necessary to object to realize the provision, installation, tests in factory, tests in field and putting in good condition of the Protection, Control system, Drive and Visualization, Interface Man Machine, as much for the local operation as remote, of each one of the Units of Generation.

They will be used, like reference, the documents of Basic Engineering and Detail that are listed in the Annex Nº 2.

The CONTRACTOR will have to put under, before initiating any action of Tries, Construction and/or Assembly, to the approval ofLA COMPAÑÍAand/or the ENGINEER OF the PROPRIETOR, all the planes, specifications and documents ofLA OBRAespecially with respect to: Plots Plan, P&ID and Single-wire, Flat of Hazardous areas, Flat Diagrams of Structures of Buildings Loaded with Traveling cranes, Planes of Bases of the Turbines and Generator, etc.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 2,1 of the Nº.1 Annex of these specifications.

  - GENERAL CIVIL WORKS

The civil works will be due to execute general whose reach is in this document without limiting itself it. It is responsibility of the CONTRACTOR to design all the civil works that are necessary for the correct operation ofLA AMPLIACIÓNhave even though not been named in this document.

The global reach of these works is transformed in the following main activities:

The CONTRACTOR will be the unique responsible being, the location, the preparation, the construction, the operation, the maintenance of the work and storage areas, of the services, the offices, the factories, the sanitary facilities and the other provisory works that can be needed for the executionLA OBRA, including particular studies, works and services for the transport, the storage, the conservation, the manipulation, the repair, the desensamblaje, the protection, the disassembling and the disembarkation of ordinary or special transports, of the equipment heavy, and voluminous.

The CONTRACTOR will have, as she leaves from the reach, to provide, to install, to maintain and to remove all the necessary provisional facilities for the complete and satisfactory execution ofLA OBRA. Eltype of facilities, the dates of installation and retirement, as well as the site of location in the place ofLA OBRA, must be put under the revision and approval of. LA COMPAÑÍA. A continuation the temporary facilities and facilities are indicated that, like minimum, will have to be provided by the CONTRACTOR:

- Medical facilities for the use of the employees in those places in which these are required. Its use is of obligatory use on the part of the personnel of the CONTRACTOR, subcontractors, as well as by the personnel of engineering, inspection and other activities associated with the development of LA OBRA.

- All the services for the offices of field, which include, without limiting itself it, the following thing: cleaning, general maintenance, services of clerks, services of document reproduction, services of mail (internal, national and international), grant of consumptions for offices, equipment of computation, etc.

- The deposits for materials and equipment, as well as factories and spaces for offices, with its corresponding grant of services.

- All the provisional structures, transport, system of disposition of solid and liquid remainders, systems of communication and radios, that are required during the execution of LA OBRA.

- All the medical services, of ambulance and medicine provision that is required.

- Services of protection and guard of the materials and equipment replaced by the CONTRACTOR or that has been given him byLA COMPAÑÍA, being the CONTRACTOR responsible for any damage or loss who undergoes any material, equipment of process, machinery for the construction, provisional pieces of spare parts, offices and other facilities.

- Dining rooms for the personnel ofLA OBRA, which will have to be protected and to be furnished to act their as suitably. It is responsibility of the CONTRACTOR to maintain these areas in optimal conditions of cleaning and hygiene.

- Also it will have to include temporary offices for use of the ENGINEER OF the PROPRIETOR (amount of considered people 10), which will have to fulfill the norm COBENIN 200 and to count, like minimum, with the following facilities:

- All the services for the offices of field, which include, without limiting itself it, the following thing: cleaning, general maintenance, services of clerks, services of document reproduction, services of mail (internal, national and international), grant of consumptions for offices, equipment of computation of last technology, printers, scanner, etc.).

- Systems of communication and radios, that are required during the execution of LA OBRA.

- Medical facilities, with all the provisional structures, transport and system of disposition of solid and liquid remainders.

    - PRELIMINARY OPERATIONS

They include/understand:

- The mobilization of the heavy machineries, vehicles and other equipment and accessories property of the CONTRACTOR until the site of the WORK, and its demobilization, once finalized the works.

- The provisional construction of all the works, facilities, facilities and services necessary to obtain the good performance of the WORK.

- The cleaning of the area affected by the construction.

- The topographic reframing of the works.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,1 of the Nº.1 Annex of these specifications.

    - FOUNDATIONS FOR MECHANICAL OR ELECTRICAL EQUIPMENT

Foundations of the vertical and/or horizontal equipment will have pedestals of concrete armed. The metallic plates of the anchorages will be contracted within the concrete one and the edges of the pedestal will be it bevel.

The foundation level will be the established one by the Ground study to realize by the CONTRACTOR.

In case it is a set of near foundations, a rigid pavement around the same was placed separating the pavement of the pedestals by means of together stuffed with asphalt material. In the case of isolate foundations perforated stone with a minimum thickness will be placed around of10 centímetros.

The leveling of the equipment would be realized by means of mortar of leveling 0% retractable Sika or similar

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,2 of the Nº.1 Annex of these specifications.

    - Quarter OF BOARDS

A house of structure of concrete will be contemplated armed conventional with ceiling of concrete plane with sobreslope of 2% like minimum, peripheral railing, bajantes of rainwater metallic entamboradas doors, guinea fowl with enamel and blocks of ventilation type blind. With sufficient area like lodging electrical boards of the project. Walls of block of concrete frisados both faces, painting of rubber and waterproofing asphalt mantle 3mm with painting red color. The foundation slab will be executed according to the indications of the ground study

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,3 of the Nº.1 Annex of these specifications.

    - TANQUILLAS

Tanquillas of concrete will be armed with fused iron cover heavy or light according to they are placed in site where it exists or nontransit of vehicles.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,4 of the Nº.1 Annex of these specifications.

    - LARGE STONE BENCHES OF POWER, COMMUNICATION AND CONTROL

It includes the construction of large stone benches and tanquillas for loss and high voltage located according to planes of routes and details to be developed in the phase of Engineering of Detail.

The large stone benches to construct will serve to undertake the telephone force, illumination, services, instrumentation and control from each one of the systems ofLA AMPLIACIONto the substation and control room, the works include without limiting themselves them:

- Large stone benches of tubes for illumination.

- Large stone benches of tubes for control and instrumentation.

- Large stone benches of tubes for electrical distribution in low tension.

- Large stone benches of tubes for electrical distribution in high voltage.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,5 of the Nº.1 Annex of these specifications.

    - DEMOLITIONS

The CONTRACTOR will be in charge to demolish or to dismantle any type of construction or structure that is prevents the works in agreement with the requirements of the project the ENGINEER OF the PROPRIETOR will be the one who determines the destiny of the material product of the demolitions of concrete, rubblework or finished, indicating the places in that it will have to be deposited. Unless the opposite has remembered specifically, all the originating materials of the demolitions and/or dismantlings are property of the COMPANY.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,6 of the Nº.1 Annex of these specifications.

    - RECONSTRUCTIONS AND/OR EXTENSIONS

The CONTRACTOR will be in charge to reconstruct or to extend the existing foundations in case she requires therefore itLA COMPAÑÍAor to reconstruct the demolished elements. For it he will have to fulfill the general requirements of design and construction and will retire the rubbish and residues of leftover materials. In the case of extension of foundations, the surface to extend will have to be completely clean thus to be able to unite the concrete one of different ages with the suitable product.

If the PLANT were required to extend a sector inside that is surrounded, close it will be of the same characteristics of the existing one in the same

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 3,7 of the Nº.1 Annex of these specifications.

  - PACKAGE OF GENERATION

    - INSPECTION, INSURANCES AND GUARANTEES OF TURBOGENERATORS TO GAS

LA COMPAÑÍAit will provide to the CONTRACTOR three (3) turbogenerators to gas and its auxiliary modules, of General technology Electric, model GE LM2500 of 22.6 MW of capacity each to conditions ISO (14.7 psia; 59º F; 60% relative humidity), with guarantee of the Manufacturer.

LA COMPAÑÍAit is committed to provide to the CONTRACTOR the following documents for the three (3) turbogenerators to gas and its auxiliary modules:

- Copies certified of the equipment, materials parts and/or components, which will be emitted by a specialized company and of international recognition.

- Copies certified of the different executed programs of maintenance to date.

- GUARANTEE of the effective Manufacturer for the moment of company/signature of the CONTRACT.

- Technical-commercial documentation certified (unprice Copy) and/or legalized to facilitate the mobilization and transfer from the place where they are stored the turbogenerators, to the site designated for the WORK.

The CONTRACTOR will have to make sure by:

- To inspect the physical state of the turbogenerators to gas and its auxiliary modules

- To verify quality and special amount of the inventory of parts, components, spare parts and tools including in the provision.

- To receive fromLA COMPAÑÍAall the technical documentation corresponding to planes of installation and assembly, manuals of operation, maintenance and service.

The CONTRACTOR is in the obligation to certify fulfillment with all the specifications and to present/display a list of exceptions, there are if them, for revision and approval on the part ofLA COMPAÑÍA. Todasthe exceptions they will have to be listed and to be justified technical and economically and will have to be supplied under the figure of REIMBURSABLE EXPENSES. If any exception to these specifications is not clarified on the part of the CONTRACTOR before the company/signature of the CONTRACT, it will be considered that the contracted reach of execution will fulfill the same. Therefore, any omission of this nature on the part of the CONTRACTOR will not justify additional costs forLA COMPAÑÍAand will force the CONTRACTOR to satisfy all the engineering specifications exactly.

The CONTRACTOR will have to assume the integral responsibility by the terrestrial and marine transport, studies of routes for the mobilization of the equipment in national territory, costs of insurances, guarantees, nationalization, taxes and other expenses from the site where to the turbines to gas and the auxiliary modules are located, until the determined place as site of the WORK, Also will have to include in their supply the costs associated tola Asistencia Técnicaof the Manufacturer for the installation, assembly and tests of the turbines to gas that guarantee the successful operation of the units.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 4,1 of the Nº.1 Annex of these specifications.

    - TRANSPORT, INSTALLATION AND INTERCONNECTION OF TURBOGENERATORS TO GAS

The installation and interconnection of the Turbogenerators to gas, have as it reaches the execution of all the activities of transport, assembly, civil, mechanical, electrical construction, tests and inspection, of instrumentation and control necessary to carry outla COMPLETACIÓN MECÁNICAof the Turbogenerators and to guarantee its operation like individual unit, assuring its functional integration with all the associated systems LA PLANTA.

For the installation of the turbogenerators to gas, the CONTRACTOR will have to follow the instructions and recommendations settled down by the SUPPLIER or Manufacturer and will have to count on the specialized human resource that guarantees the safe and correct installation of the units.

The CONTRACTOR will have to take the forecasts for the suitable unpacking from the equipment and being required, to carry out the return of the parts of special packing to his proprietor.

The CONTRACTOR will have to present/display the Plan of Execution of the WORK in which in good condition she indicates the activities associated to the installation and putting of the turbogenerators.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 4,2 of the Nº.1 Annex of these specifications.

    - TRANSFORMING TRANSPORT AND INSTALLATION OF POWER 13.8 kV/115KV

LA COMPAÑÍAit will provide the elevating transforming of associated power of tension toLA AMPLIACIÓNthat they will be installed by the CONTRACTOR.

The transforming will be three-phase of 13.8 kV like side of low tension and 115 kV in the side of high voltage. The frequency will be of 60 Hertz. and they will have a approximate additional capacity of 25% with forced ventilation (ONAF) of two stages. With each transformer a game of lightning rods will be provided and installed.

For the installation of the transforming, the CONTRACTOR will have to follow the instructions and recommendations settled down by the SUPPLIER or Manufacturer and will have to count on the specialized human resource that guarantees the safe and correct installation of the units.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 4,3 of the Nº.1 Annex of these specifications.

  - CONNECTIONS TO EXISTING SYSTEMS

    - CONNECTION TO THE SUPPLY APPARATUS OF FUEL

The new turbogeneradoras units to being installed, are of dual characteristics, that is to say can use liquid fuel or combustible gas. The CONTRACTOR will have to leave all the connections necessary why later the combustible gas feeding can be realized.

Like first option, he will be used liquid fuel, oil distillate Nº 2, which will be provided from the house of pumping of tanks 1, 2 and 3 ofLA PLANTA, by means of a pipe of 3 “of diameter until the limit of battery defined byLA COMPAÑÍA(to see Annex 3). Of this point in future the CONTRACTOR will have to develop all the activities of engineering, tries, assembly, civil, mechanical, electrical tests and inspection, of necessary instrumentation and control for the feeding and the suitable operation of the new turbogeneradoras units that guarantee the operation with liquid fuel of all the systems associated to the turbogenerators to install, also will have to consider in the design the connection for the future operation with combustible gas.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,1 of the Nº.1 Annex of these specifications.

    - CONNECTION TO THE WATER SYSTEM ON WATCH

The connection to the water system on watch, has as it reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection that they guarantee the suitable water provision on watch required byLA AMPLIACIÓNfor his operation…

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,2 of the Nº.1 Annex of these specifications.

    - CONNECTION TO THE WATER SYSTEM DESMINERALIZADA

The connection to the desmineralizada water system, has as it reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection that they guarantee the suitable desmineralizada water provision required byLA AMPLIACIÓNfor his operation.

The desmineralizada water system will have to be determine the proportions with the capacity sufficient to reduce the emissions of NOx of the units to the levels allowed by the Regulations Environmental and/or defined by LA COMPAÑÍA.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,3 of the Nº.1 Annex of these specifications.

    - CONNECTION TO THE SYSTEM AGAINST FIRE

The connection to the system against fire, has as it reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection that they guarantee the suitable operation of the system against fire required by LA AMPLIACIÓN.

The system against fire will have to be determine the proportions to cover the following areas withLA AMPLIACIÓN:

- The units turbogenerators to gas will be protected by a system against own fire of each unit, according to norms of the manufacturer.

- Size the portable fire extinguishers and appropriate class, will be located in agreement with NFPA 10 and Venezuelan regulations, throughout the facilities.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,4 of the Nº.1 Annex of these specifications.

    - CONNECTION TO THE TREATMENT SYSTEM AND DISPOSITION OF INDUSTRIAL EFFLUENTS

The connection to the system of treatment and industrial water disposition, has as it reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection that they guarantee the suitable operation of the treatment system and disposition of industrial effluents required by LA AMPLIACIÓN.

All the generated effluents will be collected, the contaminated waters with oil and chemical compound they will be isolated and lead by means of channels closed until its connection with the existing system, this separation also will be applied for the case of the rainwater.

The drainage system will be conformed by a network of harvesting of the drainages of equipment and originating potentially contaminated rainwater of the area of processes, that will be taken until the connection with the present system.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,5 of the Nº.1 Annex of these specifications.

    - CONNECTION TO THE COMPRESSED AIR SYSTEMS

The connection with the existing systems of compressed air for instruments and services ofLA PLANTA, has as it reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection that they guarantee the suitable operation of the compressed air systems required by LA AMPLIACIÓN.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 5,6 of the Nº.1 Annex of these specifications.

  - ELECTRICAL SYSTEM AND CONTROL

    - SYSTEM OF DAMPING OF ELECTRICAL DISTURBANCES

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection, that they guarantee the suitable operation of the system of damping of electrical disturbances required by LA AMPLIACIÓN.

The CONTRACTOR will have to provide all the materials, equipment, components, parts, pieces, manpower and tools necessary to object to realize the installation, and put in good condition of a system of damping of electrical disturbances.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,1 of the Nº.1 Annex of these specifications.

    - CONNECTION TO CONTROL ROOM

The CONTRACTOR will have to provide all the materials, equipment, components, parts, pieces, manpower and tools necessary to object to realize the installation, and put in good condition of general the electrical systems (Undertaken main and of the system of signals to assure functional integration with the systems associated toLA AMPLIACIONwith the located existing systems in the control room.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,2 of the Nº.1 Annex of these specifications.

    - FACILITIES FOR ELECTRICAL EQUIPMENT

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, construction, tests and inspection necessary to undertake the electricity works, which are without limiting themselves it:

- Foundation for transforming of auxiliary services according to the location planes, Route of Conductors and Large stone benches to be defined in the phase ofla Ingenieríaa to develop.

- Provision and installation of Switchgears of average tension, according to final requirements of provision and construction to be defined in the phase of Engineering of Detail and according to final requirements of provision and construction to be defined in the phase ofla Ingenieríaa to develop.

- Board provision and installation of distribution of power according to final requirements of provision and construction to be defined in the phase ofla Ingenieríaa to develop.

- Transforming provision and installation of Power, according to final requirements of defined provision and construction to being defined in the phase ofla Ingenieríaa to develop.

- Any other activity that being indicated is not necessary to carry out the correct installation and beginning of the equipment and systems.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,3 of the Nº.1 Annex of these specifications.

    - SYSTEMS OF EARTHING

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, construction, tests and inspection necessary to undertake electricity works, the verification of enmeshes of earthing ofLA PLANTA, arranged all over the same, and the identification of the points of connection as well as the interconnection of the points of earthingLA AMPLIACIONand its equipment to the existing earthing.

The CONTRACTOR will provide and install the system of earthing of all the equipment of LA AMPLIACION.

They are included, without limiting itself it, the execution of the following works:

- Exothermic connections in enmesh main and for derivations to the equipment and the metallic structures.

- Connections apernadas in the bars of earth, boxes of equipment, carcazas of transforming and boards.

- The CONTRACTOR will strictly follow the instructions of the manufacturer with respect to the execution of the exothermic connections, the storage of the powder cartridges and the amount of exothermic connections that can be executed with a mold.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,4 of the Nº.1 Annex of these specifications.

    - SYSTEM OF FEEDING AND DELIVERY OF ENERGY DC OF THE GENERATION UNITS:

The CONTRACTOR will have to evaluate the system of feeding and delivery of energy DC to the New Units of Generation and to provide all the necessary manpower, materials and equipment for the provision, installation, tests in field and putting in good condition of the banks of batteries, shippers of batteries, investors and other equipment, components and accessories of the system of feeding DC of the New Units of Generation in case of being necessary.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,5 of the Nº.1 Annex of these specifications.

    - SYSTEM OF ELECTRICAL PROTECTIONS

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection forthe verification and elaboration of coordination of protections forLA AMPLIACIONand its equipment.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,6 of the Nº.1 Annex of these specifications.

    - EXTERNAL LIGHTING SYSTEM

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, construction, tests and inspection necessary to install external lighting system of the EXTENSION.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,7 of the Nº.1 Annex of these specifications.

    - integration of signals to the DISTRIBUTED CONTROL SYSTEM

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection for the verification and elaboration of the integration of signals ofLA AMPLIACIONthe control system distributed existing of LA PLANTA.

The existing system will have to control and to acquire the necessary data of the units of generation through an interconnection I/O hardwired with the local control system, independent of the functions of control, operation and visualization of graphs realized through same, located in each unit of generation and through the interphases of Man-machine operation provided for the configuration and operation of the units of generation of combined or simple cycle and BDP. The alarms generated by the generation units will appear in the summary pages of alarms of the DCS with the printings of time placed by the control system.

The communication by means of the interphases of communication will be due to guarantee (Hardware and Software) to integrate with the control systems of equipment package (PLC).

The interconnections between the different control systems from the different control areas, will have to be superfluous and highly reliable, as well as adapted to fulfill the requirements of the control of the processes.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,8 of the Nº.1 Annex of these specifications.

    - INTEGRATION OF SIGNALS TO THE DETECTION SYSTEM AND FIRE ALARM

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection for the verification and elaboration of the integration of signals ofLA AMPLIACIONthe system of detection and existing fire alarm in LA PLANTA.

The system of detection of fire and gas (F&G) will be due to integrate to the existing system from a control unit or board against fire based on microprocessor, fulfilling all the specifications and certifications according to are the case of application. The equipment and the operation of the F&G will have to be totally independent of the control systems and unemployment of LA PLANTA.

The system of detection and fire alarm must have characteristics of tolerance of faults, distributed processing, tensile and modular, with programmable logic to facilitate the integration of functions to gas and fire and will have to provide facilities of serial communication to interconnect itself with the DCS, of form to alert in the control room and the defined zones ofLA AMPLIACION, any event, as well as the actions that has taken the system from automatic form.

The system of detection and fire alarm will have to maintain the following minimum requirements functional:

- La Interfaz with the Operator it will have to include the following thing:

- Indication of normal operation/fails of the complete system.

- Alarm and indication norm/fail for the detectors of fire and gas.

- Audible alarms.

- Recognition of Visual alarms and Audible.

- Indication of functions of “bypass” to conduct maintenance battle.

- All the operations also listed will have to be available in the DCS.

- In case of fire detection, the system will generate alarms automatically, as much in the panel of F&G like in the DCS, will activate the system against fire for the affected zone.

- In case of gas detection within confined spaces, the F&G will generate alarms in the panel of F&G and consoles of operation of the DCS, according to will be determined in the Analysis of Risks.

- All the signals and alarms will be transmitted to the DCS through protocol Modbus or Ethernet TCP/IP. The signals of fire and gas will be supervised continuously (for intentions of operation and maintenance) and will generate alarms in the operation stations, for the purposes of which the operator can take the respective actions. The recognition of the warning devices could be realized so much from the panel of the System of F&G like from the DCS.

- The F&G will detect conditions of danger (inflammable gases and fire) as soon as it is possible and it initiates preventive actions, such as the generation of pre-alarms and alarms in operation consoles, and generates field alarms audible as as much visual.

- The signals that execute blocking and opening of valves in the DCS will have to physically be twisted.

- The detectors of Fire and Gas must have suitable means that allow a easy calibration, besides being able to realize self-diagnoses and report of faults. The self-diagnosis will be able to detect open circuits or short circuits in the wiring of any signal of input/output.

- The design will allow car-I check of the complete system. It will be possible to prove the final elements in response to the sensors without needing carrying out shutdowns in the equipment that is being protected nor to interrupt the normal operation of the rest of the system.

- The configuration of redundancy and voting of the CPU and the exits of the F&G, for the activation of the control actions in case of detecting a fault, will be defined in the Analysis of Risks.

- Isolation (galvanic optician or) of the entrances and logouts will be due to have.

- The control board of the system of detection of fire and gas must count like minimum with the following functions:

- Signal of alarm.

- Signal of supervision.

- Signal of fault.

- Switch to silence audible signal of problem.

- Button to silence alarm with recognition functions.

- Switch to silence the supervision signal.

- Button of alarm reestablishment.

- The control board of the system of detection of fire and gas must receive signals of:

- Fire detectors.

- Gas detectors.

- Stations alarm manuals.

- Switches.

- Systems of unloading (example: clean agent, deluge).

- Any other equipment of extinction.

- The control board of the system of detection of fire and gas must send signals of:

- Systems of unloading.

- Systems of suppression.

- Any other system of extinction.

- As far as the Zones of Fire and Gas:

- The CONTRACTOR will provide to the devices of detection and indication according to specified in the table “the Zones of Fire and Gas” which will be developed duringla Ingenieríaa to develop.

- They will have to be able to work in conditions of humidity and temperature according to the climatic parameters without needing environment adjustment.

The software of the system will have to allow:

- To add notes to the logical stairs.

- Edition in-line/out of line of the functions of the logic.

- Aid in line.

- Compiler integrated for functions of high level.

- Protection with password selective access and protection.

- Programming with blocks functions applicable to security.

- Methods of verification of the memory integrity.

- Atmosphere for the development of special functions, specific blocks of function and programs for applications outposts of tolerant control to faults.

- Functions of control for specific applications; for example, routines of self test, calibration cards for gas detection and advanced control.

- Interrogation of the system.

- Changes of control and the user dated and hour.

- Configuration be-of-line, simulation and test of the application of the control programs.

The modules of the System must provide a standard design with such form that stays the same appearance of the System.

The System will have to be able to communicate with the DCS ofLA PLANTAand as the System of Shutdown of Plant. The CONTRACTOR will have to provide all the Hardware and necessary Software for this communication.

The communication Link could be implemented through gateway of dedicated communication.

The communication Link will have to be safe so that any bad operation in the DCS and the System of Shutdown of Planta (SPE) does not affect the correct operation of the F&G. All the ports of communication will have electrically to be isolated.

The F&G will have to be connected to the DCS in form like this one can “read” data in the F&G. The information that will be transferred from the F&G and the DCS through this Link of communication, without limiting itself it, will be the following one:

- Status of alarms and diagnoses of the system.

- Status of elements field input/output.

- Signals of Shutdown of Emergencia.

- Sequences of events with time printings.

The System will be designed to have a capacity of reserve installed of 20% in points input/output in modules, consumption of power, wiring of signals, end points, for future expansions.

One will have a 20% space of reserve within the cabinets to the incorporation of modules and chassis to future expansions. The power supply will have to be adapted to support those reserves.

It will be had a 40% of reserve of the capacity of software (capacity of processing of the CPU).

All the entrances and exits of reserves will have to be twisted to the terminal strips of exit.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,9 of the Nº.1 Annex of these specifications.

    - Integration TO the SYSTEM OF PLANT SHUTDOWN

The CONTRACTOR has as she reaches the execution of all the activities of engineering, tries, necessary construction, tests and inspection for the verification and elaboration of the integration of signals ofLA AMPLIACIONthe system of shutdown of existing plant in the PLANT.

The basic functions of the System of Shutdown of Emergencia (SPE) will have to be implemented under design type fails safe of Superfluous Modular Triple technology. The System will have to maintain the following minimum requirements functional:

- Capacity to support to redundancy and logic of sequences.

- Remote firing of valves and equipment of process.

- Interphase of serial communication with DCS.

- Interphase of serial communication with the F&G.

The CONTRACTOR will have to indicate the philosophy of redundancy of his system, modality and structure, loss of any functionality of the system in modality of “back-up”. This will have to be indicated for all the parts of the system.

The modules of the System must provide a standard design with such form that stays the same appearance of the System.

One is due to guarantee the basic functions of the System of emergencia shutdown to implement in integration with the existing system.

The System of Shutdown of emergencia will be mounted in a provided standard cabinet of key, of double access, for atmosphere use under conditioned air SEALLING 12 like minimum, the finished one will be of good quality and will have to be of the autosoportado type

The cable entrance will have to be in the base of the cabinet. It must have sufficient space free and accessible to fit and to finish all the cables; each cabinet must have its clips and the rails of support for the wiring. These cable entrances must have removable covers, fixed with Rep to us and its empacaduras. The edges of these entrances will have smooth and to be cleared.

The terminals will have to be organized in blocks. The entrance signals will have to be separated of the exit signals

All internal wiring will have to be perfectly identified in both ends indicating Tag of cable/Points of connection. For the written identification they will be due to use marquillas Thermus with indelible red.

The minimum size of the cables that will be used within the cabinet will be the indicated ones next:

- 120 VAC	#12 AWG.

- 24 VDC		#14 AWG.

The color code used for the internal wiring of the cabinet will be the following one:

- 120 VAC: (Phase) Black; (Neutral) White.

- 24 VDC: (Positive) Red; (Negative) White.

- Land of security: Green/Yellow.

- Land of Instrumentation: Green.

All the cables will be flexible of braided copper.

All the wiring will have to be in ducto portacable of plastic with removable cover. Ducto will have to be determine the proportions with a 50% of capacity of reserve with respect to the finished wiring.

The equipment will also try on separately and in integrated form. The instructions of tests and diagnosis of the original manufacturers of the equipment, as well as additional tests designed by the CONTRACTOR will be followed, mainly to verify the correct interconnection of the parts.

Special attention in demonstrating that will be had the dual criterion of configuration for the modules is fulfilled input/output of the system (configuration “Activates” and “Hot Spare”) and to the fact that the fault of one of these components does not harm the rest of the system.

This game will have to be supplied by the CONTRACTOR under the indicated GLOBAL EXTREME modality in numeral 6,10 of the Nº.1 Annex of these specifications.

- SPARE PARTS

The CONTRACTOR will have to settle down according to his better judgment the materials, necessary for the execution of the TESTS OF GOOD OPERATION and for the “COMMISSIONING” and STARTING of materials and replacedLA AMPLIACIÓN. Estosconsumable spare parts and will have to be including within the reach of the WORK and quality similar to the installed ones in LA AMPLIACIÓN.

The CONTRACTOR will have to include in his supply the necessary spare parts for the NORMAL OPERATION ofLA AMPLIACIÓNfor a period of two (2) years, as of the Act of PROVISIONAL ACCEPTANCE.

This game will have to be supplied by the CONTRACTOR under the modality Unitary Prices by line indicated in numeral 7 of the Nº.1 Annex of these specifications, beingLA COMPAÑÍAwith the option of the partial or total purchase of the same.

- SPECIAL TOOLS

The CONTRACTOR will have to present/display a list detachhed with necessary the special tools for the ordinary maintenance and the operations of each one of the systems that conformLA AMPLIACIÓN. Lastools will have to be new, without use and will have to enjoy the same guarantees of the materials and equipment covered in the reach with LA OBRA.

This game will have to be supplied by the CONTRACTOR under the modality Unitary Prices by line indicated in numeral 8 of the Nº.1 Annex of these specifications, beingLA COMPAÑÍAwith the option of the partial or total purchase of the same

- TRAINING

The CONTRACTOR will have to include in his supply, a plan of training for the personnel ofLA COMPAÑÍAwhich she will operate and realize the plan maintenanceLA AMPLIACIÓN., Elwill be directed to a group of engineers, breadwinners and operators, who will receive the training using like basic tool the simulators, the material of support like manuals, planes, diagrams and all the necessary one to guarantee a good qualification. Inla Ingenieríaa program of training with minimum requirements will be due to present/display.

This game will have to be supplied by the CONTRACTOR under the modality Unitary Prices indicated in numeral 9 of the Nº.1 Annex of these specifications,LA COMPAÑÍAwith the option of the partial or total purchase of the same.

- PLANES APPROVED FOR CONSTRUCTION

The CONTRACTOR will have to carry out definition of the more complete and exhaustive design so that the construction, the operation and the maintenance of all the equipment and components, as well as of the functional sets ofLA OBRA, can be realized of satisfactory way; having it to generate all the documents and planes that are required to such aims. In particular, the elaboration of the Approved planes “for Construction” will be responsibility of the CONTRACTOR, based on which the respective phase will be carried out, anticipating in this sense the accomplishment of consultations to manufacturers and suplidores with the intention of optimizing the design of the facilities and the equipment.

- PLANES “LIKE CONSTRUCTED”

It will be responsibility of the CONTRACTOR to giveLA COMPAÑÍAto all the information of manufacturers, salesmen and/or subcontractors, as well as the “Planes like Constructed”, which will have to be elaborated by the CONTRACTOR according to the final conditions of execution ofLA OBRA, including underground structures and normally nonvisible parts of this such as the internal details of the containers.

- SUPPORT A LA PROCURA

Each and every one of the equipment and systems to be acquired forLA OBRAthem will be due to elaborate the corresponding engineering specifications, which will have to go accompanied by a list by manufacturers or the suggested SUPPLIER, previous technical evaluation.

The company of engineering of the CONTRACTOR will have to give necessary the technical support in order that all the revisions, clarifying are carried out and certifications to that there will be place during the phase of Try, of form so to assure that all the equipment, parts and components to be acquired and that are integral part ofLA OBRA, they fulfill the engineering specifications and respective norms of quality.

- FIELD ENGINEERING

The company of Engineering of the CONTRACTOR will have to give necessary the technical support in order that all the clarifying and certifications to that are carried out there will be place during the phases of construction and completación of the WORK, to assure that all the works and works to be executed during these phases, including the assembly and installation of equipment, is realized according to the specifications, of way to guarantee the STARTING and Beginning, as well as the complete operativity of the WORK.

- SPECIFICATIONS TRY FOR IT

The execution of the activities will be responsibility of the CONTRACTOR that settle down next without being limited them. In this senseLA COMPAÑÍAand/or the ENGINEER OF the PROPRIETOR will have frees and opportune access to the factories and depots of the CONTRACTOR, as well as of the manufacturers or suplidores that participate in the execution ofla Procuraof the WORK.

The CONTRACTOR will be responsible by the purchases, revision and approval of documents of engineering of the manufacturer, insurances, streamlining (Expediting), source inspection, packing, securing and quality control and transport, load, reception, nationalization from the arrival to Venezuelan port, liberation of customs, transports until the site of the WORK, storage, conservation and permanent control of all the equipment and materials and consumption required for the execution and beginning of the WORK, as well as of the provision of the parts of spare part that consider for the STARTING and the recommended ones for two (2) years of operation necessary, with the previous one and due approval byLA COMPAÑÍA. Asísame, will include within its costs and responsibilities, studies of routes for heavy or special loads, permissions before the official beings in order to assure the fulfillment with all the responsibilities before indicated.

In case provided faults or defects of anyone of the equipment, materials or accessories, or of the realized services for the execution of the WORK are detected, the CONTRACTOR will determine the optimal way to correct such faults or defects. In any case the CONTRACTOR will have to protect the interests ofLA COMPAÑÍA, demanding the compensations that are deserved on the part of the local, selling and/or manufacturing contractors, anticipated in the orders of purchase or respective contract.

The CONTRACTOR will have to give, jointly with the equipment, the manuals, planes, documents, certificates of quality, tests and guarantees that are required byLA COMPAÑÍAas it leaves from documents object of the WORK.

The CONTRACTOR like part of the technical information, will have to provide to the licenses by at least 2 years and/or the software required or recommended by the manufacturers for the control, simulation and evaluation of the processes and for the activities of maintenance.

It will be responsibility of the CONTRACTOR to carry out any reclamation fromLA COMPAÑÍAwhich he arose as a result of the occurrence of faults or defects that deserve the change of equipment, card replacement or components; protected these by the respective guarantees.

LA COMPAÑÍAthe right is reserved to approve or to disapprove the purchase and/or the use of equipment, materials, parts of spare parts and/or components whose manufacturers do not fulfill the anticipated norms of quality for the execution of the WORK.

  - ACCEPTANCE TESTS IN MAKE

The CONTRACTOR will be responsible beforeLA COMPAÑÍAby the execution for the Acceptance tests in Factory. The intention of these tests will be individually to verify that the main equipment that conforms the facilities contemplated for the EXTENSION, fulfill the parameters established by the international manufacturers, norms and better practices.

The Acceptance tests in Factory will take place in agreement with the procedures and recommendations of the manufacturers, to the international norms that apply to each one of the equipment in test and according to indicated in the specifications in the numeral referring to tests and the inspection of the SUPPLIER.

The Acceptance tests in Factory of the control system and supervision ofLA AMPLIACIONmust cover all the aspects related to the equipment, which includes so much the software and the hardware of the electronic equipment, like the auxiliary equipment (cabinet, system of energy, wiring, accessories, etc.) and its assembly. One is due to demonstrate that the system fulfills all the specifications of design including in this document.

Especially, the results of activation of sequences and control actions in function will be validated in these tests originating signals to have simulated itself like of field, anticipating itself that deviations do not have to exist majors to 0.1% between both values.

Also it will be object of special attention, the verification of the time of calculation under conditions of maximum variability of the conditions of field, simulated for the aims of the tests.

The detailed procedures for the accomplishment of the Acceptance tests in Factory, will have altogether to be given to the ENGINEER OF the PROPRIETOR with the documentation required, at least four (4) weeks before the execution of the tests. The ENGINEER OF the PROPRIETOR will be able to suggest modifications to the procedures provided by the SUPPLIER, in case of considering it necessary. Similarly, the ENGINEER OF the PROPRIETOR reserves the right to reject in his totality the proposed protocol, providing his own protocol to the SUPPLIER, that is commited to use it and to be in force by exposed there.

The SUPPLIER will have to notify the ENGINEER OF the PROPRIETOR, at least with two (2) weeks of anticipation, the availability of the equipment for the execution of the Acceptance tests in Factory. The tests do not have to be initiated until each component of the equipment has not been proven satisfactorily by the SUPPLIER.

The SUPPLIER will have to provide the documentation that certifies that the system has been proven satisfactorily, according to its internal procedures, including any type of fault that has been detected during the execution of these tests. The Acceptance tests in Factory will be carried out in the facilities of the SUPPLIER.

The SUPPLIER will have to provide unrestricted access to the ENGINEER WITH the PROPRIETOR or the representatives designated byLA COMPAÑÍAa any installation where operations of manufacture, inspection or test of the components within the provision reach take place. Additionally, the SUPPLIER will have to provide to the ENGINEER OF the PROPRIETOR the documentation of engineering that is required to support any applied particular procedure.

The ENGINEER OF the PROPRIETOR reserves the right to reject materials, equipment or parts that have not fulfilled the requirements of quality control and criteria established in these specifications, according to they consider the results of the certificate revision and/or atestiguamiento of inspection or tests. The ENGINEER OF the PROPRIETOR will have faculties to demand the applicable necessary corrective measures, that they include repair, substitution of components, paralyzation and/or repetition of works.

The SUPPLIER will have to give all the collaboration necessary to facilitate, in the security aspects, hastens and effectiveness, the implementation of the observations that the ENGINEER OF the PROPRIETOR considers opportune for the attainment of the requirements of these specifications, during the execution of any test or inspection.

The SUPPLIER will have to notify in writing and with sufficient anticipation to the ENGINEER OF PROPIETARY on the date of accomplishment of the tests and the inspection in which its participation has remembered.

  - TRANSPORT AND STORAGE OF MATERIALS AND EQUIPMENT OF LA OBRA

- The CONTRACTOR will be the unique person in charge of the design, manufacture, packing, studies of routes, permisologías and mobilization of equipment, including heavy and special transports until the site of the WORK, the installation and/or construction, inspection and beginning, as well as of the care and guards until the PROVISIONAL ACCEPTANCE, of all those equipment, materials and accessories and systems that constitute the WORK.

- The materials and equipment acquired within the reach of the WORK will have to be protected and to be stored in safe sites, and climatic conditions of temperature and humidity, fit to the requirements stipulated by the manufacturers. Any deterioration by negligence or inexperience in the handling and storage of the materials will be of the absolute responsibility of the CONTRACTOR.

- The CONTRACTOR will have to plan and to jointly coordinate with the corresponding authorities the transfer of the equipment that is transported and/or by sea aerial, in national territory and from the port of debarkation to the specified site ofLA OBRA. Enthis sense, the CONTRACTOR will have to carry out a “Study of Routes” with the purpose of to review the routes to follow, the bridges, the passages to unevenness, etc., of way to verify that they fulfill the established thing with respect to capacity, heights, loads, etc. and to take the necessary precautions. The CONTRACTOR will be responsible for any adjustment of the route for the transport and any damage caused to the road during the operations of transport of equipment, reason why the repairs to that there will be place will be executed to their expenses.

- The CONTRACTOR will have to construct in site, a warehouse for the deposit of all the materials and equipment covered in the reach of the WORK, as she indicates herself in Numeral 8. of this specification, “Temporary Facilities and Services forla Construcción”.

- SPECIFICATIONS STOP LA CONSTRUCCIÓN

The CONTRACTOR will be responsible to execute the assembly, installation and/or construction of all those parts and/or components, as well as of the execution of all the works that were necessary, to guarantee the complete operativity of the WORK, contemplating without being limited it the mechanical, civil, electrical completación and of instrumentation of all the systems and processes described in this specification.

The CONTRACTOR will have to include to his own cost and risk and of putting under the approval ofLA COMPAÑÍA, all those, equipment, materials and/or components that explicitly will not be identified in the Annexes before indicated and that they were necessary for the total completación of Works of Electromechanical, Electricity and Instrumentation.

Also the CONTRACTOR will be responsible by the delivery for all the technical information and operational; manuals of operation and maintenance, certificates of tests and materials; elimination of all the pending points; execution of the required tests and the cleaning of the affected areas; liberation and/or compensation of damages to third parties; assuring the deliveryLA AMPLIACIONin totally acceptable conditions of operativity, security, maintenance and environmental impact.

  - MACHINERIES AND TOOLS OF CONSTRUCTION.

The CONTRACTOR will have to provide all the machineries, the required materials, equipment, accessories and tools, as well as vehicles to carry out the works of construction of the WORK, not being causal of delay in the execution of the respective works, faults or defects in no of the cases before described. It will be responsibility of the CONTRACTOR the provision of all the consumptions, consumable and services required for the operation of these, which will have to be in perfect conditions of operation and will be of the capacity and indicated horsepower for the type of realized work.

The CONTRACTOR will have to make sure that all the travelling cranes (heavy land industrialists, all land, on truck and tracks), cranes porch on tires, traveling cranes, heavy trucks, light equipment of hoisting, freight elevators, vehicles, and tools of work, are registered letter, previous the beginning of the WORK, by personnel or national or international organism, properly credited that certifies the general conditions of operation, the structural mechanical part of the equipment and the related one to the operative tests of rise: test of load and stability and the qualification of the operating personnel of the machineries. The certification of the mentioned equipment will have, at least, to fulfill the norms established in Numeral 3.7. “Inspection and Tests of Cranes and Equipment of Hoisting”. During the use of the contract, these equipment must be certificates every year.

LA COMPAÑÍAone reserves the right to inspect directly or through third parties, the physical state and the conditions of operation of all the machineries, equipment, vehicles and tools of work provided by the CONTRACTOR for the execution of the WORK.

  - TECHNICAL PERSONNEL STOPS LA CONSTRUCCIÓN

The CONTRACTOR will have to make sure that the operators of the equipment indicated in Numeral 11,1, as these specifications, are described to operate this type of machines. Norm ASME/ANSI B30.5, establishes the obligatory nature of the certification for the crane operators, as well as the mechanisms of evaluation to obtain the corresponding qualification. This certification will have to be realized by personnel or national or international organism, properly credited that the suitability of the operators for this type of operations certifies.

Also, it is of obligatory fulfillment on the part of the CONTRACTOR to make sure that the technical group of personnel of the different specialties properly is described, according to the level and classification the work to realize and count on a certification or evaluation that credits its capacity, knowledge and skills in the work to carry out in the WORK.

  - NATIONAL AND FOREIGN TECHNICAL ATTENDANCE

The CONTRACTOR will have to make sure to count on described national and foreign technical attendance that guarantees the execution, assembly and tests according to the recommendations of the Manufacturers and to the established thing in these specifications.

For the specific case of the turbogenerators to gas, the CONTRACTOR will have to count onla Asistencia Técnicaspecialized of the Manufacturer for all the activities of installation, assembly, tests and beginning.

- INSPECTION, VERIFICATIONAND TESTS

  - GENERAL REQUIREMENTS

The procedures of inspection, verification of installation and test in site will have to be in agreement to the codes and norms indicated in Numeral 3. of these specifications. The deviations will have to be clarified by the CONTRACTOR for revision and approval on the part of LA COMPAÑÍA.

The conditions and procedures of inspection, verification and tests will have to be made by the CONTRACTOR. The CONTRACTOR will have to provide to the record formats of the traffic control points and inspection of installation, as well as of the operative variables to being used during the test in site, for revision and approval on the part ofLA COMPAÑÍAand/or the ENGINEER OF the PROPRIETOR, previously to his execution.

The CONTRACTOR will specify the type and reaches of the verifications, tests and inspection that will be applied to the materials, equipment and accessories of the installed systems, as well as after them inspection and verifications of installation and after the tests of mechanical operation and conditions of process in site.

  - CERTIFICATION OF MATERIALS AND NON-DESTRUCTIVE INSPECTION

The CONTRACTOR will have to certify the mechanical and chemical properties of the materials of manufacture of the mechanical components, equipment and accessories of the different installed systems, identified by serial number or lot of production.

The welds of made elements will have to be subject to x-ray inspection. The inspection report will have to show the type, size, axial and angular location of all the found indications, along with the rejection and defect acceptance numbers.

All the inspection of END of the pipe welds, executed by the CONTRACTOR forLA COMPAÑÍA, will fill to the requirements of Norms ANSI/ASME B31.1 “Power Piping” and API 1104 “Welding of Pipelines and indicated Related Facilities” in Numeral 3,3, of these specifications.

All the inspection by END of welds in storage caves, carried out by the CONTRACTOR forLA COMPAÑÍA, will fill the requirements ofla  Norma  API650, “Welded Steel Tanks for Petroleum Storage”.

All the inspection by END of pipes of plants executed by the CONTRACTOR for the COMPANY, will fill the requirements of ANSI B31.1, “Power Piping”. All the circular welds of plant pipe will be put under on approval nondestructive in all their circumference, except the welds of prefabricated units which are excluded from any non-destructive testing, it authorizes unless it specifically LA COMPAÑÍA.

  - CERTIFICATION OF HYDROSTATIC AND/OR PNEUMATIC TESTS

The hydrostatic test of the containers under pressure will be executed according to the established thing in the ASME Code Section VIII, Division 1. The test will have to be executed in factory, according to the procedure of the manufacturer, previous revision and approval byLA COMPAÑÍA. Enno case will be due to test to conditions inferiors to the demanded ones in the ASME Code Section VIII, Division 1.

In cases in which the construction and/or final assembly of the equipment must be realized in field, the final hydrostatic test will have to be realized in the site and the CONTRACTOR will have to provide to the detailed procedure of the test for the revision and approval of LA COMPAÑÍA.

The CONTRACTOR, will have to certify that all the containers under pressure provided for the WORK have been proven hydrostatically and that they fulfill to satisfaction the requirements established in code ASME Code Section VIII, Division 1. Also the CONTRACTOR, will have under pressure to certify the fulfillment to satisfaction of all the tests of the installed systems of pipe in field, according to the indicated thing in paragraph 137 of ASME CODE FOR PRESSURE PIPING, B31 AN AMERICAN NATIONAL STANDARD.

  - CLEANING

Suitable cleaning of the materials, equipment and accessories of the installed systems is mandatoria before the MECHANICAL COMPLETACIÓN. The cleaning of the pipes and elements will have to be verified before the final assembly and certified by the ENGINEER OF the PROPRIETOR. The CONTRACTOR will have to implement securing measures to avoid the entrance of strange objects to the interior of the different elements after they have been verified and until the completion from the process of final assembly.

  - INSPECTION AND VERIFICATIONS OF INSTALLATION

The CONTRACTOR will have to carry out all the inspection and verifications necessary to certify that the installation of the components of the different installed systems, as well as the required ones for their interconnection, fulfill these specifications, the particular specifications and the general specifications ofla OBRA, before coming with the execution of Tests in Site.

  - TESTS IN SITE

The CONTRACTOR will be responsible before the ENGINEER FOR the PROPRIETOR by the execution of the Tests in Site. The intention of these tests is to verify individually that all the equipment that conforms the facilities contemplated forLA AMPLIACIONis apt to start and to operate with the availability required in this specification.

The clarifying one becomes of which some requirements of tests indicated in the particular specifications talk about to tests in factory. The CONTRACTOR will have to settle down the type and reaches required after the Tests in Site, in order to certify that the mechanical operation, the operation of the protection and control systems and the conditions of process guarantee are met stopsla COMPLETACIÓN MECÁNICAof LA AMPLIACION.

- ACCEPTANCE OF LA OBRA

The delivery and acceptance of the works executed by the CONTRACTORLA COMPAÑÍAwill become in the three following stages: MECHANICAL COMPLETACION, PROVISIONAL ACCEPTANCE and DEFINITIVE ACCEPTANCE, thus the COMPANY and the CONTRACTOR in mutual agreement will have to subscribe the corresponding Act.

- MECHANICAL COMPLETACION

For this activity the CONTRACTOR will follow his own practices and the best applicable international practices, as well as indicated in the norms and the codes of national and international reference.

The CONTRACTOR will have to present/display in writing toLA COMPAÑÍAa ahead month of the beginning of the phase of “PRECOMMISSIONING”, the detailed planning, the procedures and registries of verification that will be used for the same. LA COMPAÑÍA he will have the right to audit the corresponding documentation. The verification lists will have to be integrated by all the mechanical equipment (static and rotating), electrical and of instrumentation and control that next are indicated:

- Verification of which all the installed pipes and drainages are according to the planes and the corresponding DTI.

- Verification of the correct location and installation of the equipment, accessories and valves.

- Verification of the correct installation of the interns of the process equipment.

- Verification of the protection and control systems.

- Verification of the points of action of the safety valves.

- Verification of the manuals of Operation.

- Verification that the sluice valves correctly are installed with reference to the flow direction.

- Verification that the orifices correctly are installed

- Verification of the systems of lubrication in the rotating equipment.

- Registry of operation of rotating equipment: Pumps, motors, air compressors service, generators, turbines, etc.

- Verification of the Manuals of Maintenance.

The CONTRACTOR, before energizar or in good condition putting any equipment or system of wiring, will have to realize in the presence of the ENGINEER OF the PROPRIETOR all the settled down inspection and tests in these specifications, in the applicable norms and codes and those that to good the ENGINEER OF the PROPRIETOR asks for.

The CONTRACTOR will have to compile the test resultses and to elaborate a complete report on the condition of the conductors and equipment, which will have to present/display before asking for the acceptance of the WORK.

The acceptance of the WORK associated to the electrical systems will be submitted to the correct one and completes operation of the systems according to the specifications, planes and according to information provided by the manufacturers of the equipment.

The CONTRACTOR will have to adopt all the safety measures necessary to protect to the personnel at the time of realizing tests of isolation or some other in which they are present electrical tensions of another nature.

The tests of conductor insulation and equipment of low tension must take control of a measurer of maximum isolation of 500V and the condition of the element in test will be considered acceptable if the isolation is equal or greater from (1) a Megohm.

The boards of average power and low tension, as well as the control centers of motors will not have to be energizados under any circumstance before:

- To inspect and to prove all the associate switches

- To complete with satisfactory results all the tests of isolation.

Before energizar any system the CONTRACTOR will have to come to disconnect under the supervision of the ENGINEER OF the PROPRIETOR, the secondary conductors of the transformer that will provide with energy all the switches of referred boards, to realize tests of isolation of the bars and conductors of feeding to boards and to register the results.

Completed the tests of isolation to land of the bars of boards and the conductors of feeding to these, continuity of the neutral one of the transformer with the earthing of the board will be due to reconectar the secondary one of the transformer and to verify.

The CONTRACTOR, after verifying that the test resultses are satisfactory, will come to energizar the electrical system of lighting system and power outlet, to verify tension A stage phase, A stage neutral and energizar each circuit of the board to verify the ignition of all the lights and that exists tension in the power outlets according to stipulated here.

Once completed successful this test, the CONTRACTOR will have to verify the existence of the legend of identification of boards.

The completación of inherent the electrical systems and instrumentation toLA OBRA, will only take place after the CONTRACTOR has installed, proven and operated each one of the systems integrate that it, in agreement with the design specifications. The WORK will not be considered completes if some of the following points has not been realized to satisfaction of the ENGINEER OF the PROPRIETOR.

The CONTRACTOR will have to verify the following thing:

- All the electrical devices count on their corresponding identification.

- The electrical equipment are of dust or any other crud free.

- The painting of the equipment and electrical devices has been altered to correct any damage.

- The identification of the circuits in distribution boards is correct and it is in site.

- All the ends of electrical ductos of reserve count on appropriate corks.

- The system of electrical ductos has been wiring and counts on all accessories and elements of support.

- The connections of the system of earthing are adapted in number, location and quality.

- All the pending points that the ENGINEER OF the PROPRIETOR has reported previously have been resolved suitably.

- All the leftover materials have been given inventoried to the ENGINEER OF the PROPRIETOR properly

- Unless he defines himself of another one of way, for the completación of the works of electricity, the CONTRACTOR must have given:

- The planes “like constructed” with letter of acceptance of the same by the ENGINEER OF the PROPRIETOR.

- The calculation of all the materials and equipment installed and accepted, given by LA COMPAÑÍA.

- The calculation of all the materials installed and accepted, given by the CONTRACTOR.

- The calculation of all the materials and equipment, given byLA COMPAÑÍA, leftovers and recovered.

- To verify the electrical wiring. The CONTRACTOR will have to present/display certificates of continuity checks and of blinded and to guarantee that the conductors provide the power required to the Control Panel or Control Panels and to the corresponding equipment from the source of supply.

- To verify the interconnections fromLA AMPLIACIONthe rest ofLA PLANTAand electrical Substation.

- To certify the tests in field of all the following electrical equipment: relays, switches, transforming of power and measurement, as well as the certificates of aferición of the equipment of measurement of energy.

- Verification of the maintenance manuals.

- Individually calibrated verification that all the instrumentation of the equipment is working appropriately and with its respective certificates.

- Verification of all the bows of control ofLA AMPLIACION, from the instrument to consoles of operation, the premises and of the main control room.

- Verification of the warning levels of the instrumentation installed in the equipment.

- Verification of the conexionado one in each one of the analogical and digital boxes, as well as concerning: Distributed control system, System of Shutdown of Emergencia, System of Detection of Llama, PLC (the CAP), etc.

- Verification of the action of the interLock systems.

- Verification that the control valves correctly are installed with reference to the flow direction.

- Verification of calibration of lightening valves.

- Verification of installation of filters of enmeshes for the tests in the bridles of the lines of air of instruments to avoid the possibility of entrance of dirty that they can contaminate the registry of the new instrument.

- Verification of the Manuals of Maintenance

The CONTRACTOR once concluded and completed all the phases of: construction, “PRECOMMISSIONING”, program of training for the personnel ofLA AMPLIACION, gives of the manuals of Operation and maintenance and other requirements including in Alcance ofLA OBRA, will have to notify in writing toLA COMPAÑÍA, the date to carry out the company/signature of the MECHANICAL ACT OF COMPLETACIÓN. In the lapse of veintiún (21) days after receiving the notification of the CONTRACTOR,LA COMPAÑÍAit will have to inform to the CONTRACTOR if it finds some defect, it details to slope or incompletos works in writing and it will have to justify to the CONTRACTOR the reasons to deny the company/signature of the MECHANICAL Act of COMPLETACION. The CONTRACTOR will have to correct the defects notified byLA COMPAÑÍAand repeating the process of MECHANICAL delivery of COMPLETACION of the WORK, until obtaining the acceptance on the part of LA COMPAÑÍA.

LA COMPAÑÍAhe will decide to his single discretion the Partial Act emission of MECHANICAL COMPLETACION of the WORK.

Once signed and emitted Act of COMPLETACION MECHANICAL on the part ofLA COMPAÑÍA, will come within lapse from four (4) weeks with “COMMISSIONING” and STARTING ofLA AMPLIACIONwhich OPERATION will allow to realize TESTS OF GOOD, which must like intention determine the integral operation of all the systems ofLA AMPLIACION, level of security, efficiency, consumption of raw materials and of services industrial, Megavatios net Generated (Net Plant Power Output) and export of energy electrical to point of interconnection indicated in Alcance ofLA OBRA(conditional to the coordination that has decidedLA COMPAÑÍAwith the operating being of the SEN), rate of thermal consumption (Net Plant Heat Rate), rate of load taking, environmental tests of emissions and noise, as well as the level of operabilidad and trustworthiness ofLA AMPLIACION, in accordance with these specifications and other requirements of the CONTRACT.

- PROVISIONAL ACCEPTANCE

Like previous activities to the company/signature of the Act of PROVISIONAL ACCEPTANCE ofLA OBRA, the CONTRACTOR will have to put under the equipment and systems that constituteLA AMPLIACIONto final tests with the aim of verifying the operation, capacity, yield, flexibility and trustworthiness, in accordance with indicated in these specifications and established thing in the CONTRACT.

The final tests to take place before the STARTING and BEGINNING ofLA AMPLIACIÓN, and after to emit the MECHANICAL Act of COMPLETACION of the WORK, will have to be the following:

- Functional tests: they include the ARRANQUE tests (COMMISSIONING).

- TESTS OF GOOD OPERATION: they include the TESTS OF CAPACITY with respect to: Megavatios net Generated (Net plant to power output), efficiency, rate of thermal consumption (Net plant heat rate), rate of load taking, consumption of raw materials, environmental tests of emissions and noise.

- Test of Trustworthiness (Availability).

The Functional Tests will have to be carried out to assure the progressive and safe starting each one of the systems, to prove the integrity and functionality of the components ofLA AMPLIACIÓN, and to demonstrate that this one has been constructed to operate in whole agreement with the specifications and to provide the required functionality. At the end of the Functional Tests, the CONTRACTOR will have to be completely preparation to execute the TESTS OF GOOD OPERATION and Trustworthiness.

In the TESTS OF GOOD OPERATION, one will be due to demonstrate the good operation for each one of the installed systems, the safe, efficient and reliable operation ofLA AMPLIACIÓNand the fulfillment with the engineering specifications and the contractual terms of the CONTRACT. Also one will be due to try, that under the rank of normal operation ofLA AMPLIACIÓNthis fulfills the referring specifications to the noise, to the control of emissions and protection of the environment.

The Tests of Trustworthiness will be due to carry out satisfactorily once concluded the TESTS OF GOOD OPERATION. With these tests the capacity of exporting energyLA AMPLIACIÓNof continuous and reliable form to the National Electrical System will be due to demonstrate.

All the Functional Tests, of GOOD OPERATION and Trustworthiness, will be due to carry out with the instrumentation, equipment, tools and system of monitoring and controls available and installed inLA AMPLIACIÓN. Todatool or special instrumentation required to carry out these tests, including calibration elements, will be due to consider as it starts off of the provision and within Alcance of the WORK.

For the environmental tests and of noise, the instrumentation, equipment, tools and systems of monitoring and control will be due to use to the maximum available and installed inLA AMPLIACIÓN, but additionally they will be due to consider the use of tools and special equipment even though these do not comprise of the provision of LA AMPLIACIÓN.

The CONTRACTOR will have to integrate to the tests the own personnel of the PLANT, with the purpose of to train it in the execution of the tests, as well as to the manufacturer of the equipment and installed systems to technically support the development of the tests.

For all the tests a Plan of Management will be due to elaborate ofla Calidad, that will have to include the detailed, graphical procedures, photos, drawings, tables, detailed lists of verification and instructions.

For each test one will be due to elaborate a planning anticipated with reports and procedures, which will have to include the following minim information:

- Objectives of the test.

- Criteria, ranks and limit values of acceptance/rejection.

- Required personnel.

- Procedures, equipment and tools to use.

- Cronogram and sequence of activities in the time.

- Description of the conditions required for the test.

- Formats, tables, to use in the test.

- Taken data, registries, including examinations of laboratory, measurements.

- Ground visual aids, photos, videos, graphs and diagrams.

- Conducted calculations.

- Detailed results and commentaries.

In case of interruptions of the tests by external factors of greater cause or interruptions of fuel provision, the test will be reinitiated so soon is passed the condition, in the interruption point.

In case of interruptions of tests by defects or malfuncionamiento of the process or equipment, by causes imputable to the CONTRACTOR, the test will be reinitiated so soon is corrected the condition, in the point of beginning of the test.

  - FUNCTIONAL TESTS

The Functional Tests will be due to initiate once concluded the Tests of COMPLETACION MECHANICAL and signed the corresponding Act. The preparations and Functional Tests of ARRANQUE (COMMISSIONING) must have three (3) stages, that are the following:

- Preparations of the Functional Tests.

- Execution of the tests.

- Documentation and Certification of the tests.

The procedures of the tests will have to be realized according to the established thing in ASME PTC46, and/or ASME PTC 22.

The formation of a organizational structure for the Functional Tests of STARTING and the definition of the packages or systems of starting in early form will be required, including a detailed planning with the landmarks and required priorities, to reach the goals drawn up in the program of the WORK.

    - PREPARATIONS OF THE FUNCTIONAL TESTS OF STARTING

The work of the ARRANQUE preparations (COMMISSIONING) will have to contemplate the following activities:

- Preparation of Organization of STARTING, that will have to include to the personnel who will operateLA AMPLIACIÓN, and specialists of manufacturers of the main equipment.

- Definition of the STARTING of equipment and systems.

- Consumable planning of resources, personnel, materials, spare parts and for the starting.

- Preparation of the formats to use for the registry of the tests.

Which will have to include like minimum: for each system or package the corresponding identification, required schemes, items to verify, results, expected values, observed values, columns of observations, reference to registry, signature block of the executor and the witnesses, and date of the verification.

    - EXECUTION OF THE STARTING TESTS (COMMISSIONING)

The Tests of STARTING will have to consist of the functional and individual progressive verification of all the systems and main equipment, according to the STARTING manual, to guarantee that they fulfill the parameters of design and criteria of operation, and to verify their availability for the beginning of the Tests of STARTING of the equipment and the execution of the later tests.

During the STARTING of the equipment and Systems, the SUPPLIER representatives of or manufacturer with the object will be due to arrange in the site of the WORK to provide the required technical support.

They will be due to elaborate ready of verification, with tables for taking of data, each system. The tables of data will have to indicate the acceptable rank of operation for the systems and equipment.

Generally, all the indicated systems and equipment next will have functionally to be proven of progressive form:

- Turbogenerators and their Aids, including the protection and control systems.

- Control system Distribuido and Interlock.

- System of Shutdown of Plant.

- System of Detection and Fire Alarm.

- Control system Supervisorio, Transmission of Voice, Data and Telecommunications.

- Transformer of Power of 13.8 kV/115 kV.

- Transforming of Auxiliary Services of 13.8 kV/0,48 kV.

- Switchgears 13.8 kV, Boards of Force, TDP and Control centers of Motors

- Shippers of batteries, batteries and uninterruptible systems of power.

- Tests of STARTING of the units.

Once the CONTRACTOR has completed all the tests of STARTING and functions of remote control and supervision, each of these functions will have to be including in the bow tests, and given and accepted by the group of STARTING by means of a signed Act on both sides.

After the starting and the progressive stabilization of the individual systems, one will be due to come to the integral starting, in periods of test between 48 and 72 hours, being monitored the parameters of operation of the same, with all the automatic control systems in and coming to stop it to correct the problems that appear during these periods.

LA COMPAÑÍAthe right is reserved to add any Functional Test, that he is reasonable and it is notified to the CONTRACTOR with at least sixty (60) days before the beginning of the Tests of Trustworthiness and these will have to be considered like integral part of the CONTRACT.

    - DOCUMENTATION AND CERTIFICATION OF THE FUNCTIONAL TESTS AND DELIVERY OF INFORMATION

A preliminary report with the results of these tests will be due to emit forLA COMPAÑÍA, in a lapse nongreater to two (2) weeks after the tests. The CONTRACTOR will verify that the registered results have been signed and validated by the parts and that the repetition of any of these tests in regard to any contractual document will not be required.

The delivery will be due to carry out with formal procedures that will include like minimum the following thing:

- Act of Completación de Functional Pruebas of ARRANQUE (COMMISSIONING).

- Planes and documents with its final modifications including in the systems or packages of delivery (P&ID, single-wire etc.).

- Company/signature of involved governmental or municipal authorities, in case of being necessary (independent ministries, institutes, etc.)

  - TESTS OF GOOD OPERATION

The CONTRACTOR will have to carry out the TESTS OF GOOD OPERATION regarding the net capacity and thermal power consumption of the units with the aim of demonstrating that they fulfill themselves the contractual guarantees established in the engineering specifications and other contractual documents.

The CONTRACTOR will have to present/display a plan of total and partial development of tests ofLA OBRA, following the strategy of execution settled down in the Plan of Execution to provide jointly with la Oferta.

These tests are critics for the fulfillment of the requirements established in these specifications, and the maximum efforts will be due to make to fulfill the same. If the capacity net of the units, divided equally and corrected, determined by the test, is minor who required, or if the net efficiency of thermal power consumption, mediated and corrected, determined by the test, is major that the required one,LA OBRAit will be considered nonACCEPTABLE and the CONTRACTOR will have to make the modifications and corrections necessary to fulfill the settled down requirements.

The net capacity and thermal power consumption of the new units will have to be determined in agreement with norms ISO. To the tolerances and correction factors necessary to effect will be due to apply to compare with the Guarantees of OPERATION. For the individual system tests, the CONTRACTOR will have to emit a list with the standards that will be used of reference.

    - TEST EQUIPMENT AND CALIBRATION

All the devices of measurement will have to be appropriately calibrated before the tests, and the corresponding results and Acts will have to be available stops LA COMPAÑÍA.

The net capacity and thermal power consumption will have to be registered in the measurers that have been installed by the CONTRACTOR as it leaves from his reach. The devices of measurement of the tests will have to be of suitable precision and appropriately identified (tag numbers) in the plan of tests, before the beginning of these. Additionally diagrams will be due to provide, showing these instruments with their identification.

    - CONDITIONS OF THE TESTS OF GOOD OPERATION

Like minimum, the TEST OF Net CAPACITY, will have to consist of three tests of one (1) hour of duration each, within a diurnal period of 9 hours. The data taken in sufficient amount, in each one of the three (3) tests, will have to be corrected by environmental conditions and to be divided equally in one (1) hour. For the net efficiency of thermal power consumption during hourly of the three (3) tests the fuel burnup will be due to register and they will be taken as reference at least three (3) samples from the same, to be analyzed in the local chromatograph and to determine its properties. Before the beginning of the measurements of the tests, the units will have to be stabilized and to be in correct conditions, in agreement with the guarantees of the diagram of calculated calorific balance. During the TESTS OF GOOD OPERATION the operation ways will have to be:

- Patient as primary cartridge.

- All the systems and auxiliary equipment in delay.

- Conditions of permanent regime.

They will have to be operated in a normal way that he is representative of an operational configuration in the long term, with all the equipment operating as they have been designed and specified within the alarm limits, with all the bows of automatic and consistent control in with a good practice of industry of power generation. The normal systems of operation could not be put out of service, nor will be able to eliminate alarms or to bypass them, unless specifically it is allowed in the decided procedures of tests.

    - CORRECTIONS TO THE BASIC CONDITIONS OF THE GUARANTEES

The results registered during the conducted TESTS OF GOOD OPERATION in conditions different from the established ones in the GUARANTEES, will have to be corrected according to the factors including in curves or you formulate presented/displayed in the supply and decided by the parts. The curves and you formulate of correction will have to be provided in the procedures for the TESTS OF GOOD OPERATION. The following curves of correction will have to be the unique corrections allowed for the TESTS OF GOOD OPERATION.

- Ambient temperature correction.

- Temperature correction of humid bulb

- Correction by humidity.

- Correction by barometric pressure.

- Correction by power factor.

- Correction by frequency.

    - MEASURERSFOR THE TESTS

The measurements of electric power of exit ofLA AMPLIACIÓNwill have to be taken in the terminals of the elevating transforming, with standard measurers of the precision established in the specifications and with the transforming of established current and tension in documents. All the used electrical measurers for verification of the GUARANTEES will have to be calibrated and certificates before the tests.

Measurers of quality of the precision fuel will be due to use, in agreement with the norms of Tests of Operation.

The measurers for fuel flow must have a certificate of quality of an independent being.

    - PROCEDURES FOR THE TESTS OF GOOD OPERATION

In the procedures it will have to be decided and clearly defined the following thing:

- Conditions of the Tests of References.

- Duration of the tests.

- Curves and formulas of correction.

- Position of the valves.

- Internal load.

    - TESTS OF RATE OF LOAD TAKING

The capacity will be due to demonstrate that has the EXTENSION like a set of which the conditions and start-up time are fulfilled as it is established in these specifications.

The performance of the EXTENSION in the rate of load taking (“ramping rate”) will have to register with the information of the megavatios generated by the turbogenerators to gas at the beginning of taking of load of a stable minimum of generation and the time integrated from this beginning to the operation as primary cartridge. This registry will have to take place for a minimum of ten (10) percent. The operation in shutdown will have to fulfill the guarantees required by the engineering specifications and other contractual documents. After its generation has been reached as primary cartridge and the registries of megavatios and time have taken place, the shutdown will have to unload and the generators to leave synchronism and to take place of, taking themselves and registering the time required for the shutdown. All these operations will have to take place with the control systems in automatic.

    - ENVIRONMENTAL TESTS

With these tests one will be due to demonstrate that it fulfills the specifications and established environmental norms in the national laws as far as noise, emissions and protection of the environment. The CONTRACTOR will have to inform toLA COMPAÑÍA, ahead of time the date anticipated for the accomplishment of the tests.

      - TESTS OF EMISSIONS

The following thing will be due to include in the procedures of tests of emissions:

- Plane detailing the locations of the points of measurement of emissions.

- Confirmation and details of the instrumentation that will be used during the tests.

The emission tests will have to be lead by the CONTRACTOR or some other company subcontractor, with ample experience in the matter, and acceptable on both sides and registered in the registry of the Ministry of the Popular Power for Ambiente (MINAMB). For the tests it will have to prepare a protocol and reports of tests, which will have at least to be approvedLA COMPAÑÍAby twenty (20) days calendar before taking place the tests. The report of the tests will have to be received byLA COMPAÑÍAin the twenty (20) days following to the conclusion of the same.

The Monitoring and Control system of Emisiones (CEMS) will have to be installed, with its certificate of MECHANICAL COMPLETACIÓN, all the conducted tests of STARTING and satisfactory results and totally accepted byLA COMPAÑÍAlike requirement executing the tests of emissions. During the Tests of Emissions one will be due to demonstrate by registry of the CEMS, and by provided tests of verification by a company specialized in tests of emissions, that the exhaust gases are in form continues below the guaranteed limits.

      - NOISE TESTS

The tests will be due to lead that demonstrate thatLA OBRAit fulfills the limits of noise that are required contractually and according to the norms and laws established by the MINAMB. The revision and approval of the procedures of testLA COMPAÑÍAwith forty and five (45) days of anticipation to the programmed date of beginning of tests will be due to emit at least for.

Before carrying out the tests ofLA OBRA, all the test equipment will be due to try, carrying out nocturnal tests, in period of calm, in time dry and low environmental noise, and with a minimum of vehicles in circulation.

For work areas, the acceptance tests will have to be taken to1 mfrom distance of the surface of the equipment, from its closing, acoustic housing it has if it or quarter.

The test resultses will have totally to be reported along with the metereológicas conditions of operation of the equipment, conditions, measurement of noise, location of instruments and details of the same.

The procedure of test of noise will have to include:

- Plane detailing the locations of registry of the noise.

- List of operation ways, during which a set of noise measures will have to be taken.

All the measurements will have to be registered and will have to include the certificate of calibration of the instruments. One will be due to take information from the other condition and wind speed and its direction during the tests of the time.

The final report of tests will have to be emitted and to be givenLA COMPAÑÍAto a to more take to the 21 days calendar of to be completed the tests.

    - REPORT OF THE TESTS OF GOOD OPERATION

Within the seven (7) days after the completación of the tests one will be due to prepare and to emit forLA COMPAÑÍAa rough draft of the report that will have to include the following thing:

- Summary of Tests.

- Calculations.

- Results (without correcting and corrected).

- Curves of correction.

- Spreadsheet with data and curves.

After the revision and approval byLA COMPAÑÍAof the report rough draft, the Closing report of the TESTS OF GOOD OPERATION to the 28 days completación will be due to emit calendar of the tests, and will have to include the final analyzes of fuels and results.

  - TRUSTWORTHINESS TESTS (AVAILABILITY)

The Tests of Trustworthiness will have to be executed after the TESTS OF GOOD OPERATION and will have to demonstrate the capacity to export power of continuous and reliable form to the Interconnected System National, according to the office of load of the network and within the established design and operational criteria in the CONTRACT.

The intention of the Tests of Trustworthiness is to try that he is able to operate as primary cartridge and in conditions of three (3) turns by a significant period of time, identifying any operational defect to be corrected before the delivery ofLA OBRA. Lastests will have to include a number of tests specified for periods of availability, loads, profile of operation and way. The Tests of Trustworthiness will have to include demonstrations of starting of, stopped, and successful performance with well-educated loads by the office. The tests will have to last of thirty (30) days, divided in three periods of ten (10) days consecutive. All the tests will have to be realized with all the control systems in automatic.

    - DESCRIPTIONOF THE TRUSTWORTHINESS TESTS

The trustworthiness ofLA OBRAwith all equipment and services required for the total efficient and safe operation, will have to be demonstrated operating it under normal conditions by thirty days, divided in periods of ten (10) days without interruptions. The periods are defined next:

- Ten (10) days with continuous operation to primary cartridge.

- Ten (10) days with two turns (12horas c/u) of continuous operation taking load from partisan to primary cartridge under the direction from the COMPANY.

- Ten (10) days with two turns (12 hours c/u) of continuous operation taking zone charge or primary cartridge under the direction from the COMPANY.

It will have to operate within his limits specified through the tests including but not necessarily restricted to emissions, noise, quality of liquid effluents and temperature. All the tests will have to be realized with all the control systems in automatic.

The profile of operation in the 30 days of the Tests of Trustworthiness (Availability) will have to be decided before entersLA COMPAÑÍAand the CONTRACTOR, taking into account the requirements from WITHOUT and the supply apparatus from fuel. The operation profile will have to include a rank of loads and transitory situations, like which normally they would be expected during the commercial operation. One will be due to fulfill any reasonable request ofLA COMPAÑÍAfor such demonstrations.

    - DEFECT ACCEPTANCE NUMBERS

If in each one of the three cycles of ten (10) days of the Readiness tests, the new units would have operated during a 98% of the cycle (contractual rate of load and time and the other conditions), in satisfactory form forLA COMPAÑÍA, it will consider that the cycle has been completed successful and the test will be approved.

The Readiness tests will be considered like completed successful if the three cycles that have been completed fulfill the previous paragraph.

In case the tests must be interrupted by causes imputable to the CONTRACTOR, such as defects of the design, the materials or the manpower that are in favor including in the contractual reach and of these causes not obtain 98% in a cycle,la Pruebaof Availability of that cycle will have to be reinitiated from the beginning.

In case the tests must be interrupted by other people's causes or outside the control of the CONTRACTOR such as, without limiting itself them: greater force, fuel nonavailability, or provided facilities byLA COMPAÑÍAor third parts or nonavailability of WITHOUT receiving or accepting the generation ofLA AMPLIACIÓN, the cycle will enter pause in the point in which he was interrupted. The tests will be declared reinitiated when new units are ready for a new office or in the same conditions in which the cycle was interrupted. The tests will have to be continued and the time will have to be credited to which it was had accumulated before the interruption within the respective cycle of tests. In that case, of a delay in the Readiness tests, the affected terms and contractual conditions will have to be negotiated.

    - READINESS TESTS. CYCLE 1

The new units will have to be operated as primary cartridge (it holds to instructions of the office) by a duration of 240 hours beginning with a cold start.

The availability of the new units will have to be a complete with all equipment and services required for total, safe and efficient operation. LA AMPLIACIÓN in these conditions it will have to be tried by a consecutive period of 240 hours without interruptions, except external interrupts.

    - READINESS TESTS. CYCLE 2

This session of tests will not have to be taken until after the satisfactory completación of Cycle 1 of tests. Primary cartridge will have to be operated as and zone charge under the direction of the CONTRACTOR.

During this cycle they will be due to demonstrate the duration of cold starts, lukewarm, I warm up and reason of taking of load of new units according to the values specified in the engineering specifications. A cycle of five days (120 hours) of continuous operation of new units to nominal power will be due to include, can vary within a 5% of the guaranteed exit subject to the restrictions that the load office imposes.

In this cycle the satisfactory operation and of any superfluous equipment will have to try on that has been including.

The new units will have to operate under the landlords pre-established and decided to demonstrate their flexibility in commercial operation, as it were specified.

    - READINESS TESTS. CYCLE 3

This session of tests will not have to be taken until after the satisfactory completación of Cycle 2 of tests. Primary cartridge will have to be operated as and zone charge under the direction of the CONTRACTOR.

Measurements from the tests during the operation of this cycle that allow to calculate and to register the net capacity and thermal power consumption in discreet values of load between stable minimum generation and primary cartridge will be due to take.

The new units will have to be taken and taken to his stable minimum value of generation and it will verify that the emission of NOx by a minimum period of 4 hours is fulfilled and maintains. In a while appropriate during this period of 4 hours one will be due to measure the net power of exit of new units (Megavatios), fuel consumption, frequency of the network and the room temperature (dry bulb), relative humidity and barometric pressure. All the measurements will have to be registered.

LA AMPLIACIÓNit will have to be taken to 50% of his nominal power and maintained in these conditions by a minimum period of 4 hours. In a while appropriate during this period of 4 hours one will be due to measure the net capacity of exit ofLA AMPLIACIÓN(Megavatios), fuel consumption, frequency of the network and the room temperature (dry bulb), relative humidity and barometric pressure. All the measurements will have to be registered. This test will be due to also carry out with a 75% of its nominal power.

LA AMPLIACIÓNit will have to be tried to demonstrate his ability to operate with zone charge. As guide initial one suggests a continuous operation of 12 hours (ex 7am to 7pm) with 70% of his nominal power and 12 hours continuous (ex 7pm to 7am) to total load, by a period within this cycle of 10 days, as it indicatesLA COMPAÑÍAand under the conditions of the load office.

- DEFINITIVE ACCEPTANCE

The Act of DEFINITIVE ACCEPTANCE, will have to be signed byLA COMPAÑÍApassed the period of GUARANTEES of twenty-four (24) months, established in Numeral 28. of this specification, unless pending damages or claims existed.

The DEFINITIVE ACCEPTANCE will happen when all the conditions that are indicated next have been satisfied.

- Signed the Acts of MECHANICAL COMPLETACIÓN and PROVISIONAL ACCEPTANCE of the WORK.

- Fulfilled successful with all the TESTS OF GOOD OPERATION.

- Fulfilled to satisfaction ofLA COMPAÑÍAwith all the pending points and/or decided with the CONTRACTOR on the solution any pending point of the (s) in writing it lists (s).

- LA COMPAÑÍAit has received all the Planes “Like Constructed”.

- Fulfilled on the part of the CONTRACTOR with all the contractual commitments with professional, technical and working the personnel that I participate in the WORK, as well as to demonstrate that it was fulfilled the payments of invoices to Subcontractors, suppliers, commercial Companies of Services and other beings.

LA COMPAÑÍAit will have to receive from the CONTRACTOR all the technical and financial documentation that could be established like an obligation of payment of the CONTRACTOR towards third parties.

The CONTRACTOR is responsible for the protection and conservation of the WORK to date in which jointly withLA COMPAÑÍAthe Act of DEFINITIVE ACCEPTANCE of the WORK subscribes, therefore, will be the person in charge to repair and/or to replace, to its exclusive cost and satisfaction ofLA COMPAÑÍA, the damages and/or losses which they will happen prior to this date, all this without decline of the covers including inla Garantíaof Stability of the WORK that the CONTRACTOR will have to send to favor and satisfaction of LA COMPAÑÍA.

LA COMPAÑÍAit can refute the company/signature of the Act of DEFINITIVE ACCEPTANCE, if defects or faults not yet solved by the CONTRACTOR exist that limit the operations ofLA AMPLIACIÓNor present/display insecurity situations or the terms and conditions demanded in these specifications and the CONTRACT are not fulfilled.

With the company/signature of the Act of DEFINITIVE ACCEPTANCE,LA COMPAÑÍAit recognizes that the CONTRACTOR has fulfilled all contractual obligations except the Agreements of Confidentiality and those other effective obligations that must remain major time according to specifies in the CONTRACT or the Venezuelan legislation.

Once subscribed the Act of DEFINITIVE ACCEPTANCE and whenever any part of the WORK or any obligation of the CONTRACTOR is not pending, it will be come to subscribe the respective settlement

- PLANNING, PROGRAMMING AND MEASUREMENT OF PROGRESS

  - PLANNING AND PROGRAMMING

    - EXECUTION PLAN

The CONTRACTOR will have to elaborate a Plan of Execution of the WORK that includes the times considered for each phase and the activities critics, initiating withla Ingeniería Básicaand of Detail until the NORMAL OPERATION (last activity of closing and gives of the WORK) ofLA AMPLIACIÓN. Parathe elaboration of this plan an equal Software or superior to Microsoft Project 2003, Spring, Lulo will have to use.

The plan to elaborate will have to be based on a Structure of Partition of the Work (Work Breakdown Structure-WBS), in which the different areas, packages and levels of execution are grouped and reflected ofLA OBRA. Debidamentecodified with the purpose of to identify the different products that were executed as it leaves from each one of the phases of the WORK.

The Plan of Execution will have to be developed initiating activities for the indicated date in the Plan of Execution decided withLA COMPAÑÍA, with the company/signature of the Act and/or approval byLA COMPAÑÍAof the beginning of LA OBRA.

The CONTRACTOR will have in good condition to present/display the Plan of Execution of the WORK with the detailed activities for the installation and puttingLA AMPLIACIÓN, taking the forecasts necessary not to interfere with the regular operations of the PLANT. The CONTRACTOR will have to fulfill the requirements of run time of the WORK before indicated.

The Plan of Execution to be elaborated and presented/displayed jointly withla Oferta, will have to be on the basis of the systems, according tola Hojaof Budget of the WORK, annexed to this specification.

This Plan will have later to be presented/displayed with reviewed the Technical-Commercial supply and withLA COMPAÑÍA, previous beginning of the WORK.

The CONTRACTOR will execute the contemplated activities in the work within four (04) months continuous, counted as of the date of the company/signature of the beginning act and will have to present/display in his supply a masterful cronogram of execution that fulfills the established term. The masterful cronogram will have to indicate the landmarks of beginning and completion of the activities macro of the project.

- Beginning - aim of basic engineering

- Beginning - aim of the engineering of details

- Beginning - aim tries of it of the equipment of long time of delivery

- Beginning - aim of the construction

- Beginning - aim of the tests

- Beginning - aim of the putting in good condition

The CONTRACTOR will present/display a detailed cronogram of execution one (01) week after to have decided the definitive reach the activities and products to be given during the starting meeting. The CONTRACTOR will put under the approval of the COMPANY his better strategy of execution of the contemplated activities in the reach of the work.

The detailed cronogram of execution will be presented/displayed in software (Project/Spring), according to the structure of work partition that settles down during the beginning of the works, and according to the lineamientos been suitable with the COMPANY.

    - PAYMENT PLAN

The CONTRACTOR will have to elaborate a Plan of Payment mensualizado with landmarks clearly defined and not with the inclusion of activities that are realized partially, considering the beginning from works object from this CONTRACT, and the Plan of Execution mentioned in Numeral 23.1.1.

The Plan of Payment will have to contain the component in Strong Bolivars and Dollars that are considered to disburse month to month, until the completación of the works and signs of the Act of PROVISIONAL ACCEPTANCE of LA OBRA.

  - MEASUREMENT OF PROGRESS

The CONTRACTOR will evaluate the physical and financial progress of the WORK with base in the plan of execution reviewed and approved by LA COMPAÑÍA.

La Mediciónof the Progress Engineering will be made monthly in global form for each one of the phases (, Tries, MECHANICAL Construction and COMPLETACION on the basis of all the landmarks to decided between the CONTRACTOR andLA COMPAÑÍAin previous meeting to the company/signature the contract between the parts.

To be assigned parameters and weights stopla Mediciónof the Progress will be established by the CONTRACTOR and put under the approval of LA COMPAÑÍA.

The functions of Management, Programming and Control, Securing ofla CalidadofLA OBRA, as well as other activities not associated with the own execution of the works of field, will not generate advance physical and consequently they will not be considered inla Mediciónof the Progress of LA OBRA.

    - MEASUREMENT OF THE PHYSICAL AND FINANCIAL PROGRESS

The physical Progress will be measured in terms of Landmarks reached, being based after it on codes of accounts of the WBS, lists of products, (specifications, planes, documents, etc.) and by organization responsible for the executed work. The advance will be measured independent of the used hours men, costs, expenses or time calendar.

The CONTRACTOR will be responsible by the elaboration for the report of Measurement of Physical and Financial Progress of the WORK which will have subsequent to be presented/displayed to the approvalLA COMPAÑÍAof in the first five (5) days of the month the passed one.

The Physical Progress will be determined based on the gained value, based this on the advance reached according to the Landmarks of progress approved byLA COMPAÑÍAafter each type of product. Each one of the landmarks will establish a percentage of pre-established advance. The percentage multiplied by the amount indicated in the budget, would determine the gained value of the corresponding product.

The gained value can talk about to hours man, amounts or financial advance, following the units established for each one of the budgets of products.

The sum of the values gained by product within a divided code of account, by the total budget of this account, determines the percentage completed of the same.

    - MEASUREMENT OF THE ENGINEERING PROGRESS

The measurement of the progress of this phase LA OBRAwill be realized by Landmarks of advance approved byLA COMPAÑÍA, applied these to products to be generated (specifications, planes, documents, etc.). Each discipline would prepare a list of its corresponding products and each product will have a certain budget and pre-established landmarks of advance, with percentage of completación that correspond to specific points of progress, crediting itself the advance once fulfilled the landmark corresponding.

The Physical Progress of the Basic phase of Engineering and Detail will be determined according to the development reached in the following Landmarks:

- Document development, and memories of calculation:

- 50% of advance: Rev. “To” Emission for commentaries

- 100% of advance: ”0” Final emission

- Development of Planes:

- 50% of advance: Rev. “To” Emission for commentaries

- 90% of advance: ”0” Emission for Construction

- 100% of advance: Constructed planes like

- Engineering specifications:

- 50% of advance: Rev. “To” Emission for commentaries

- 100% of advance: ”0” Emission for Construction

The Landmarks previously indicated can later be reviewed and be decided with the CONTRACTOR, once signed the CONTRACT.

    - MEASUREMENT OF THE PROGRESS OF TRIES

The measurement of the progress of this phase LA OBRAwill be realized with base in a methodology similar to the used one to measure the progress ofla Ingeniería, that is to say by gained value and landmarks of advance, approved byLA COMPAÑÍA, applied these to the emission of order request, positioning of the order, emission, approval of manufacture planes, manufacture of the equipment, arrival to Venezuelan port, reception in warehouse.

The gained value will be the physical progress, multiplied by the budgeted cost or the amounts of equipment, materials and/or components whose advance is being moderate.

The Physical Progress of the phase of Tries will be determined according to the development reached in the following Landmarks:

- 30% with the positioning ofla Ordenof Purchase

- 50% with the reception of the planes of the Manufacturer

- 70% with the completion of the works in factory

- 90% with the acceptance of the works in factory

- 100% with the reception in the site of LA OBRA

The Landmarks previously indicated can later be reviewed and be decided with the CONTRACTOR, once signed the CONTRACT

    - MEASUREMENT OF THE CONSTRUCTION PROGRESS

The Progress of Construction will be determined by the measurement of the amounts or constructed and/or installed work games, the advance landmarks will be previously decided between the CONTRACTOR andLA COMPAÑÍA. Lasamounts corresponding to each one of the established codes of account for the different packages or areas of the WORK, divided by the amounts of work budgeted or installed equipment will allow to establish the percentage of reached physical advance.

    - GLOBAL MEASUREMENT OF THE PROGRESS

The Global Advance of the WORK will be determined combining the average advance of each of phases of the same.

    - MEASUREMENT AND CONTROL OF LA FUERZA HOMBRE

Jointly with the execution plan, the CONTRACTOR will have to present/display a Plan of Assignment of personnel, who will be based on Histograms of Control, which they will have to be realized concerning each one of the disciplines and of each phase of execution of the WORK. The CONTRACTOR will have to present/display to the previous approvalLA COMPAÑÍAof to the company/signature of the CONTRACT the Plan of Assignment of personnel who will participate in all the phases of LA OBRA.

    - MEASUREMENT AND MODE OF PAYMENT

The payments will be realized on the basis ofla Mediciónof Progress of each one of the phases ofLA OBRAaccording to the indicated thing in numerals 23.2.1., 23.2.2., 23.2.3., 23.2.4 and 23.2.5 of these specifications.

For the request of the payment corresponding to executed works, the CONTRACTOR will have to present/display original and two (2) copies of the invoice, with the amount to be cancelled byLA COMPAÑÍA, which will be calculated taking as it basesla Medición Globalof the Progress, certain according to the methodology indicated in numeral 23.2.5 of this specification.

Each invoice will have to come accompanied with the measurement of corresponding advance properly approved by the ENGINEER OF the PROPRIETOR and the COMPANY.

  - PRESENTATION OF INFORMATION

The CONTRACTOR will emit periodic reports with tabulations and graphs that contain significant information that it allows the COMPANY to evaluate the state of the project.

The CONTRACTOR will prepare formats for each type of report required for the revision and approval on the part of the COMPANY. Any change to the format will have to be approved by the COMPANY.

The monthly cut for the generation of monthly reports will be day 25 of the month and the monthly report will be issued 2° working day of the month.

The indicated list next summarizes, generally, the main reports that the CONTRACTOR will emit with the indicated frequency. The CONTRACTOR will emit additional reports if therefore she requires the COMPANY. The specific reports that apply during each phase of the project and its frequency, will be decided with the COMPANY.

    - Engineering

Nº table 23,1 Reportes de Ingeniería

| Report | Frequency |
| --- | --- |
| State of engineering | Monthly |
| List of planes | Periodic update |
| List of equipment | Periodic update |
| Index of planes of manufacturers | Periodic update |

    - It tries

Nº table 23,2 Reportes de Procura

| Report | Frequency |
| --- | --- |
| State tries of it | Monthly |
| State of the O/C | Monthly |
| Report of O/C pursuit | Monthly |
| Index of requests of materials | Periodic update |
| List of emitted O/C | Periodic update |
| Reports of inspection | When emitting itself |
| Plan of tries of LPE | Periodic update |

    - Construction

Nº table 23,3 Reportes de Construcción

| Report | Frequency |
| --- | --- |
| State of the construction | Monthly |
| Report by subcontractor | Monthly |
| Photographies | Monthly |
| Report of hours man | Monthly |
| Weekly plan of construction | Weekly |

    - Costs

Nº table 23,4 Reportes de Costos

| Report | Frequency |
| --- | --- |
| Report of costs of the project | Monthly |
| Report of change orders | Monthly |
| Financial report | Monthly |

    - Planning

Nº table 23,5 Reportes de Planificación

| Report | Frequency |
| --- | --- |
| Program of main landmarks | Periodic update |
| Up-to-date program | Monthly |
| Histogram of personnel | Monthly |
| Curves of progress | Monthly |
| Report of critical route | Monthly |

    - Others

Nº table 23,6 Other Reports

| Report | Frequency |
| --- | --- |
| List of manufacturer planes | Monthly |
| Curve of isometric | Biweekly |
| Manufacture of pipe | Biweekly |

    - Monthly report

The CONTRACTOR will have to prepare a detailed monthly report being indicated the progress of the project during the previous month, in summary the progress reached to the date.

The report will contain, like minimum, the following sections:

- Executive summary

- Summary of the state of the project

- Flagrant aspects during the period

- Areas of attention and planned actions of mitigation

- Global state of the project

- State of the execution program

- State of costs and projection of flow of box of 6 months

- Tendencies in costs and times

- State of the change orders

- Indices of security

- Securing of the quality

- State of engineering

- State tries of it

- State of the construction

- Annexes: Tables, graphs and photographies of progress.

The executive Summary will include a summary of the project to the date, including description of the progress reached during the month, a list of important landmarks reached and the dates. This section must identify of clear way any areas of attention and must indicate any remedial actions or mitigants implemented or planned by the CONTRACTOR.  The executive Summary must contain sufficient information to provide a photography of the state of the project to the high management of the COMPANY.

The global State of the project will include a global curve of the project having compared the real progress and the foretold one with the programmed one, in terms of percentage against a monthly scale of progress. The evaluation of progress of the CONTRACTOR must easily be verifiable by the COMPANY. This section also must include histograms of personnel, monthly, accumulated and foretold.

The CONTRACTOR will provide a monthly projection of the flow of box for the global planning of the project. The report also will include details of the state of the change orders indicating tendencies, cost of the approved ones, emitted or in preparation, indicating changes in the manpower costs and materials.

The sections of Indices of security and Securing of quality must detail to the programs of security and reaches to the date.

- INSURANCES AND GUARANTEES

The CONTRACTOR will commit itself to subscribe and to maintain during the implementation time of the present Contract and the one of his prorogations effective there will be if them, policies of certainly insure all the risks with his respective employees assigned to the fulfillment of the execution ofLA OBRAincluding, but without limiting themselves until death, injuries, diseases and, accidents.

The costs corresponding to this concept comprise of the reach of the CONTRACTOR and will have to be including in their Supply.

The CONTRACTOR will be forced to contract and to maintain effective during the time of the execution of the WORK and of his you prorogue there will be if them, and to date of the company/signature of the Act of PROVISIONAL ACCEPTANCE, insuring companies accepted byLA COMPAÑÍA. Asísame are committed to present/display before the date of beginning of the WORK the following guarantees and insurance policies:

  - GUARANTEES

The CONTRACTOR will contract insurance agencies or banking institutions to satisfaction ofLA COMPAÑÍAand will give at the time of the company/signature of the contract the following guarantees:

    - GUARANTEE OF FAITHFUL FULFILLMENT

Guarantee of Faithful Fulfillment by the sum of ________________ (Versus.) equivalent to the twenty percent (20%) of the total amount of the CONTRACT to guarantee toLA COMPAÑÍAthe fulfillment of each and every one of the obligations assumed by the CONTRACTOR under the present CONTRACT, as well as the good one and had to execution of the WORK and its opportune and exact completion. This Guarantee will be effective to date of the company/signature of the Act of DEFINITIVE ACCEPTANCE and will guarantee also, the payment of the obligations that will be pending at the expense of the CONTRACTOR in favor ofLA COMPAÑÍA, as well as the fulfillment of any other obligation in charge of the CONTRACTOR derived from the present CONTRACT and the other documents that integrate the same. La Fianza of Faithful Fulfillment of the CONTRACT it will be released byLA COMPAÑÍAafter the last certificate of DEFINITIVE ACCEPTANCE of the WORK corresponding to the last equipment has been granted, according to settles down in Numeral 18. of these specifications. In the case of breach on the part of the CONTRACTOR, of anyone of the obligations assumed in this CONTRACT,LA COMPAÑÍAit will retain the 20 percent (20%) of each one of the payments thatLA COMPAÑÍAthe CONTRACTOR does. This bottom of guarantee, in case of not being used, will be given to the passed CONTRACTOR a year after the company/signature of the Act of DEFINITIVE ACCEPTANCE of the WORK.

    - GUARANTEE OF LABOR RESPONSIBILITY

Guarantee of Labor Responsibility by the sum of ________ (Versus.), equivalent to the ten percent (10%) of the portion of the cost considered for the work of construction (either manpower) of this CONTRACT, to guarantee toLA COMPAÑÍAthe fulfillment on the part of the CONTRACTOR of all the labor, legal or contractual obligations, in front of its foreign or Venezuelan workers, derivatives of the execution of the WORK of the present CONTRACT. La Fianza to that literal one talks about this will be constituted by an insurance agency or a banking organization residing in Venezuela, in any case the document constituted ofla Fianzawill have to be approved previously byLA COMPAÑÍA. Lapresent Guarantee will stay effective up to 12 months after the date of the Act of DEFINITIVE ACCEPTANCE and could be released byLA COMPAÑÍAbefore that period, as long as the CONTRACTOR presents/displays the labor settlements of each of his workers accredited byla Inspectoríaof the Work of the zone where the WORK was executed. Also it will have to present/display the solutions corresponding to the INCE and the one of the Venezuelan Institute of the Social Insurances. La Fianza of Labor Responsibility before described it could be replaced by retention. In this case,LA COMPAÑÍAit will retain the 20 percent (20%) of each one of the payments thatLA COMPAÑÍAthe CONTRACTOR does. This bottom of labor guarantee, in case of not being used, will be given to the passed CONTRACTOR a year after the company/signature of the Act of DEFINITIVE ACCEPTANCE of the WORK, previous presentation of the labor solution emitted byla Inspectoríaof the Work and the solutions corresponding to the INCE and the Venezuelan Institute of the Social Insurances.

    - MAJORITIES OF THE GUARANTEES

La Fianzawith Faithful Fulfillment and Labor Responsibility stipulated and any other Guarantee that is demanded in the CONTRACT they will have to satisfy the following requirements:

- To be granted by banking institutes or Venezuelan insurance agency accepted by LA COMPAÑÍA.

- The emitting institution ofla Fianzawill have to know in all parts documents the CONTRACT and the reach the obligations that the CONTRACTOR assumes.

- The use ofla Fianzawill have to depend exclusively on the fulfillment of the obligation of whose guarantee it treats, thus the document of Guarantee will not have to contain no clause or condition that makes depend its duration or use on the expiration of a term, of the payment of the premiums, the accomplishment of some act, is this on the part of the CONTRACTOR or ofla Institucióntransmitter of la Fianza.

- The one will not be admitted thatla Fianzacontains clauses that condition or make mention to possibilities of cancellation ofla Fianzaby the CONTRACTOR or emitting institution ofla Fianzabefore the terms of time or fulfillment of the obligations have been fulfilled.

- La Fianzait will have shared in common and to be constituted by means of authenticated or registered document and will have to contain express mention of which the fastener resigns to the benefits that decide articles to him 1833, 1834 and 1836 of the effective Venezuelan Civil Code.

- The CONTRACTOR will have to opportunely pay the amounts corresponding tola Fianzaand maintaining respective documents to date of COMPANY liberation totally effectivela Fianza. LAreserves the right to pay the amounts settled down in these documents on behalf of the CONTRACTOR, without needing his express authorization, loading themselves in the liabilities or discounting to him of the payments that correspond to him, the amounts that bondsman by the concepts before indicated pays to the organization. It is understood that it is only a right ofLA COMPAÑÍAand not an obligation, and that, therefore, does not affect in any case the obligation of the CONTRACTOR of paying the corresponding amounts opportunely and to fulfill to the organization bondsman all the obligations that to him the respective contract of guarantee imposes.

If the CONTRACTOR does not solicit, she does not present/display or she does not maintain the Guarantees of Faithful Labor Fulfillment effective and,LA COMPAÑÍAwill carry out the retentions to the CONTRACTOR on each payment that is done to him, until covering the amount of cover required like guarantee. LA COMPAÑÍA he will be able to fit the amount of these retentions when he considers that an increase or diminution in the risk has taken place that is persecuted to cover. The retained amounts will not generate interests in favor of the CONTRACTOR, this one will receive when subscribing the Act of DEFINITIVE ACCEPTANCE, the amount corresponding to the retentions by concept of the Guarantees.

  - INSURANCE POLICIES

The CONTRACTOR commits itself to contract and to maintain effective, throughout the run time ofLA OBRAand until the definitive reception of the same, with insuring companies properly authorized, the following insurance policies, to satisfaction ofLA COMPAÑÍA,

    - POLICIES OF GENERAL AND CROSSED CIVIL RESPONSIBILITY

That it covers personal injuries, death or material damages caused to the personnel of the CONTRACTOR, as well as third parties and derivatives of:

- Estates and Operations

- Contractor Independent

- Damages to the properties where it works

- Crossed Civil responsibility

It is understood that the present policy will have to protect all the facilities, equipment and goods against all risk by its value of replacement, as much own as of third parties, as well as the properties of third parties that were affected or destroyed by a wreck protected by this policy.

This policy and its cover only contribute to the fulfillment of the responsibility assumed by the CONTRACTOR, and that of no way limits, it releases nor it exempts to this one of the obligations that can she have as a result of this responsibility.

Limit of Cover:

Corporal injuries or death of a person by accident and/or material damages of Five Million Dollars of the United States of America (US$ 5.000.000, 00) by everything and each event or occurrence.  The deductible one will be exclusive responsibility of the CONTRACTOR.

    - POLICIES OF SUPERVISORY RESPONSIBILITY

That it covers the difference between the amount with the indemnification that corresponds by the Obligatory Social Insurance and the established one inla Contrataciónof the Electrical Sector.  In the areas where it does not govern the Obligatory Social Insurance, the policy will have to cover the limits anticipated in the referred Contract.  Concerning subjects noncovered by the Obligatory Social Insurance, the policy must cover besides the limits established in the Contract of the Electrical Sector, the dispositions anticipated in Title VIII ofla Ley Orgánicaof the Work, as well as the complete cover by medical expenses.

    - POLICIES FOR FOREIGN PERSONNEL

For the brought personnel of the foreigner of the CONTRACTOR, a policy with cover demanded byla Leyof Compensation for the Workers, including legal domestic cover in any area where the Work or any other jurisdiction is carried out in which the CONTRACTOR is forced to pay benefits or to provide cover for that personnel who toils according to the present Contract.  In view of the previous thing, the CONTRACTOR commits itself to contract to Insurances of Compensation of Workers and Insurances of Incapacity (“Workmen' s Compensation and Statutory Disability Benefits Insurance”) and Insurances of Supervisory Responsibility (“Employer' s Liability Insurance”) that are sufficient to assure the payment any judicial failures, by arbitration or compensations that is adjudged by any courts, commissions, meetings or civil servants or agencies of them, because of injury, incapacity or death of any worker of the CONTRACTOR recruited in the outside to carry out the Work, that happens while he is dedicated, in any form to realize activities included within the object of the present Contract.  This Insurance of Supervisory Responsibility will be contracted by the CONTRACTOR with limits nonsmaller FIVE MILLION DOLLARS OF the UNITED STATES OF AMERICA (US$ 5.000.000, 00) by injury or death.

    - POLICIES OF CIVIL RESPONSIBILITY OF VEHICLES

Basic and with excess of limits, that injuries or death cover with any person, and damages to properties of third parties, of the CONTRACTOR and ofLA COMPAÑÍA, a.c.

Limit of Cover:

Corporal injuries or death of a person by accident and/or material damages of Five Million Dollars of the United States of America (US$ 5.000.000, 00) by everything and each event or occurrence.  The deductible one will be exclusive responsibility of the CONTRACTOR.

    - PROPERTIES

The tools and equipment that is property of the CONTRACTOR and the subcontractors or has been rented by them will have to be places setting by a policy against all risk with a guaranteed amount equivalent to the value of replacement of the tools and equipment. The deductible one will be exclusive responsibility of the CONTRACTOR.

    - ENVIRONMENTAL CONTAMINATION

The amount of the cover is of Five Million Dollars of the United States of America (US$ 5.000.000, 00). The deductible one will be exclusive responsibility of the CONTRACTOR.

    - OTHER COVERS

The CONTRACTOR will have to demand his Subcontractors to contract and to maintain the insurance policies effective according to the covers applicable to the portion of subcontracted Work.

If necessary, he will have to include an insurance policy of Civil Responsibility by the aquatic airships (including helicopters) or ships, with a limit that will not be inferior to Five Million Dollars of the United States of America (US$. 5.000.000, 00).

    - GENERAL CONDITIONS

- All the required insurance policies and the national legislation will be contracted with insurance agencies domiciled in Venezuela until the amounts demanded by the national legislation.

- In the cover of the insurance policies subscribed by the CONTRACTOR the insured will be the CONTRACTOR andLA COMPAÑÍA.  Enthese policies express mention of which will have to become the civil responsibility is crossed in case of damages between the coinsured, with respect to the risks assumed by the CONTRACTOR by virtue of the present Contract.

For this effect, and as far as each one of the required covers of insurance of the CONTRACTOR, one will name toLA COMPAÑÍA, solely until the limits of responsibility explicitly accepted by the CONTRACTOR in the present Contract.

- The insurance policies will have to contain the resignation on the part of the insurer of the subrogation right.

- The insurance policies will have to contain a clause of automatic restitution of the assured amount.

- In case of victory of the policies indicated, before the definitive completion of the Contract, they will have to be renewed by the CONTRACTOR; in case of not doing itLA COMPAÑÍA, it will be able to arrange directly what considers advisable for the maintenance of the cover of such risks and its cost will be discounted of the payments that by any concept must make the CONTRACTOR. The CONTRACTOR will demand his Subcontractors who contract and maintain during the execution of subcontracts and until the definitive completion of the same, the insurances before indicated, when the risks are not insured by the insurances contracted by the CONTRACTOR.

- The CONTRACTOR will not initiate the execution, total or partisan, of the Work, nor will allow that she does no of his Subcontractors, until the insurance contracts have not been celebrated and are in use the policies demanded in this Contract, for which it will have to present/display toLA COMPAÑÍA, copy of supporting the corresponding ones.

- LA COMPAÑÍA, he will not be responsible by the limits, deductible nor limitations of the text including in the insurance policies of the CONTRACTOR.

It is specifically established that the presentation on the part of the CONTRACTOR of the indicated insurance policies in this clause is indispensable to come with the company/signature of the present Contract and, therefore, to give beginning to the execution ofLA OBRA.LA COMPAÑÍA, unilaterally will be able to accept the starting ofLA OBRAwithout the presentation of such insurance policies, in which case,LA COMPAÑÍA.the right is reserved to retain of any sum owed to the CONTRACTOR an amount equivalent to the percentage established in the norms of LA COMPAÑÍA.

These retained amounts will be only released until the CONTRACTOR fulfills the obligation to give the insurance policies in the terms anticipated in this CONTRACT.

- The breach of the CONTRACTOR to present/display the insurance policies in a reasonable period within the use of the present CONTRACT, will give straight unilateral and exclusive toLA COMPAÑÍA, to consider the amount retained like compensatory by the insured risk and, consequently, not giving back it by penalty concept.

- Any sum retained byLA COMPAÑÍA.and that by this concept is given back, it will not devengará interests and it will follow the same conditions for his liberation that the established ones in the respective insurance policies.

    - POLICIES OF ALL RISK OF CONSTRUCTION

The CONTRACTOR will have to present/display a policy to cover any physical loss, general civil responsibility by all risk of construction or the damages of the facilities or facilities including all the equipment and materials that conform either will comprise of the WORK, are these of property of the CONTRACTOR like ofLA COMPAÑÍA, during the time that lasts its guard and guards and until the PROVISIONAL ACCEPTANCE of the WORK the limit of the cover of this policy will have to be the amount that is from the sum of the total of the amount of the CONTRACT, but corresponding to the provided equipment, parts and spare parts so thatLA COMPAÑÍAthey are part of the WORK. The CONTRACTOR will give special attention to the manufacture, assembly, transport and other activities related to inside try and acquisition of the equipment and materials national and concerned as much as outside the Venezuelan territory, for which it will have to contract and to maintain policies effective of certainly they reconstitute losses or damages to goods equipment and materials during his manufacture and assembly, as well as during its transport until place specified for the WORK.

The policy will have to cover, without exception, the turbogeneradoras units and their auxiliary modules, provided byLA COMPAÑÍA, as it leaves from the components of the WORK.

- DAMAGES TO THIRD PARTIES AND EXISTING FACILITIES

Any damage to third parties or existing facilities that are caused as a result of the construction of the WORK, including the responsibility of operations or external activities related such as the transport of equipment or materials, will be of the exclusive responsibility of the CONTRACTOR, who will support to all the resulting expenses of the repairs or indemnifications that will be to place.

The CONTRACTOR will be responsible before the competent authorities, of any activity that realizes and that causes damages to the environment or third parties, they are well by activities executed as a result of the works of construction of the WORK, like outside them.

- EXPENSES OF NATIONALIZATION

The CONTRACTOR will pay all the expenses who causes the import of the equipment, materials, tools, articles and effects generally, of permanent character, that is part of the WORK, which they happen to be property ofLA COMPAÑÍAand which according to documents of the CONTRACT they are of obligatory provision of the CONTRACTOR. The costs that demand the demanded Expenses of Nationalization in this specification will have to comprise of the reach of the CONTRACTOR, and will have to be including in the amount of their SUPPLY.

- TAXES

The CONTRACTOR will have to pay all that with rates, national and/or municipal taxes and other positions, including tax on the rent, as a result of anyone of the works carried out, based on the values settled down for these works on documents of the CONTRACT.

The tariffs by concept of the equipment and materials concerned to being provided by the CONTRACTOR, according to the terms and conditions of this CONTRACT, will be paid by the CONTRACTOR, independent of the type and nature of the tariff.

All the tributes, including taxes, rates and contributions that in accordance withla Leyand the regulation laid downs in the manual that are generated by the activities of the CONTRACTOR by virtue of the CONTRACT, inside or outsidela República Bolivarianaof Venezuela, are responsibility and will have to be paid by this one, as well as will have the CONTRACTOR to support the retentions of tributes who in accordance with such dispositions must carry outLA COMPAÑÍAto him, without in no case the CONTRACTOR has right to reimbursement some by the payment of the tributes that she will have had to cancel or the retentions that she will have supported.

The CONTRACTOR declares that in the amounts to be paid byLA COMPAÑÍA virtue of the present CONTRACT, they are including all the taxes to be paid in the geographic area where the CONTRACT will be executed. Consequently, the CONTRACTOR is forced to fulfill his obligation opportunely to carry out the declarations or the payment of the Taxes or Patents of Industry and Commerce inla Municipalidadcorresponding, in accordance with the applicable legislation in each zone and in agreement with the location where the CONTRACT is executed, and to the nature or particular characteristics of the activities conform that them.

The CONTRACTOR will be the unique and exclusive person in charge of the payment of the Tax to Valor Agregado (IVA), and any other tax, as well as of the rights caused by the import and/or export of the consumptions, equipment and materials and any spare parts required forLA OBRAand the fulfillment of the present CONTRACT.

LA COMPAÑÍAhe will retain of each payment to which one is forced under this CONTRACT, or in agreement with national, state and/or municipal laws, the corresponding amount according to the had thing inla LeyTax Onla Renta, its Regulations, Decrees, as well as in any other applicable legal disposition without distinction some.

- INCENTIVES AND PENALTIES

LA COMPAÑÍAit will present/display in occasion to the Clarifying meeting the Incentives and Penalties that will prevail for this process.

- GUARANTEES

LA AMPLIACIÓNand all the equipment and Systems compose that it, will have to fulfill to satisfaction ofLA COMPAÑÍAwith the GUARANTEES of MECHANICAL COMPLETACION, established PROVISIONAL ACCEPTANCE and DEFINITIVE ACCEPTANCE in these specifications and the CONTRACT.

All the equipment and components to be provided by the CONTRACTOR will be under the shelter of the GUARANTEES, with duration of twenty-four (24) months as of the date of company/signature of the Act of PROVISIONAL ACCEPTANCE. In case it is found some defect during the operation of the equipment, materials and systems installed in the WORK, in such a way that the same must be replaced or be repaired within first half of the period of GUARANTEES, this one will extend by an equal period to the period of GUARANTEES surplus, counted as of the date in which such equipment, materials and systems failed. The new period of GUARANTEES surplus, would begin to count itself as of the date in which such equipment, materials and systems are put again in operation.

The equipment constructive majors and minors, accessories, devices and elements must be new and under no circumstance repaired, reconstructed equipment will be accepted or with use.

The CONTRACTOR, will be responsible beforeLA COMPAÑÍAby the GUARANTEES for the equipment and materials acquired through third parties. In this sense the CONTRACTOR will have to ask for to the SUPPLIER the respective GUARANTEES of the required equipment stopsLA OBRAof the CONTRACT of the EXTENSION. The CONTRACTOR will have the responsibility to determine the terms of GUARANTEES that are advisable, in order that the same serve as endorsement for the GUARANTEES of the work demanded in the CONTRACT.

In the specific case of the turbogeneradoras units and auxiliary modules, provided byLA COMPAÑÍA, the CONTRACTOR will assume the integral responsibility of the same from the moment of the company/signature of the CONTRACT and will have at the end ofLA OBRA, with the company/signature of the Act of PROVISIONAL ACCEPTANCE and once fulfilled to satisfaction the described FUNCTIONAL TESTS in Numeral 21,1 of these specifications, to make delivery of the GUARANTEES subscribed by the Manufacturer, with a duration of twenty-four (24) months as of the date.

The CONTRACTOR will have to commit itself to replace, to repair and to install without position some forLA COMPAÑÍAand of diligent and opportune form, of way to avoid consecuenciales damages toLA COMPAÑÍAby the cease of operation of any component, equipment or provided system, within a period of twenty-four (24) months, as of the date of company/signature of the Act of PROVISIONAL ACCEPTANCE.

Each and every one of the requirements demanded in documents are included in the GUARANTEES.

The CONTRACTOR will assume all the costs and expenses by desinstalación concept, transports from and to the site of location ofLA AMPLIACIÓN, reinstallation, technical attendance in site for test and beginning of anyone of the components and equipment object of reclamation by GUARANTEES.

If the defect or fault of operation cannot be corrected or be repaired, the CONTRACTOR will have to replace possible, more soon free of position forLA COMPAÑÍA, the materials, equipment and/or parts that have been reclamation object.

If the time required by the CONTRACTOR to repair to the equipment or component exceeds reasonable lapses and/or puts in risk the trustworthiness of the operations ofLA COMPAÑÍA, the CONTRACTOR will have to be diligent in providing a temporary solution with way to mitigate the possibility of causing consecuenciales damages. This will be carried out in mutual agreement entersLA COMPAÑÍAand the CONTRACTOR.

- PLAN OF QUALITY MANAGEMENT(PGC)

The CONTRACTOR will have to develop and to settle down a System of Management of Quality, that covers the management, engineering, tries, work inspection, materials and equipment, acquisition of certification, documentation and data of subcontractors, and construction of the facilities contemplated in the CONTRACT forLA AMPLIACIÓN. DichoSystem will have to assure the management quality like a whole, of all the works and activities that are contemplated forLA OBRA, from the same beginning of such works and activities to the total culmination of the same.

The CONTRACTOR will have to elaborate a Plan of Management of Calidad (PGC) that will follow during the execution of the WORK, which will have to be structured according to its own policy and system of the quality, and to be related to the nature, the reach and the complexity of the activities and contemplated works stops LA AMPLIACIÓN.

The CONTRACTOR will have to present/display, once granted the good pro for the execution of the WORK, the PGC for the revision and approval ofLA COMPAÑÍA. Encase that the CONTRACTOR did not present/display the referred Plan, could not give to beginning to the works object of the CONTRACT. The PGC presented/displayed by the CONTRACTOR will be reviewed byLA COMPAÑÍAfor their approval, of being originating, will be emitted in the meeting of beginning of the works. Any modification subsequent to the approved Plan will have to be sent for the approval of LA COMPAÑÍA.

The CONTRACTOR will have to settle down and to maintain an organization of Management of Quality during the execution of the WORK, which will have to guarantee the strict fulfillment of the approved PGC.

The PGC that presents/displays the CONTRACTOR, will have to contain, without limiting itself it, the following thing:

- Policy of Quality, establishing the objectives that are persecuted

- Plan of Quality ofla Ingeniería, fulfilling the indicated minimum requirements in Numeral 30,1. of this specification

- Plan of Quality ofla Procura, fulfilling the indicated minimum requirements in Numeral 30,2. of this specification

- Plan of Quality ofla Construcción, fulfilling the indicated minimum requirements in Numeral 30,3. of this specification.

- Procedure to follow for the handling of changes in the execution of the WORK.

- In his Supply, the CONTRACTOR will have to present/display a Preliminary Plan of Management of Quality of the WORK, being covered the three lines previously mentioned.

  - PLAN OF MANAGEMENT OF QUALITY OF ENGINEERING

The minimum requirements that the CONTRACTOR will have to fulfill in the Plan of Management of Quality la Ingenieríagive next:

All the pages of the Plan of Management of Quality must indicate:

- Number of Contract and Title of la Ingeniería

- Number and Date of revision (controlled document)

- “Elaborated by”, “Approved by” from the CONTRACTOR; and “Approved by” fromLA COMPAÑÍAwith the complete companies of the representatives of the CONTRACTOR.

- Procedures and lists of verification to use.

- Procedure for the handling of the nonconformities.

- Activities of Engineering by discipline settling down responsibilities for each one of the phases of execution of the WORK.

- Activities that will be executed by subcontractors. These activities will have to be detachhed by discipline and they will not have to be grouped if they own different characteristics.

- In each one of the lines of the Plan of Management of Quality la Ingenieríathe description of all the activities or tasks to be reviewed, verified and validated, presenting/displaying in summarized form will be due to indicate the following information:

- Brief description of the activity or task.

- Procedure, specification, norm ofLA COMPAÑÍA, norm of the CONTRACTOR, national or international norm, to being applied, indicating the number of the norm, section, aside and page.

- Person in charge of the procedure and approval, according to the established organizational chart.

- Characteristic or aspect of quality to review.

- Method or tool to use in the revision.

- Record format (to include Title and no. of codification).

- It does not have to present/display spaces without information or noticeable with “it does not apply”.

Additionally, the Plan of Management of Quality ofla Ingenieríawill have to contain copies of the following information:

- Summary of the reach of la Ingeniería.

- Cronogram of execution ofla Ingeniería, indicating any work subcontracted by the CONTRACTOR. This cronogram will have to be properly codified, signed and sealed by the representative of the CONTRACTOR.

- Organizational chart of the CONTRACTOR, properly signed and sealed by the representative of the CONTRACTOR. In this Organizational chart the positions must be indicated to carry out the works in correlation with the Plan of Management of Quality. Also, Quality will have to be indicated from the high level of responsibility to the supervisor responsible for all the activities related to the Plan of Management. If then subcontractors existed the organizational chart she will have to include them.

  - PLAN OF MANAGEMENT OF QUALITY OF LA PROCURA

The minimum requirements that will have the CONTRACTOR to include in the Plan of Management of Quality ofla Procura, occur next:

- Organization for the handling tries of it

- Detailed description of the equipment and materials that will be provided by companies subcontractors, Manufacturers or Suppliers

- Number and Date of the document of try

- Strategy of tries of materials/equipment and storage

- Procedure of request of purchase of the materials or equipment

- Procedure for the handling of the not-conformities.

- Procedure to follow for the handling of changes in the request of purchase of materials and equipment.

Form leaves from the Plan of Management ofla Calidadofla Procuraof the CONTRACTOR, the documentation on Quality control of the SUPPLIER. This documentation will have to be available for revision ofLA COMPAÑÍAand/or the ENGINEER OF the PROPRIETOR and will have to include, but a will not be limited:

- List of verifications, standard inspection and tests for the package and components within the provision reach, with its respective procedures of execution.

- Requirements of standard quality for forges

- Requirements of standard quality for smeltings.

- Procedures of repair of smeltings.

- Requirements of standard quality for made elements.

- Specifications of welding procedures - welding procedure specifications - applicable for made elements and repairs.

- Qualification of welding procedures - qualification of welding procedures (PQR) - applicable for made elements and repairs.

- Applicable procedures for heat treatments of tension lightening post-weld for made elements and repairs.

- Procedures applicable for Hydrostatic and/or pneumatic Test to static equipment and systems of pipes.

- Defect acceptance numbers and rejection for non-destructive testings.

- Criteria of balance for rotating elements.

- Procedures of test of components and operation of the units.

LA COMPAÑÍAit will specify the type and it reaches of the verifications, tests and inspection that will be applied to the components of the package. The SUPPLIER will carry out all the tests and inspection that comprise of their standard system of quality, even thoughLA COMPAÑÍAit will not have specified them. LA COMPAÑÍA it will indicate if the tests and inspection will not be testified, observed or testified.

  - PLAN OF MANAGEMENT OF QUALITY OF LA CONSTRUCCIÓN

The minimum requirements that will have to include the Plan of Management of Quality ofla Construcción, occur next:

- Procedure for the handling of the not-conformities.

- Activities of construction by discipline and contracted installation.

- Activities of inspection and tests, in work or factories.

- Procedure for Certification of hoisting equipment, machineries, vehicles and tools used for the WORK, by an credited being.

- Procedure for Certification of the technical personnel specialized for the WORK by a being or credited natural person.

- List of verification for startings and deliveries of equipment and facilities.

- Activities that will be executed by companies subcontractors. These activities will have to be detachhed by discipline and they will not have to be grouped if they present/display different characteristics to inspect.

- In each one of the lines of the Plan of Management of Quality la Construcciónthe description of all the activities or tasks to be inspected or to be evaluated, presenting/displaying in summarized form will be due to indicate the following information:

- Brief description of the activity or task.

- Procedure, specification, norm ofLA COMPAÑÍA, norm of the CONTRACTOR, National norm or the International, to being applied, indicating the number of the norm, section, aside and page.

- Person in charge of the inspection procedure and approval, according to the established organizational chart.

- Characteristic or aspect of quality to inspect and/or to evaluate.

- Method or tool of inspection or evaluation.

- Record format (to include Title and no. of codification).

- It does not have to present/display spaces without information or noticeable with “it does not apply” or “visual inspection”.

- Additionally, the Plan of Management of Quality ofla Construcciónwill have to contain copies of the following information:

- Summary of the reach of the works of Construction.

- Cronogram of execution ofla Construcción, which will have to indicate any work subcontracted by the CONTRACTOR and tries of materials of own provision. This cronogram will have to be properly codified, signed and sealed by the representative of the CONTRACTOR.

- Organizational chart of the CONTRACTOR, properly signed and sealed by the representative of the CONTRACTOR. In this Organizational chart the positions must be indicated to carry out the works in correlation with the Plan of Management of Quality. Also, the organizational chart will have to be indicated from the high level of responsibility to the supervisor responsible for all the activities related to the Plan of Management of Qualityla Construcción. Siof would exist then subcontractors will have to include them.

- The CONTRACTOR will have to maintain a representative of his organization of Quality in the site ofla Construcción, which will have to guarantee the strict fulfillment of the Plan of approved Management of Quality.

In the site ofla Construcciónlegible copies of the Plan of Management of Quality and of certificates of hoisting of equipment will have to stay, qualification of the soldering irons, electricians, operators of equipment, effective calibrations of machines to weld, equipment of measurement, test certificates, certificates of quality of materials, etc.

- BOOKS OF LA OBRA

When finalizingla Construcciónof the WORK, the CONTRACTOR will have to giveLA COMPAÑÍAto an original unit in and two copies of Books of the WORK, in Spanish language, with the following content:

- GENERAL (ORGANIZATION AND MANAGEMENT OFLA OBRA)

- General structure of Libro of the WORK, including:

- Analytical structure of the Works.

- Organization of the WORK.

- Responsibilities.

- Qualification of the Personnel.

- Planning and Control of the WORK, including:

- Manual of Coordination of the Project.

- Plan of Execution of the WORK.

- Manual of Planning and Control.

- Monthly information of Progress.

- Closing report of the WORK.

- Plan of Management of Calidad (PAC).

- Management of the WORK

- Engineering, Tries and Construction

- Internal audits of Quality, including/understanding:

- Program of Audit of the Systems and Processes.

- Qualification of the Auditors.

- Documents of Security, Hygiene and Atmosphere, including:

- Specific plan of Security, Hygiene and Atmosphere.

- Considerations of Environmental impact taken during la Construcción.

- Administrative data, including:

- Meetings of Managemental Coordination.

- Communications and Correspondences.

- Control of Changes of Reach.

- ENGINEERING

- Documents of Engineering.

- Leaves Summary of Isometric Planes and, indicating: No. of planes, no. Of Isometric, no. of details.

- Formats of Control of Isometric: Identification, Diameters (yes it applies).

- Manuals of Operation of each System or Facility of the EXTENSION.

VOLUME - IT TRIES

- Control of Purchases and Evaluation of sub. - contractors, including:

- Criterion of Evaluation of Suppliers and sub. - contractors.

- Lists of Suppliers and sub. - contractors.

- Control of Material/Equipment provided byLA COMPAÑÍA, including the Control program of provided Material (material balance).

- Inspector certification of the CONTRACTOR for revision and approval of documents of engineering of the PROVEDOR and for certification of tests of equipment in factory.

- Dossier' s of Equipment Majors, discriminated by System: Mechanics, electrical and of Instrumentation (5 copies), according to the particular specifications of each System, that includes like minimum the following information:

- General description of the Equipment

- Manuals of Installation, Operation and maintenance, in Spanish language.

- Identification of the Manufacturer and/or Salesman (name, direction, person contact, etc.)

- Engineering specifications/data sheet (with which the equipment made)

- Planes manufacture certificates

- Catalogs of auxiliary parts of the equipment

- Guides of Diagnosis of faults (“troubleshooting”)

- Documentation applicable to the manufacture (Reports of inspection, certificates of quality of materials, factory tests, act of liberation of the equipment, guarantees, copy of the order of purchase)

VOLUME IV- CONSTRUCTION

- Control of the Processes of Construction and Assembly, including:

- Mechanic.

- Electricity.

- Civilian.

- Instrumentation and Automatization.

- Telecommunications

- Preparation of Surface, Painting and Coating.

- Inventory of Equipment of Process.

- List of Procedures.

- Full formats of Registry of the Processes.

- Formats and procedures of verification of civil, mechanical, electrical installation and of instrumentation and control.

- Planes like Constructed

- Drafts of Meetings realized duringla Ejecuciónof LA  OBRA

- Registries of Heights and Amounts of Fillings Loaded in the Equipment.

- Daily reports of Personnel and Equipment.

- Registries of Certification of Equipment of Hoisting and “Holiday Detector”.

- Leaves Summary of them Equipment of Hoisting where the General Model is indicated, Capacity, Certification.

- Inspection and Test, including:

- Plan of Inspection.

- Defect acceptance numbers or Rejection.

- Criteria for Identification of the State of la Inspección.

- Full formats of Manholes.

- Inspector certification of the CONTRACTOR.

- Statistical control of the Processes: Weld, Coating, Painting, etc., (to include graphs).

- Tests referred to the Isometric ones. The isometric ones will have to present/display summary of: Number of realized Welds, Percentage of Totalización of RX, Pressure of Accomplishment ofla Prueba Hidrostática(yes it applies), Preparation of Surface (type), Amount of Coats of Paint, Identification of X-ray.

- Specification of the Painting Procedures, Specification of the Welding procedures and heat treatments, Record of the procedures of Qualification of Welds, List of Soldering irons, registries of Soldering irons and Card, Control of Welds by Soldering iron, taken Analyzes and Remedial actions.

- Reports of Physical, Chemical Tests and Tests (laboratory).

- Certification of Materials: Consumable and nonConsumable.

- Summary of Materials: Type of Material, no. of Identification, no. of Tap, Manufacturer and Diameter (yes it applies).

- Manhole of Covering of Materials: No. and Type of Received Material, Date of Delivery, no. of Order of Delivery, Control of Reception.

- Registries of Calibration of: Machines To weld, Painting Pressure gauges, Cash registers, Equipment, etc.; presenting/displayingla Hoja Resumenof the Equipment where it is indicated: Model, Serial, Capacity, Last Date of Calibration.

- Leaves Summary of X-rays, where it is indicated: Name of the X-ray Companies, the Equipment, no. of X-ray Reports Elaborated, Nº de Radiographed Juntas, % by ricochet, Amount of Repairs, Analysis of the Problem (yes it applies).

- Reports of X-rays.

- Leaves Summary of Hydrostatic Tests, where it is indicated: The Equipment, Normal Pressure of Operation, Maxima Pressure of Operation, Design pressure, Pressure ofla Prueba, Minimum Time of Duration ofla  Prueba, to annex copy of the disc (for the hydrostatic test).

- Reports of Hydrostatic Test (lines, interconnections, carretos of pipe, etc.).

- Leaves Summarize of Penetrating Dyes: Corresponding number of Reports and Pieces or another non-destructive testing.

- Leaves Painting Summary where anchorage profile is indicated, thicknesses of painting, masking time, no. of the Equipment.

- Reports, Control and Procedures of Application of Paintings and/or Internal and External Coating (sanded and painting)

- Procedure of Application of Internal and External Coating (yes it applies) and Control of its Application (it draws resin from, PEAD, sleeves, etc.).

- Registries of Tests with Electromagnetic Tool

- Procedures and registries of tests in site for mechanical, electrical components, of bows of instrumentation and control and verification of conditions of process guarantee of each system

- Procedures and electrical registries of tests in site to systems and components and of verification of conditions of guarantee and operation of each system

- Plan of Securing ofla Calidad:

- Control of the Equipment of Inspection and Measurement, including:

- Inventory of the Equipment and Instruments (capacity, condition of operabilidad, certification and program of calibration).

- List of documented Procedures to control, to calibrate and to realize maintenance.

- Control of the Conditions of Not-Conformity, including/understanding:

- Identification and Report of Opportunities of Improvement.

- Remedial actions.

- Manuals of Maintenance

- PERMISSIONS

The CONTRACTOR will have to transact and to obtain all the permissions required byLA COMPAÑÍAand/or the Governmental Authorities, for the execution of the WORK, these include, among others: Municipal mayorship, Ministry of the Popular Power forla Infraestructura(MINFRA), etc. As far as the permissions of the Ministry of the Popular Power for Ambiente (MINAMB), such as: Authorization of Occupation of the Territory (AOT), Authorization stopsla Afectaciónof Recursos Naturales (AARN) and the Registry of Activities Susceptible To degrade the Atmosphere, will be of COMPANY responsibilityLA COMPAÑÍA. LAwould collaborate with the CONTRACTOR in the pertinent managements, being understood that these functions correspond in their overall nature to the CONTRACTOR and will be of its complete responsibility.

The CONTRACTOR must maximize his force of work with existing resources in the zone, reason why it is necessary, to inquire with the municipal authorities on the existing cooperative, operating organizations and other being, in order to obtain from these organizations the required human resource for the construction of LA AMPLIACIÓN.

As a reference one appears in Table 32.1, the responsibilities of the COMPANY and the CONTRACTOR as far as procedure and obtaining of permissions and authorizations:

Nº table 32,1 Responsibilities for the Obtaining of Permissions

| DOCUMENTO/REGISTRO | THE COMPANY | THE CONTRACTOR |
| --- | --- | --- |
| Registry of Activities Susceptible To degrade the Atmosphere of the MINAMB. | X |  |
| Registry of the company before Municipal Property | X |  |
| Permission regarding load and unloading of equipment to install for the construction ofLA AMPLIACIÓN, sent byla AlcaldíaPoliceman. |  | X |
| Permission of Construction of the Municipal Mayorship |  | X |
| Permission of the MINFRA for the Transport and mobilization of Heavy Equipment |  | X |
| Authorization of the MINFRA for incorporation of signaling for the operation stage | X |  |
| Programming and Procedure of permissions of work before the Office of Regional Load and the National Center of Management of the Electrical System, |  | X |
| Approval of WORK of organisms public for foreign personnel |  | X |
| Approval of Firemen for the habitability of the EXTENSION. |  | X |
| Approval of Firemen of the project of the System of detection and fire extinguishing |  | X |

- REQUIREMENTS OF SECURITY, HYGIENE AND ATMOSPHERE

  - BASIC PREMISES

The CONTRACTOR must fulfill the different dispositions settled down inla Constituciónfromla República Bolivarianaof Venezuela, in the laws, decrees, regulations and resolutions in the matter of Security, Hygiene and Atmosphere. In Numeral 3, “CODES AND APPLICABLE NORMS” of this specification, appear, to way of reference, norms and decrees issued byla República Bolivarianaof Venezuela of strict fulfillment in the areas of Security, Hygiene and Atmosphere.

Jointly withla Oferta, the CONTRACTOR will have to present/display a Specific Plan of Security, Hygiene and Atmosphere for the WORK, the Plan will have to contain the aspects that are applicable to the WORK, including the cronogram of activities for his fulfillment. This Plan once reviewed and approved will comprise of the CONTRACT.

The CONTRACTOR will have to count on an organization of Security, Hygiene and Atmosphere, that to him the technical support for the suitable application provides with this requirement, especially in: the processes of risk identification and their preventive measures, evaluation of aptitude in Security, Hygiene and Atmosphere, evaluation of the Specific Plan of Security, Hygiene and Atmosphere, Pre-beginning of the WORK and Evaluation of Performance.

The CONTRACTOR will have to replace so many inspectors of Security, Hygiene and Atmosphere as she requires by the norms and Venezuelan laws and in agreement with the complexity or magnitude of the entrusted work.

  - INDUSTRIAL SECURITY

The CONTRACTOR will be forced to fulfill the dispositions contained in the national laws and effective norms in the matter of Hygiene and Industrial Security, as well as any international norm thatLA COMPAÑÍAshe indicates.

The CONTRACTOR /3.20. /3,21 and 3,22 of these specifications and all those norms related tola Prevenciónof Accidents.

The CONTRACTOR will have to fulfill for this CONTRACT with the notification of inherent risks to the works for which she has been contracted, according to stipulated in paragraph one of the article 6to. Ofla Ley Orgánicade Prevención, Conditions and Environment of Work.

  - HYGIENE

The CONTRACTOR will have to maintain the site of the free WORK of accumulations of materials of remainders and wastes caused by the execution of the construction and will have to reasonably maintain the storage and work areas in a condition ordinate and that does not represent risks for the personnel who works there.

The CONTRACTOR will have to present/display the registry of the Ministry of the Popular Power forla Energíaand Petroleum, the handling and use of generating sources of Ionizing radiations, as well as a program of Radiological safety, Plan of Emergencia and a procedure of Transport of Sources. Similarly, he will have to adjust to the technical dispositions contained in the decree 2,210 “Practical standardses and Procedures for Manejo de Radioactive Material”, of the 23 of April of 1.992.

The served waters that are originated during the phase of construction can be prepared in septic tanks and drains, or suitably treated by the CONTRACTOR, being this aspect submissive previously the revision and approval of LA COMPAÑÍA.

() The site (s) of boat of the disposable materials product of the earthwork, will be defined byLA COMPAÑÍA, during the development of the stage of construction of LA AMPLIACIÓN.

  - ATMOSPHERE

The Study of Impacto Ambiental (EIA) is a requirement indispensable established by the Ministry of the popular Power for Ambiente (MINAMB) for all the projects of works and services that are executed in the national territory, like previous step for the obtaining ofla Autorizaciónof Occupation of the Territory (AOT), Authorization forla Afectaciónof Recursos Naturales Renovables (AARN) and the Registry of Activities susceptible To degrade the Atmosphere. In AOT and AARN the MINAMB establishes the conditions under which the affectation of the atmosphere will be developed during the stages of execution of the WORK, adjusting in addition, to the program of of measures and conditions established in the approved environmental evaluations. The results of this study, as well as of the measures and/or recommendations emitted in the AARN, to diminish or to mitigate the environmental impact in the phases of design, construction, operation and maintenance ofLA AMPLIACIÓN, comprise of documents to provide byLA COMPAÑÍAand must be of strict fulfillment on the part of the CONTRACTOR.

The CONTRACTOR, person in charge by the execution of the works including in this specification, as well as the workers who toil in the same, are subjects to the fulfillment of the different dispositions settled down inla Constituciónfromla República BolivarianaVenezuela and the laws, decrees, regulations and resolutions in the matter of Security, Hygiene and Atmosphere. To reference way they appear in Numeral 3, “CODES AND APPLICABLE NORMS” of this specification, the norms and decrees issued byla República Bolivarianaof Venezuela of strict fulfillment in the environmental areas.

During the construction stages, the CONTRACTOR will have to take the measures necessary to avoid or to diminish the impact caused to the atmosphere. In this sense, he will be able or have to reforest sensible areas, to maintain the species vegetal and to avoid any type of additional intervention.

The CONTRACTOR will have to orchestrate all the necessary measures of protection of the environment, related to the areas of influence of the works to be executed, as much the settled down ones in individual form like the settled down ones byLA COMPAÑÍA, besides the settled down ones in the applicable legislation. The CONTRACTOR will be forced to guard by his fulfillment and will be responsible for all the actions that could carry outLA COMPAÑÍAbefore any governmental being, when personal detecting that and/or teams of the CONTRACTOR, by negligence, inexperience, negligence and/or ignorance, have realized activities to the detriment of the environment.

- ORGANIZATION OF THE CONTRACTOR

The CONTRACTOR will have to integrate an organization who will have to include all the resources of personnel in her different scales professional, working and working in order to execute each and every one of the phases of the WORK, to develop the activities of engineering, supervision, planning and control, tries, installation, assembly, construction tests, training, necessary to fulfill all the technical and administrative aspects that the WORK requires, being the CONTRACTOR the unique person in charge by the execution of each and every one of the activities of the WORK before indicated. The CONTRACTOR will have to brief for the moment of the company/signature of the CONTRACT, the Curriculum vitae of each and every one of the integral professionals of his organization, as well as the one of one second person who can replace the holder in case of partial or total retirement during the run time of the WORK.

The propose organization as well as the personnel who the Integra will be put under the approval ofLA COMPAÑÍAbefore beginning the works, having to be said personal highly described and to own the sufficient labor experience with multidisciplinary groups and in similar works to raised here. This personnel will work in the offices of the CONTRACTOR.

The CONTRACTOR will have to assign a Manager of the WORK that will have to be authorized to act in the name of the CONTRACTOR and with whomLA COMPAÑÍAwill be able to make consultations to any reasonable hour and which could not be removed without his authorization. Also he will have to postulate a Manager of Engineering and a Manager of Construction, who could not be removed without the authorization ofLA COMPAÑÍA. Asísame will integrate the organization, leaders of discipline, engineers and field engineers. In particular one will be due to maintain resident an engineer described, inspecting, a work controller, personnel of supervision and quality control, technician of integral protection, for this type of work, resident in the site of the works by the term of the same.

The functions concerning management and coordination will have to be in favor preferably carried out of professionals enabled with classification of level superior at level 6 and the Manager of the WORK will have at least to be a P-10 professional, in agreement with the professional scale of the School of Engineers of Venezuela (C.I.V.).

The Manager of Construction will be authorized to speak and to act by account and name of the CONTRACTOR, being exerted the functions to represent it during the execution of the WORK. The breach of this requirement is sufficient reason so thatLA COMPAÑÍAit can order the paralyzation of the works without the CONTRACTOR can demand indemnification some or payments per lost time, nor prorogation of the CONTRACT.

Before carrying out the mobilization to the site of the WORK, the CONTRACTOR will emit an authorization, with copy forLA COMPAÑÍA, in which the appointment of the Manager of Construction certifies to act in its name, in the pertinent subjects to the execution of the WORK.

In the particular case of the soldering irons, the use will be only allowed as which they have been described and approved byLA COMPAÑÍAand at any time during the execution ofLA OBRA, the ENGINEER OF the PROPRIETOR will be able to suspend and to ask for the contingent replacement of some noncompetent soldering iron.

Of equal way the CONTRACTOR will be responsible for the technical supervision, services, protection and industrial safety inspection, necessary to fulfill the pertinent measures for the execution of each one of the games, quality control, monitoring, administration, utilities, taxes and unforeseen expenses to executeLA OBRAaccording to the planes, specifications, norms, contract and instructions of the inspection.

If in the opinion ofLA COMPAÑÍA, the protection and industrial security, the securing of the quality is insufficient or he is not apt, the CONTRACTOR will have to assign to the additional personal work or to replace it by particularly described personnel.

AlsoLA COMPAÑÍAthe right is reserved to ask for to the CONTRACTOR the desincorporación of the personnel who properly is not enabled for the execution of the assigned works or that demonstrates to inexperience or ignorance in the execution of the same.

The CONTRACTOR will be able to transfer or to remove personnel supervisorio or personnel nails under its control inLA OBRA, if its opinion this one incurs inefficiencies or commits serious offenses, without requiring the previous approval ofLA COMPAÑÍA, nevertheless is his to have to notify it in writing toLA COMPAÑÍAat least with reasonable anticipation.

La Organizaciónproposal by the CONTRACTOR will have to include like minimum without being limited it the following positions:

- POSITIONS STOP LA EJECUCIÓN DE LA OBRA

- Manager of the WORK

- Planner/Controller of the WORK

- Manager of Engineering

- Leader of Mechanical Discipline

- Leader of Discipline Processes

- Leader of Civil Discipline

- Leader of Discipline Instrumentation

- Leader of Discipline Electricity

- Supervisor of Tries of Materials

- Manager of Construction

- Planner/Controller of Construction

- Mechanical supervisor of Construction

- Supervisor of Civil Construction

- Supervisor of Construction Instrumentation

- Supervisor of Construction Electricity

- Supervisor of Security and Environmental hygene

- Supervisor of Labor Relations/Handling of the Surroundings

- Leader of Securing of Quality/Engineering Construction

- Personnel of Engineering/Working Workers/

- Annex 1: BUDGET OF LA OBRA

BUDGET OF LA OBRA

REACH: It includes the development ofla Ingeniería Básicaand of Detail, It tries, Inspection, Transport to the Site, Construction, Precommissioning, Commissioning, Tests of Good Operation, Expenses, Starting and Beginning of Nationalization, Tax, Guarantee, Insurance (IPC), GLOBAL SUM, of all the equipment, systems and facilities necessary to obtain the construction and putting in Normal Operation ofLA AMPLIACIÓNa a capacity of 67.8 MW (ISO), also comprises of the reach ofLA OBRAthe autosoportada Tower of telecommunications and the training for the technical and professional personnel of operation and maintenances, the special spare parts and tools.

| Games | Description of Games | Amount | Component in Bolivars | Component in Dollars | Total bolivars |
| --- | --- | --- | --- | --- | --- |
| 1. | STUDIES OF CHARACTERIZATION OF THE SITE AND ENVIRONMENTAL IMPACT |  |  |  |  |
| 1.1 | TOPOGRAPHICAL RISE | S.G. |  |  |  |
| 1.2 | GEOTECHNICAL STUDY | S.G. |  |  |  |
| 1.3 | STUDY OF ENVIRONMENTAL IMPACT (EIA) | S.G. |  |  |  |
| 2 | BASIC ENGINEERING AND OF DETAIL |  |  |  |  |
| 2.1 | BASIC ENGINEERING AND OF DETAIL | S.G. |  |  |  |
| 3. | GENERAL CIVIL WORKS |  |  |  |  |
| 3.1 | PRELIMINARY OPERATIONS | S.G. |  |  |  |
| 3.2 | FOUNDATIONS FOR ELECTRICAL AND MECHANICAL EQUIPMENT | S.G. |  |  |  |
| 3.3 | QUARTER OF BOARDS | S.G. |  |  |  |
| 3.4 | TANQUILLAS | S.G. |  |  |  |
| 3.5 | LARGE STONE BENCHES OF POWER, COMMUNICATION AND CONTROL | S.G. |  |  |  |
| 3.6 | DEMOLITIONS | S.G. |  |  |  |
| 3.7 | RECONSTRUCTIONS AND/OR EXTENSIONS | S.G. |  |  |  |
| 4. | PACKAGE OF GENERATION |  |  |  |  |
| 4.1 | INSPECTION, TRANSPORT, INSURANCES AND GUARANTEES OF THREE (3) TURBOGENERATORS TO GAS AND ITS CORRESPONDING AUXILIARY MODULES. It includes: national transport from port of debarkation located in the Margarita island to the site of the work, nationalization, insurances and guarantees. | S.G. |  |  |  |
| 4.2 | INSTALLATION AND INTERCONNECTION OF THREE (3) TURBOGENERATORS TO GAS AND ITS CORRESPONDING AUXILIARY MODULES. It includes: installation, assembly, tests, beginning and foreign technical attendance. | S.G. |  |  |  |
| 4.3 | ELEVATING TRANSFORMING TRANSPORT AND INSTALLATION OF 115 POWER 13.8 kV/kV. It includes: national transport from port of debarkation located in the Margarita island to the site of the work, nationalization, insurances and guarantees, installation, assembly, tests, beginning and foreign technical attendance. | S.G. |  |  |  |
| 5. | CONNECTIONS TO EXISTING SYSTEMS |  |  |  |  |
| 5.1 | CONNECTION TO THE SUPPLY APPARATUS OF FUEL | S.G. |  |  |  |
| 5.2 | CONNECTION TO THE WATER SYSTEM ON WATCH | S.G. |  |  |  |
| 5.3 | CONNECTION TO THE WATER SYSTEM DESMINERALIZADA | S.G. |  |  |  |
| 5.4 | CONNECTION TO THE FIRE PROTECTIVE SYSTEM | S.G. |  |  |  |
| 5.5 | CONNECTION TO THE TREATMENT SYSTEM AND DISPOSITION OF INDUSTRIAL EFFLUENTS | S.G. |  |  |  |
| 5.6 | CONNECTION TO THE COMPRESSED AIR SYSTEMS | S.G. |  |  |  |
| 6. | ELECTRICAL SYSTEM AND CONTROL |  |  |  |  |
| 6.1 | SYSTEM OF DAMPING OF ELECTRICAL DISTURBANCES | S.G. |  |  |  |
| 6.2 | CONNECTION TO CONTROL ROOM | S.G. |  |  |  |
| 6.3 | FACILITIES FOR ELECTRICAL EQUIPMENT |  |  |  |  |
| 6.4 | SYSTEM OF EARTHING | S.G. |  |  |  |
| 6.5 | SYSTEM OF FEEDING AND DELIVERY OF ENERGY DC OF THE GENERATION UNITS |  |  |  |  |
| 6.6 | SYSTEM OF ELECTRICAL PROTECTIONS | S.G. |  |  |  |
| 6.7 | EXTERNAL LIGHTING SYSTEM | S.G. |  |  |  |
| 6.8 | INTEGRATION TO THE DISTRIBUTED CONTROL SYSTEM | S.G. |  |  |  |
| 6.9 | INTEGRATION TO THE DETECTION SYSTEM AND FIRE ALARM | S.G. |  |  |  |
| 6.10 | INTEGRATION TO THE SYSTEM OF PLANT SHUTDOWN | S.G. |  |  |  |
| 7. | SPARE PARTS | P.U. |  |  |  |
| 8. | SPECIAL TOOLS | P.U. |  |  |  |
| 9. | TRAINING | P.U. |  |  |  |
|  | TOTAL |  |  |  |  |

Notes:

: Global sum

P.U.: Unitary price

- ANNEX 2. BASIC ENGINEERING AND OF DETAIL

| Code | PRODUCT |
| --- | --- |
|  | GENERAL DOCUMENTS |
|  | GENERAL |
|  | List of Planes and Documents |
|  | Description of the Process |
|  | FiloSofia of Operation and Control of Planta |
|  | Simulations Bases and Premises |
|  | Heat balance of Planta |
|  | Hazop analysis |
|  | Schematic diagram of plant. |
|  | Diagram of Water Balance of plant. |
|  | Block diagram of Process |
|  | Symbolism of Instrumentation |
|  | Plane of Mechanical Symbolism |
|  | Plane of Symbolism Electricity |
|  | Plane of General Implantation |
|  | Plane of Identification of Areas of Planta |
|  | Program of Technical Training for Operation and maintenance |
|  | DESIGN CRITERIA |
|  | Criteria of Civil Design |
|  | Criteria of Design Electricity. |
|  | General criteria of Design |
|  | Criteria of Design Instrumentation |
|  | Criteria of Design of the System of Communication |
|  | Criteria of Mechanical Design |
|  | Criteria of Design of Processes |
|  | STUDIES OF SITE CHARACTERIZATION |
|  | Topographic Descriptive-Rise memory. |
|  | Study of Geotechnical |
|  | Topographical survey |
|  | Study of Environmental impact |
|  | GENERAL SPECIFICATIONS |
|  | MECHANICS |
|  | Specifications of Weld |
|  | Painting specifications |
|  | Specifications of Hydrostatic and Pneumatic Test |
|  | Specifications of Materials of Pipes |
|  | Specifications of Supports of Pipes |
|  | Specifications of Heat insulation |
|  | Specifications of Coatings of Pipes |
|  | Specifications of Manufacture and Installation of Pipes |
|  | Specifications of Valves |
|  | Specifications of Containers under pressure |
|  | Specifications of Utilitarian Centrifugal Pumps, Process and Transference |
|  | Installation specs of the System Against Fire |
|  | INSTRUMENTATION |
|  | General specifications Instrumentación |
|  | Particular specifications of Instruments |
|  | Cause-Effect diagram |
|  | ELECTRICITY |
|  | Specification of Center of Distribution of Power |
|  | General Cable specification of Low Tension |
|  | General Cable specification of Average Tension |
|  | MEMORIES |
|  | DESCRIPTIVE MEMORY |
|  | Descriptive memory of Processes |
|  | Civil Descriptive memory |
|  | CALCULATION MEMORIES |
|  | MECHANICS |
|  | Memory of Calculation of Thickness of Pipes |
|  | CIVILIAN |
|  | Memory of Calculation earthwork/road |
|  | Memory of Calculation rainwater Drainage |
|  | Memory of Calculation of white waters, black waters and oily waters |
|  | Memory of Calculation of Foundations of Equipment and containers |
|  | Memory of Calculation Drawer of Drainage |
|  | ELECTRICITY |
|  | Memory of Calculation of Feeders of Loss and Average Tension. |
|  | Memory of Calculation Enmeshes of Earth. |
|  | Memory of Calculation of Center of Distribution of Power. |
|  | Memory of Transforming Calculation of Services |
|  | Memory of Calculation Short circuit |
|  | Memory of Outer Calculation of Illumination. |
|  | PROCESSES |
|  | Memory of Calculation Processes |
|  | List of Tie-in |
|  | INSTRUMENTATION |
|  | Memory of Calculation Instrumentation |
|  | LISTS |
|  | Bill of material and Electrical equipment |
|  | Electrical Cable list and Canalizations |
|  | Mechanical bill of material and Equipment |
|  | List of Lines of Processes |
|  | TYPICAL DETAILS |
|  | Typical details of Electrical system of Instruments |
|  | Typical details of Installation of Instruments to Takings of Process |
|  | Typical details of Supports |
|  | Typical details of Pneumatic Installation of Instruments |
|  | Typical details of Coupling boxes |
|  | Details Bancadas and Tanquillas Instrumentation |
|  | Diagrams of Bows |
|  | GENERAL CIVIL WORKS |
|  | Specifications of Construction of general civil Works. |
|  | General Modified Topografía plants |
|  | General Pluvial Drenaje plants |
|  | Details of Pluvial Drainage |
|  | Plane of General Implantation |
|  | TURBOGENERATORS |
|  | Specifications of Turbogenerators provided by the COMPAÑÏA |
|  | Installation specs and Interconnection Turbogenerators |
|  | Foundation for Turbogenerators - It plants, Sections, Piles |
|  | Leaves of Technical Characteristics Guaranteed Board of Average Tension 13.8 kV Auxiliary Services |
|  | Leaves of Technical Characteristics Guaranteed Center Engine control of Auxiliary Turbogenerators |
|  | Single-wire diagram Turbogenerators |
|  | System of Protection Turbogenerators |
|  | Diagram Unifilar.Tablero de Distribución de Auxiliares Turbogenerators |
|  | Transforming specification of Auxiliary Services 13.8 /0, 480-0,208 kV |
|  | Leaves of Guaranteed Technical Transforming Characteristics of Services. |
|  | SUPPLY APPARATUS OF FUEL (SSC) |
|  | Installation specs and Interconnection of SSC |
|  | DFP including mass balance |
|  | Descriptive memory |
|  | Specifications of Instrumentation and control of the SSC |
|  | Single-wire diagram SSC |
|  | List of Instruments |
|  | List of Signals of Entrance and Exit of Instruments of the SSC |
|  | Bill of material and Equipment |
|  | List of Lines |
|  | Data sheet Instruments of Instrumentation and control of the SSC |
|  | Plane of Route of Pipe |
|  | DTI of the SSC |
|  | SUPPLY APPARATUS OF WATER OF SERVICES (SAS) |
|  | Installation specs and Interconnection of SAS |
|  | Plane of Route of Pipe |
|  | SUPPLY APPARATUS OF WATER DESMINERALIZASA |
|  | Installation specs and Interconnection of SAD |
|  | Plane of Route of Pipe |
|  | SYSTEM OF CONNECTION TO THE SYSTEM AGAINST FIRE |
|  | Installation specs and Interconnection of SSC |
|  | Plane of Route of Pipe |
|  | SYSTEMS COMPRESSED AIR |
|  | Installation specs and Interconnection of the Package of Compression of Air for Instruments and Service |
|  | Specifications of Instrumentation and control of the Air Package of Instruments |
|  | Single-wire diagram Sist. Compressed air |
|  | List of Instruments |
|  | List of Signals of Entrance and Exit of Instruments Compressed air System |
|  | Data sheet Instruments of Instrumentation and control of the Air Package of Instruments |
|  | Plane of Route of Pipe of Air of Instruments and Service |
|  | List of Lines System of Air of Instruments and Air of Services |
|  | Diagram of Air Distribution of Instruments |
|  | Diagram of Air Distribution on watch |
|  | DTI Air System of Instruments and Air of Services |
|  | ELECTRICAL SYSTEM |
|  | GENERAL |
|  | Motor leaves of Guaranteed Technical Characteristics of AC voltage |
|  | General Single-wire diagram |
|  | Single-wire diagram Board Average tension. |
|  | CONTROL ROOM |
|  | Details of Electrical Interconnection |
|  | Details of Interconnection of Signals |
|  | ELECTRICAL SUBSTATION OF AVERAGE TENSION |
|  | Specification of Switchgear Average Tension 13.8 kV |
|  | Leaves of Technical Characteristics Guaranteed Switchgear Average Tension Common Services |
|  | SYSTEM OF EARTHING |
|  | Specifications Earthing System |
|  | Plane of System of Putting Earth |
|  | POWER BOARD |
|  | Leaves of Guaranteed Technical Characteristics of Auxiliary Systems |
|  | Single-wire diagram System Auxiliary Services |
|  | LARGE STONE BENCHES OF POWER, COMMUNICATION AND CONTROL |
|  | Route of Conductors and Large stone benches of Power Electricity |
|  | Route of Conductors and Large stone benches Instrumentation |
|  | EXTERNAL LIGHTING SYSTEM |
|  | Specification of Lights for Exteriors |
|  | Outer plant of Illumination |
|  | Route of Conductors and Large stone benches of Outer Illumination |
|  | DISTRIBUTED CONTROL SYSTEM |
|  | Architecture of the Distributed Control system |
|  | SYSTEM OF DETECTION AND FIRE ALARM |
|  | Specification of the System of detection of fire and gas |
|  | SYSTEM OF PLANT SHUTDOWN |
|  | Specifications of Systems of Shutdown of Plant |

- ANNEX 3. SUPPLY APPARATUS OF FUEL LÌQUIDO