PROJECT DESIGN BASIS

Project Name and Location – Somanga Power Plant, Somanga, Tanzania

Nearest City – Dar es Salaam, Tanzania

Project Proposal Number	T 1108					Due Date 15 March 2011

Proposed COD Date -  2012

Customer Name and Address						EGT POWER LTD

801 Twin Tower Baniyas Street

P.O.Box 15162 Dubai, UEA

Site Information:

Elevation - 180 ft						Av RH - 61 – 96%

Temp High – 102 deg F						Temp Low -  50 deg F

Design Temp – 80 deg F						Design RH – 78%

Design Wind Speed – 80 MPH					Direction

GENERATION and MAJOR EQUIPMENT:

Type and Size Generation –					 Two GE 9171 (123 MW)

GTG Exhaust Stack Req’d – 					Height – Yes – 60’

Water Injection, Sprint, Evap Cooling Req’d – 			Water Injection Req’d

Emergency / Black Start Generation Required – Type / Size – 	Yes 750 KW - DFO

HRSG Required, Type, Size, Pressures – No Future

Steam Turbine Generator Required – Type / Size –No  Future

CIVIL / STRUCTURAL:

Soil Bearing PSF – Assume 1500 psf			Piles Required – Assume None

Soil Boring Responsibility – PES Contractor

Buildings Required:

.. Office/Control – Size – Yes Pre Fab – 50’x60’ – 12’ Eve

.. Warehouse – Size Yes Pre Fab – 60’x75’x 14’ Eve      	Crane 10 Ton 1 Bay

.. Water Treatment Bldg – Size – Yes Pre Fab 50’x75’x14’ Eve

.. DFO Treatment Shed – Size - None

.. Electrical Utility Bldg – Size – One each Pre Fab 50’x60’14’ Eve – AC Electrical Room

.. Substation Bldg – Size – One each Pre Fab 15’x20’x12’ Eve w/ AC

.. Guard House – Size – One Pre Fab 15’x15’x10’ Eve AC

Soil Drainage Required – Type – Swales and ditches to Owners ditch

Perimeter Fence Required – Type – 8’ w/ Barbed Wire

Oily Waste Water Drain Required w/ Separator – Yes PVC Pipe – O/W Separator

Waste Oil / Waste Water Tank Required – Size – 10,000 gal waste oil

Sludge Tank Required – Size - none

Plant Roads Required – Type – yes – Black Top

Plant Parking Lot Required – Type and Size – Yes 75’x200’ Black Top

Site Gravel Required – Type and Depth – Yes over plant 6”

MECHANICAL

Fuel Requirements:

..  Dual Fuel and Type – Single – Fuel Gas

..  Natural Gas Pressure Available – Assume 1000 psig 20 KM away – prepare alternate price for 20 KM pipeline.

.. Gas Compression Required - Type and Number – Shed – assume none

..  Fuel Gas Heating Required – Type – assume yes size unknown

..  DFO / HFO Treatment Required - none

..  HFO Heating Required – Type/Size - none

.. HFO / DFO Truck Unloading Required - none

.. Days of HFO / DFO Storage Required - none

Water Requirements:

.. Water Injection, STIG, Evap Cooling, HRSG Required – Assume NOx water- no evap – no HRSG

.. Demin Treatment Required – Yes for water injection and water wash

.. Potable Water Treatment Required – Quantity – Yes 1000 GPD

.. Source of Raw Water – Type – Assume well water reasonably good

.. Fire Water Required – Plant, GSU,other - No

.. Fire Water Equipment Required – Type - No

.. Days of Water Storage Required – Raw/Fire/Demin/Evap/RO /Potable –

Raw Water 3days	Demin Water 2days		Potable Water – 1000 Gal

Electrical:

High Voltage: 	132 KV ?						Frequency: 50 Hz

.. Generated Voltage –11 KV

.. GSU Required / High Voltage / No. Windings – GSU Req’d, 132 KV, Two Winding

.. Substation Required – Type – Assume Simple Radial

.. SF6 Breaker / Disconnect / Required – Quantities – 2ea SF6 Brkrs, 3 Disconnects, Dead End Tower, Static Wire

.. Metering / Protective Relaying Required – Yes

Low Voltage:

.. Low Voltage – 400 volt

.. Aux Transformers Required – Voltage – Type of Configuration 11.5KV/400volt, Utility type configuration

.. Type of Distribution  Building – PDC, Pre Fab, Other – Pre Fab Electric Utility Bldg 50’x60’

.. Area Lighting Required – Type – Yes 40 ft Metal Poles – Sodium Vapor Floods

Instrument and Control

.. PLC Plant Control System Req’d - Yes

.. GTG and GCP Panels – In Electric Utility Bldg w/ Batteries and Chargers