- Engineering Details

Thermo Plant Generating Electric Energy Josefa Camejo

- Pages1-3

Index

- Page 4

- 1.	OBJECTIVE

This document describes the scope of all  work related to the mechanical montage, alignment and starting up of the Siemens Westinghouse A-3001 Turbo generating Unit Model W501F belonging to Pacific Rim Energy (PRE) to be installed in the Thermo Plant of Generation of Electric Energy “ Josefa Camejo” belonging to CADAFE.

The Josefa Camejo Plant is located in the Avenida Intercomunal Ali Primera, Round about “El Taparo- Via Judibana, Punto Fijo, municipio Los Taques, Estado falcon, to the northeast of the country, in the city of Punto Fijo.

- 2.	DEFINITIONS

To the effects of this document, the following definitions will be considered:

THE JOB: It refers to the partial supply, construction, installation, testing and start up, up to the NORMAL OPERATION, corresponding to the electromechanical tasks associated to the first Turbo generating Unit in the Project Plant Josefa Camejo, belonging to CADAFE.

- THE CLIENT: It refers to CADAFE or their legal Representative.

THE COMPANY: It refers to the Pacific Rim Energy (PRE) Consortium, company that subcontracts the services for the construction of the job according to the scope of labor that forms part of the Labor Contract and in the itemized details of labor in same contract.

THE CONTRACTOR: It refers to the company that executes the construction of the job over the foundation of Scope of the work in the Contract for the Job and the details of the “partidas” of the Job on the same contract.

THE SUPPLIER: It refers to enterprises, companies, manufacturers, all approved by THE COMPANY, suppliers of services or equipments that participate conjointly with THE CONTRACTOR in the development of the accomplishment of the job.

THE INSPECTOR: It refers to the representative of THE COMPANY to whom all inspection of the labor included in the scope of the job is assigned.

- Page 5

‘

“Labor Contract”: It refers to the document officially written for “THE COMPANY” to be executed by the CONTRACTOR, whereby all of the technical and commercial pursues are described according to both parties.

“Scope of the Work” It refers to the technical part of the labor contract whereby all the jobs to be done by the CONTRACTOR are described.

“Parts of the Execution of the Job”: It refers to the detailed description for each job and itemized with quantities to be executed by THE CONTRACTOR.

- 3.	SCOPE OF WORK

The job consists of the installation, alignment, pre-commissioning and commissioning tests, start up and calibration of one W501F SIEMENS WESTINGHOUSE Turbo generating Unit for dual combustible, which, in the future, will work in a combined cycle. This unit is completely new and it is acquired by Pacific Rim Energy (PRE) directly from the Siemens Westinghouse Power Corporation. THE CONTRACTOR must consider for its offer, that this unit, its systems, components and equipment are complete (No one single system, component or equipment for the correct installation, start up and operation is missing.)

All these works are described in section 5 (“Description of Partidas”), and are supported by drawings and documents attached.

The scope of the Mechanical Montage, in summary, will include all activities involved in the erection and installation of the components of the turbo generating unit, such as:

- Visual verification of conditions of each module at the time of completion.

- Erection and setting up on the concrete foundation of each associated module,

(with the exception of the turbine and the generator)

- Enclosure of modules that allow it (What???) including stairs, platforms and lighting.

- Alignment of main components according to manufacturer specifications.

- Page 6

- Leveling and bolting to base with application of leveling grouting, according to drawings on each respective module.

- Interconnection of all auxiliary systems and accessories associated to each equipment, system or packet.

- Installation of gas pipes, cooling agents, hydraulic fluid, lubricants, ventilation, drainage including gaskets, leakage tests and its bearings.

- Installation of electrical and controlling conduits with supports.

- Cabling and tests on tying and continuity on cables of potency control.

- Installation, cabling, connection, and linking tests on all of the associated instruments.

- Leakage tests in all of the lines and lubricant lines, hydraulic fluids, combustible gas (gas oil) Compressed air, and cooling agents.

- Initial Load of all lubricants, grease, hydraulic fluid, and cooling agents.

- Retouching of superficial paints.

- Functioning tests” Pre-Commissioning and Commissioning”.

- Start Up of the Unit, Calibration, Vibration tests, noise, and performance.

Any job that will be necessary for the mechanical completion or “Pre-Commissioning” of the packets, system and/or equipment, that are neither listed nor  specifically indicated, must be described, included and notified to THE CLIENT, in a Partida titled Additional  Labor, that for that reason is being left opened.

- Page 7

The CONTRACTOR must in a separate way:

a) Indicate the estimated time for the mechanical completion and the “Pre-Commissioning” of the unit with its systems and/or equipment, through a calendar of activities. The time estimated by THE CLIENT for the installation of the Unit will be communicated by the client in due time to THE CONTRACTOR in order to adjust the budget.

b) List global sum for provision of technical personnel and work crews to execute labor involving “Commissioning” under supervision and instructions of THE CLIENT and THE BUILDER (This term is not on page 4).

For the preparation of the offer, THE CONTRACTOR will have available a set of drawings “as built” (which are listed and are attached to this document), where (THE CONTRACTOR)? could locate all the information on dimensions, weights, elevation, relative location of components, electrical and controlling diagrams, lists of materials, cables (wiring)  and instruments, tests to be executed, etc.

- These drawings and attached documents are duly identified and listed.

- 3.1	 Scope and Provisions of PACIFIC RIM ENERGY (PRE)

The detailed scope of PACIFIC RIM ENERGY (PRE) is detailed in the attachment “SCOPE OF SUPPLY AND DIVISION OF RESPONSIBILITIES”.

The scope of supplies include all the modules, systems and equipment plus their respective accessories, that will be installed, complete and in good conditions, including the supply of new gaskets, screws and nuts  for the fixation and assembling of equipment.

The scope also includes the supply of all instruments that will be installed inside the turbo generating unit as well as the supply of wires, conduits and tubing with their respective accessories for a correct installation and connectivity of the instruments.

All the modules corresponding to the turbo generating unit will be transported to the site and erected over its basis of concrete by the Transporting Company designated by PACIFIC RIM ENERGY (PRE) under its supervision and responsibility.

- Page 8

It will also be the responsibility of PACIFIC RIM ENERGY (PRE) the provision on time of the anchor bolts that will be embedded in the concrete foundations, in quantities and specifications according to the manufacturer of the Generating Unit, with the exception of the “Hilti” type, when these are required.

The drawings “As built” of all the packets, systems and equipment for the installation and assembly of the equipment.

Installation Manuals, Operation and Maintenance (IOM) of all the packets, systems and equipment.

- Materials for thermo insulation and personal protection, according to application.

Metallic structures, platforms, handrails and stairs, grating, plates for skirting boards  ? with accessories, indicated in this document.

All of the pieces of the unions in the modules, sections of the smokestack?, structures of support for air cooling.

The wedges (for leveling off) correct leveling of the equipment over their foundations.

All the products and fluids necessary for the first run such as lubricant oils, hydraulic fluids, grease, cooling agents, hydrogen, and any other product obtainable product through the Siemens Westinghouse.

- Detailed drawings for the fabrication of supports for all the aerial pipes.

  - PROVISSIONS BY THE CONTRACTOR

The necessary equipment for erecting, installing, securing, leveling tests and start up of accessories associated with main modules of the project, such as cranes, porticos, slings, structures, tools, welding machines, elevators (for lifting materials), air compressors , lighting equipment,  cleaning, calibration instruments, etc., in conditions and adequate quantities, that allow the accomplishment of the work to a complete

- Page9

Satisfaction of THE CLIENT and in the time agreed. All these equipment must be in good conditions, well maintained, with their respective certificates and adequately protected against adverse environmental conditions of the place, in such a way as to allow a secure development of the job.

Consumable Materials, such as: Oxygen tanks, acetylene, argon, wires, furnishing material, electrodes, shining discs, sandpaper, lubricants, x-rays, if applicable, testing equipment, fuel for machinery and vehicles in general, all consumable materials required for the correct execution of the jobs and montage of the equipment.

Paint to retouch equipment and its application, when required, including all the materials, paints and solvents. It comprises the retouching of paint on that equipment that had suffered some damage while being transported within THE PLANT or during their installation.

The required materials for installing equipment, such as leveling irons, elements of installation (frames), sealers of joints between equipment and base, as necessary, for the lubrication of pegs and bolts.

All instruments and equipment for calibration (Measurement) to be used during the installation, which must be accompanied by their up to date certificates of quality and calibration.

Scaffolds and associated materials, that would be inspected and approved, before being used on the job.

Generation of Electricity or any other form of energy (pneumatic, vapor, etc.) for all tools and equipment to be used by THE CONTRACTOR in the activities of the project.

All the material and equipment for non destructive testing that  is required, such as films, warning signals, penetrant inks, developers, etc. if required.

Leveling “Grouting”, cementing and commercial “epoxy”, if applicable.

- Page 10

- ADDITIONAL CONSIDERATIONS:

It is essential that before starting the task of installing the equipment, all “As built” documents available for each packet, system and equipment must be at hand and had been consulted. It is fundamental to know and to follow each and every one of the particular manufacturer directions per equipment contained in the respective instructions for installation, Operation and Maintenance (IOM), in each case.

The Verification that bases as well as the motors (individually), are connected to earth, and the verification of the rotating direction of the motors.

The Supply and the fabrication of the temporary coil indicated in the Diagram of Pipes and Instrumentation  VEN326-XG02-MB-011200 Rev.3 Page 40/40 is not the responsibility of THE CONTRACTOR, this will be provided by THE CLIENT, however, the installation and dismantling of it will form part of the activities in which THE CONTRATOR will assist with  during the start up  of the Turbo generating Unit Number 1. Likewise, THE CONTRACTOR will install the permanent coil as indicated in the Pipe and Instrumentation diagram VEN326-XG02-MB-011200 Rev. 3 Page 40/40.

Installation and Montage of the packets, systems or equipment, in their respective bases, verification of location, elevation, and orientation of the bases, boquillas? holders, anchor bolts and pipes of the system to which the equipment belongs to, before installing the equipment and to inform of any discrepancy found on the drawings and/or documents to THE CLIENT.

Protection of parts and/or delicate pieces (such as, graseras, instruments, etc. once the equipment is installed.

Coordination with other CONTRACTORS working at the site.

External cleaning, once the equipment are mounted.

Internal cleaning, in cases that are necessary, either with solvent, or pressure washing with nitrogen or with gas.

The prompt notification to THE CLIENT to repair and/or substitute elements, parts, or equipment that get damaged during transportation form the ware houses and /or during installation and assembly of the package.

- Page 11- .

Adjustment and filling up with lubricants, when applicable, re-greasing of ball bearings of motors.

The connection of electrical cables, instruments and controls, and the connection of pipe lines and/or piping from the limits of each packet, system and or equipment described in one of the parts (partidas) to the respective cables and service such as compressed air, drainage, oil, water, etc. are activities that will be executed by other CONTRACTORS.

- 5.	DESCRIPTION OF THE PACKETS. (PARTIDAS)

  - Partida (Item) No 1 M01-01 Installation of the Turbine

Assuming that the turbine is already placed on its base, this partida (Item) consists of:

Cleaning, leveling, alignment with wedges? for calibration, fixation to the base and correct fastening of the respective anchor bolts, application of the “grouting” in parts it is required, alignment and adjustment of the turbine and the generator.

Installation and connectivity of all instruments that will be placed directly inside the turbine carcass.

The installation of pipes and/or pipe line whose connection goes from and to the carcass of the turbine. The installation of the module of piping inside the house of the turbine.

Connection of the Turbine to all lines (tubes and/or tubing) of services required.

External Cleaning of the turbine to remove with solvent or pressure water cleaning all dirt, grease, or material that might be inflammable.

The installation of the tail cone of and the tewel for discharge of hot gases towards the chimney, including the expansion joint and its external cover.

The installation of insulation jackets over the body of the Turbine, once completed the tasks of connections to services above mentioned by THE CONTRACTOR and all the activities such as the installation and connection of instruments that ARE NOT going to be connected directly

- Page 12

in the carcass of the Turbine, the connection of electrical cables, of instruments and controls, as well as the connection to earth in all those indicated points in the drawings of the project.

  - Partida No M01-02 Installation of Turbine Enclosure

This step comprises of transporting the acoustic enclosure of the Turbine, from the warehouse of THE PLANT to the place of installation, its assembly and correct fixation to its base. This enclosure consists of pre-assembled panels, the insulating material is found installed inside between the internal and external plates of each panel, therefore the installation will consist of basically activities of erection, assembly of columns and panels, the fixation with anchor bolts and nuts between the panels and the beamed structures for support, the welding of seals between the panels and the supply of  and application of filling up with “fiberglass” in the joints between the panels and the enclosing columns.

Also it is included in this partida the placement of doors for access, their stairs, with platforms and handrails, grillage flooring (“grating”), including paint, installation of internal lighting and the system of detection and extinguish fire with a clean agent.

  - Partida No. M01-03 Installation of the system for Injection and Extraction of Air for Ventilation in the enclosure of the Turbine.

This partida consists on the transportation of the components of the system of injection and extraction of air for the enclosure of the Turbine, from THE PLANT’s warehouse to its place of installation, assembly and correct fixation over the roof of the turbine enclosure. The enclosure consists of panels, acoustic structures, air injection fans and motorized doors; the insulation material is installed between the internal and external plates that form each panel.

The control for the fans and the electrical connections are included, as well as the required earth connections according to the drawings of the project.

- Page 13

5.4.	Partida No M01-04 Installation of Cooling Air System for the axis of the Turbine.

This Partida consists of the transport and installation of the components of the system of injection of air for cooling of the axis of the Turbine, from THE PLANT’s warehouse to the place of its installation, its assembly and correct fixation to the carcass of the turbine. This system consists of an air cooler of two bays and two motor-ventilators and a set of thermal insulated piping which conform the cooling ties of the combustion steps of the turbine.

The Air Cooler will be placed over an elevated structure to be supplied by PACIFIC RIM ENERGY (PRE) but installed and assembled by THE CONTRACTOR.

- The electrical connections and motor controls are included.

  - Partida No M01-05 Installation of the spiral of entry of air to the turbine.

This Partida consists on the transportation of the shells with their joints which make up the “spiral of entry of air to the turbine” from THE PLANT’s warehouse to the place of its installation, assembly and correct fixation in the aspiration section of the turbine.

This system consists of a set of metallic shells that when they are joined at the flexible rubber point, they form the final adjustment between the duct for external air, the section of aspiration and the cabinet of enclosure of the Turbine.

  - Partida No M02-01 Installation of the Generator

It is the same, as in the case of the Turbine, the generator will be transported and placed over the base by others, under the supervision and responsibilities of PACIFIC RIM ENERGY (PRE).

- Page 14

Assuming that the Electrical Generator is already placed on its base, this partida consists of:

Fixation to the base and correct fastening of respective anchor bolts.

- Leveling, application of “grouting” in the required parts.

Assembly of accessories such as elevated  metallic floors with stair cases, hand rails, grillage flooring (“grating”), including paint, panels electrical cables, and controls, adjustment of ducts of electrical bar, as well as the connection to earth in all the points indicated in the corresponding drawings.

- Alignment and adjustment of the Generator with the starter Motor and with the Turbine.

The external cleaning of the Generator and the removal of dirt, which will be done with solvent or with pressure washer eliminating all dirt, grease, or material that might be inflammable.

  - Partida No M02-02 Installation of Enclosure of the Generator

This partida consists on transporting the acoustic enclosure of the Generator, from THE PLANT’s warehouse to the place of its installation, its assembly and correct fixation to its base.

This enclosure consists of panels already pre-assembled, the insulating material is installed between the external and internal plates of each panel, therefore the installation will consist of basically the activities of erecting the structure, assembly of columns and panels, fixation with anchor bolts and nuts between the panels and the beamed structures for support, the welding of seals between panels and the supply and application of  filling up with “fiberglass”  of joints between the panels and columns of enclosure.

In this partida it is also included the placement of doors for access, their stairways with platforms and handrails, grillage flooring (“grating”), including paint, installation of internal lighting and the system of detection and extinguish fire with a clean agent.

- Page 15

5.8		Partida No M02-03 Installation of the system of Injection and Extraction of Air for the Ventilation of the Enclosure of the Generator.

This partida consists of transporting the components of the system of injection and Extraction of Air of the Enclosure of the Generator, from THE PLANT’s warehouse to the site of its installation, assembly and correct fixation to the enclosure of the generator.

- The insulating material is installed between the internal and external plates that form each panel.

This enclosure consists of panels, acoustic structures, air injection fans and motorized doors, therefore the installation will consist basically of activities of erection, assembly and fixation with anchor bolts and nuts of the describe components.

The electrical connections and control of the fans are included, as well as the connection earth in all the points indicated in the respective drawings.

5.9		Partida No M02-01 Installation of the Start Up packet

The start up packet consists of a structural contact shoe, covered with a metallic enclosure. This metallic enclosure contains the electric Motor of start up of the Turbine and its accessories, such as the des-connector of the Generator, elevated metallic floors, control panels, internal lighting and all other elements for the connection and electrical feed and controls.

This partida consists of transporting the start up packet of the Turbine from THE PLANT’s warehouse to its site of installation, erecting it and appropriately placing it on the concrete foundation.

The supply and the preparation of slings and beams to distribute the loads are included.

Once the start up packet is in place, this partida will include:

- Page 16

Cleaning, leveling, fixation to its base and correct fastening of the respective anchor bolts, application of “grouting in the areas that it requires.

Placement of staircase and platforms with handrails and grating, the connection of switchboard, electrical wiring, instruments and control panels, system of detection and extinguish fire, internal lighting, module of injection and extraction of fresh air, as well as the connection to earth in all the points indicated in the corresponding drawings.

The external and internal cleaning of the start up packet will be for removing with a solvent or with pressure water all dirt, grease, or material that might be inflammable.

- The insulating material is found installed between the internal and external plates of each panel.

5.10	 Partida No M)$-1 Installation of the Filtering House.

This Partida consists of transporting the Filtering House of The Turbine from THE PLANT’s warehouse to its site of installation, erecting it and appropriately placing it on the concrete foundation.

This Filtering House consists of a metallic structure of three levels, with enclosing panels, supporting frames for the filters, rain protecting screens, filtering panels, stairs, platforms, access doors, internal lighting and a system of calibration and measurement of differential pression.

This Partida contains:

Transportation from the warehouse, cleaning, leveling, assembly of the metallic structure that makes up the Filtering House, posterior placement and anchor bolting of the acoustic external paneling (lateral, floors, roof), the welding of the seals between the panels and the rain protecting screens with a screen against insects, supports for the filters, installation of the disposable filters, leveling and application of “grouting” in the parts that are required.

- Page 17

The external and internal cleaning of the Filtering House to remove with solvent or with pressure washer all dirt, grease, or material that could be introduced in the Turbine.

Also included is the placement of marine stairs, the doors to access all levels, platforms with handrails and “grating”.

The acoustic material is found installed between the internal and external plates that make up each panel.

  - Partida No M05-1 Installation of the Air Entry Duct of the Turbine with a silencer.

This Partida consists of transporting for the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete the Air Feeding Duct of the Turbine.  This duct consists of a metallic structure, with metallic panels of enclosure, which starts with the adjustments in the house of Filters and ends with the adjustments in the Entry Coil of the Turbine.

This Partida consists of:

Cleaning, leveling, and assembly of the metallic structure and anchor bolting of external acoustic panels ( lateral, floors, roof) that conform the air duct, with the application of “grouting” in the areas that it requires, as well as the connection to earth in all the places indicated in the corresponding drawings.

The external and internal cleaning of the Filtering House to remove with solvent or with pressure washer all dirt, grease, or material that could be introduced in the Turbine.

The installation of the acoustic material placed between the internal and external plates that make up each panel of the air ducts.

- Page 18

  - Partida M06-01 Installation of the  Mechanical Packet (“LubeOil”)

This Partida consists of transporting for the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete the Mechanical Packet and its electric interconnection, controls and piping with all the other attached packets. This Partida will include the preparation and supply of slings and beams of distribution of load (in the case of lifting with cranes) or sliding pontoons and hydraulic jacks(in case of positioning through a horizontal haulage or drag).

This Mechanical Packet consists of a structural contact shoe, covered with a metallic enclosure (already installed) which in turn contains the acoustic material between the internal and external plates that make up each panel. Internally this packet is conformed by pumps for the system of lubricating oil with its tank and oil filters, a packet of compressed air, a metallic floor, potency control panel  and controls, pipe line and elements of connection of potency control, internal and external and system to detect and extinguish fire.

All the components before described are already installed, cabled and connected with each other with their respective pipe line.

Once the Mechanical Packet is over its respective base, this Partida consists of:

Cleaning, leveling, and assembly fixation to its base and correct fastening of all respective anchor bolts of the packet, leveling, application of “grouting” in each area that it is required, as well as the connection to earth in all the places indicated in the corresponding drawings.

The external and internal cleaning of the packet will be to remove with a solvent or with pressure water all dirt, grease, oils or material that might be inflammable.

  - Partida M06-02 Installation of External Equipment of the Mechanical Packet (“Lube Oil”)

The accessories of the Mechanical in this Partida include:

- Page 19

One (1) “Air Cooler” of fluttered tubing, for the oil of the Turbine of two bays and two fans.

One (1) vapor separator filter/oil of the Turbine, conformed by filtering tank, two centrifugal fans and an extraction piping.

One (1) additional tank of compressed air, that is an air receiver complimenting that one found inside the mechanical packet.

- A set of perimetrical handrails to the mechanical packet.

All the components described above and the metallic structure (handrails) will be placed over the roof of the mechanical packet.

This Partida consists of transporting, from THE PLANT’s warehouse to the place of its installation, erection, assembly and correct placement over the elevated metallic structure, of the External Equipment of The Mechanical Packet, including the preparation and supply of slings and beams of distribution of the load for lifting with crane.

The cleaning, leveling, fixation to the structure and correct fastening of the respective anchor bolts.

Wiring Connection for electrical feed, instruments and controls, oil piping, vents, drainage, returns, stairs, elevated platforms with handrails and lighting, as the connection to earth in all the points indicated in the corresponding drawings.

The external and internal cleaning of the accessories will be to remove with solvent, with pressure water all dirt, or internal sweeping of all dirt, grease, oils or undesired materials.

  - Partida M07-01 Installation of Electrical Packet

This Partida consists in transporting from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete the Electrical Packet and its accessories, as well as the supply and preparation of slings and beams for the distribution of the load for lifting with crane.

- Page 20

The Electrical Packet consists of a structural contact shoe, covered with a metallic enclosure (already installed) which in turn contains the acoustic material between the internal and external plates that make up each panel. Internally it contains switchboard and control panels to control the Turbine, a room with auxiliary batteries, the air condition units that refrigerate all the electric components and switchboard and cabinets for the electric interconnections with other modules. All the components before described, with the exception of the air condition units and the batteries, are already installed over the contact shoe inside the enclosure.

Once the Electrical Packet is over its respective base, this Partida consists of:

The installation of all loose accessories of this Packet, two units of air condition of a compacted type over their aerial metallic bases, the bank of batteries inside the hut and its electric wiring and controls.

Cleaning, leveling, and assembly fixation to its base and correct fastening of all respective anchor bolts of the packet, leveling, application of “grouting” in each area that it is required.

Installation, connections and identification of electric wires, instruments and controls towards the other modules, continuity tests, megawatt and link tests, as well  as the connection to earth in all the places indicated in the corresponding drawings.

The external and internal cleaning of the packet will be to remove with solvent or with pressure water all dirt, grease, or oils.

5.15	 Partida No. M08-01 Installation of Contact shoe for Washing Water Injection

This Partida consists of transporting for the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete of the Contact Shoe for De-mineralized Water Injection for cleaning the Turbine, as well as the supply and preparation of slings and beams for erection with crane.

This equipment consists of an uncovered structural contact shoe which supports a pump for the pressured injection of de-mineralized water, a tank of

- Page 21

storage of liquid detergent, piping, valves and its connection box to electrical services.

Once the contact shoe is placed over its respective foundation or base, this Partida comprises:

Cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts of the packet, application of “grouting” in parts in which it is required, alignment of the pump with its accionador (switch???) and its posterior adjustment.

- Connections with pressure water discharge towards the Turbine.

The external and internal cleaning of the packet will be to remove with solvent or with pressure water all dirt, grease, or oils.

Connections and identification of electric wires, instruments and controls with final operational test, as well as the connection to earth in all the places indicated in the corresponding drawings.

5.16	Partida No. M09-01 Installation of Chimney of the Turbine

This Partida consists transporting from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete of the Discharging Chimney of the turbine and the supply of slings and beams for distribution of the load for lifting with crane.

The sections of the Chimney must be pre-assembled and placed in the corresponding order and welded (or anchor bolted) according to manufacturer specs.

Once placed over its respective foundation or base, this Partida will include:

The cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts welding of the unions, application  of “grouting” in the area that is required, as well  as the connection to earth in all the places indicated in the corresponding drawings.

- Page 22

Adjustment in the section of entry to the discharging channel of the Turbine or duct of transition of the Turbine.

Installation of internal parts of the Chimney  like the deflecting wings and the vertical acoustic  panels and thermo panels.

The placement of external marine stairs, the platforms with handrails, and grilled floor or “grating”.

Installation, wiring,  and testing of “Environmental Emission Sensors”   CEMS.

External cleaning of the Chimney to remove with solvent or with pressure water all dirt, grease, or material that might be flammable.

The acoustic material is placed between the internal and external sheets that make up the enclosure and acoustic panels of the Chimney, needing only minor arrangements that could apply to damages arisen during transportation.

  - Partida No M10-01 Installation of The FM-200 Packet

These packets are made of a connector shoe that contains FM-200 Bombonas, carboys???, the control panels with wires to the detectors zone, transfer tubing of gas extinguisher, accessories for piping, steam of pipe, fire extinguishers and flooding and blocking valves.

This Partida consists in the transportation of  the Packet, from the warehouse in THE PLANT to its place of installation, erection, leveling, fixation to its base or foundation of concrete and correct fastening of the respective anchor bolts, application of “grouting” in the parts that it requires.

Connection of all extinguishing piping system to all different modules to protect, wiring and connection with flame sensors placed in the different modules and anti-fire switchboards, operational tests, drills, leakages and initial load of FM-200.

- Page 23

Connections of electric wiring, instruments and controls with final operational tests, as well as the connection to earth in all the places indicated in the corresponding drawings.

External cleaning of the set with solvent or pressure water eliminating all dirt, grease, or material that might be flammable.

  - Partida No M11-01 Installation of Accessories of the Control Emissions System

The Accessories of the Control Emissions System to be installed consist of a packet of Gas Filters, a packet of Fuel Oil Injection< a packet of Water Injection and a packet of FO/WI.

The Packet of Gas Filters consists of a vertical filter, a group of pipes and closing and control valves, totally assembled over a structural connector shoe with its respective erecting ears.

The Fuel Oil Injection packet consists of two recipients equipped with filter, a pump to inject fuel oil, a switchboard, closing and control valves, totally assembled over a structural connector shoe with its respective erecting ears.

The Water  Injection packet consists of a tank equipped with a filter, a pump for de-mineralized water injection, switchboard, closing and control valves, totally assembled over a structural connector shoe with its respective erecting ears.

The FO/WI consists of switchboard, accumulators, divisors of fluid, and closing and control valves, totally assembled over a structural connector shoe with its respective erecting ears.

This Partida consists on transporting The Accessories of the Control Emissions System, from the warehouse in THE PLANT to its place of installation, erection, preparation and supply of slings for lifting with crane.

- Page 24

Leveling, fixation to its base and correct fastening of all respective anchor bolts welding of the unions, application of “grouting” in the area that is required, external cleaning of the filters, tubing and valves that makes it up.

External cleaning of the Set will be done with solvent or with pressure water eliminating all dirt, grease, or material that might be flammable.

  - Partida No M12-01 Installation of “Surge Cubicle”

This Partida consists in the transportation the Protection against Lighting Packet from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete and its accessories as well as the supply and preparation of the slings and beams for distribution of the load for lifting with crane.

This Packet consists of a covered structural contact shoe with a metallic enclosure (already installed) which also contains the acoustic material between the external and internal sheets that make up each panel. It contains internally electrical elements and switchboards or cabinets for the electrical interconnections with other modules. All components already described, are already installed over the connector shoe inside the enclosure.

Once the “SURGE CUBICLE” is over its respective foundation or base, this Partida includes the installation of the loose accessories and its electric and control wiring.

The cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts welding of the unions, application  of “grouting” in the area that is required.

Connection and identification of electric wires, instruments and controls towards the other modules, continuity tests, megado (megawatt???)  and link tests, as well  as the connection to earth in all the places indicated in the corresponding drawings.

External cleaning of the packet will be doneto remove with solvent or with pressure water all dirt, grease, or oils.

- Page 25

  - Partida No M13-01 Installation of “Bearing Lift Oil Skid”

This Partida consists of transporting from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete connector shoe of oil pressurization of the bearings of the Turbine, its electrical interconnections, controls and piping of all other packets attached. This Partida will include the preparation and supply of slings and beams of distribution of loads (in case of erection by crane) or sliding pontoons and hydraulic jacks (in the case of positioning through horizontal haulage).

This Mechanical Packet consists of a structural connector shoe, covered with a metallic enclosure already installed) which also houses the acoustic material, that is found between the internal and external sheets that make up each panel. Internally this packet is formed with pumps for the system of lubricating oil with its tank and oil filters, metallic floors, control panel for potency and controls piping system and elements of potency connection and control.

All the elements described above are already installed, wired and connected to each other with their respective piping.

The cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts of the packet, leveling, application  of “grouting” in the parts that are needed.

Electrical interconnection of control and piping with other packets, filling up with lubricant, operational tests, links, start up, and calibration as well as the connection to earth in all the places indicated in the corresponding drawings.

The internal and External cleaning of the packet will remove with solvent or with pressure water all dirt, grease, oils or materials that might be inflammable.

5.21	 Partida No M14-01 Installation of the Connector Shoe of the Compressed Gas

Page 26

This Partida consists transporting from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete of the Connector Shoe of the Compressed Gas for the operation of components and pneumatic valves of the Turbine, as well as the preparation and supply of slings for lifting with crane.

This Partida consists of an uncovered structural contact shoe which supports an air compressor, a tanque pulmon, breathing tank???, air dryers, tubing, valves, a control and potency box of connections and utility service.

Once the connector shoe is over its respective foundation or base, this Partida includes:

The cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts welding of the unions, application  of “grouting” in the area that is required, alignment of the connector shoe, connection with piping system of pressurized air discharge towards the Turbine.

The external cleaning of the packet will be to remove with solvent or with pressure water all dirt, grease, or oils.

Connection of electrical wiring, instruments and controls, with final operational tests as well as the connection to earth in all the places indicated in the corresponding drawings.

5.22		Partida No M15-01 Installation of the Packet “Control Oil Skid”

This Partida consists transporting from the warehouse in THE PLANT to its place of installation, erection, assembly and appropriate placement over its base or foundation of concrete the Connector Shoe of the Oil control for the Turbine, its electrical interconnection, of control and piping tie in with other attached packets. This Partida will include the preparation and supply of slings and beams of distribution of loads (in case of erection by crane) or sliding pontoons and hydraulic jacks (in the case of positioning through horizontal haulage).

This Packet consists of a structural connector shoe, covered with a metallic enclosure already installed) which also houses the acoustic material, that

Page 27

is installed between the internal and external sheets that make up each panel. Internally this packet is formed with two pumps for the system of lubricating oil with its tank, a heat exchanger with fluttered tubing and oil filters, a metallic floor, Potency switchboards and controls, piping and elements of connectivity, potency and control.

All the elements described are already installed, wired, and connected to one another with their respective piping system.

Once the packet is over its respective foundation or base, this partida consists of:

Cleaning, leveling, fixation to its base and correct fastening of all respective anchor bolts welding of the unions, application  of “grouting” in the area that is required.

Controlling electrical interconnection, and piping with other packets, loading of lubricants, operational tests, links, start up and calibration, as well as the connection to earth in all the places indicated in the corresponding drawings.

The internal and external cleaning of the packet will be done to remove with solvent or with pressure water all dirt, grease, oils or materials that might be inflammable.

  - Partida No M16-01 Work in the basement of the Electric packet

Electrical Works Associated

PACKET OF ELECTRICAL INSTALLATION OF THE WIRE (CABLE) HOLDER IN THE BASEMENT

This partida consists of the installation of trays of aluminum wires, with or without lids, level change, turns, reductions or derivations, fixation supports, anchor bolts, joins, expansion joints, bridges with insulated earth wirings (green) between trays, and labor necessary to complete the installation of the trays with wires in horizontal or vertical sections, according to technical specifications and

Page 28

corresponding drawings. The required supports are included, the cleaning of the place of work and the identification of the trays with paint.

THE CONTRACTOR must utilize bi-metallic connectors for earthing the trays, as well as placing an inhibiting oxidizing compound (Penetrox), in all those points in which par galvanic might occur. The bi-metallic connector as well as the inhibitor will be supplied by THE COMPANY

Page 29

  - Partida No. M17-01 Gas Line Provisional Coil

This Partida consist of fabricating, transporting to site and provisionally installing without posterior removal a provisional coil of piping in the natural gas feeding line to the turbine, according to the Diagram of Instrumentation and Piping VEN326-XG02-MB-011200 Rev. 3 Page 40/40.

This coil would be installed only in the required tests and its dimensions must coincide with those of the defined spool which is shown in the following drawing.

# pages		Description				Document 		 Revision

Number

01/02		FUEL GAS ORIFICE METERING SYSTEM		2335J14		04

This Partida includes the supply of materials for the coil according to respective piping class, fabrication of the coil, hydrostatic tests and X Rays wherever they apply, Transport to the site, installation over supports and anchor bolting with gaskets.

  - Partida No M18-01 Permanent Gas Line Coil

This Partida consists of the removal of the provisional  coil described in the partida M18-01, and installation of permanent calibration spool in the piping line of natural gas feed to the turbine, according to the Diagram of Instrumentation and Piping VEN326-XG02-MB-011200 Rev. 3 Page 40/40 and in the following table.

# pages		Description				Document 		 Revision

Number

01/02		FUEL GAS ORIFICE METERING SYSTEM		2335J14		04

Page 30

This Partida consists of the removal of the provisional coil line and handing down to THE CLIENT in his warehouse transport and permanent installation of the calibrating spool

according to the Diagram of Instrumentation and Piping VEN326-XG02-MB-011200 Rev. 3 Page 40/40 its correct anchor bolting and hydrostatic testing.

  - Partida No M19-01 Additional work

This Partida is left open for THE CONTRACTOR to include any additional  work that he considers necessary for the mechanical completion or the “Pre-Commissioning “ or the packets, systems and/or equipment that are no listed or specifically indicated, like paint retouch, minor repairs for damages caused by transport of  third parties, minor repair of insulation, testing assistance, etc. All work included in this Partida must be duly described and  appraised with cost per crew hours and machinery.

  - Partida No. E05-TTABB01 Installation of Elevating Transformer n16.5-115KV

This Partida includes but is not limited to, to the use of equipment and tools, supply of materials, supervision and labor to install, (place align, level, and fix) a transformer, in each one of the places in which it Is indicated in the drawings of the project, according to the details of installation developed for such goal and the documents provided by the manufacturer. The work includes the montage of the equipment over the designated foundation for it.

The transformers of Potency will be provided without oil, therefore, once installed THE CONTRACTOR must execute treatment, filtering, filling up, measurement of dialectic resistance of oil. If the results are inferior to the minimal values prescribed by standards, THE CONTRACTOR must proceed to dry up and new oil treatment. The required equipment consists of barrel, tank that conserves oil, radiators, low pressure insulators, high voltage insulators, control panel, all the

Page 31

elements that constitute part of the transformer indicated in the drawings of the manufacturer must be correctly assembled leveled and tested.

The Partida includes: Connection of electrical wires and of control, with final operational tests, as well s the connection to earth in all points indicated in the corresponding drawings.

  - Partida No.E05-TTABB02 Installation of Transformer of Auxiliary Services 16.5 – 4.16 KV

This Partida includes but it is not limited to, the use of equipment tools, supply of materials, supervision and labor to install, ( place, align and fix)a transformer, in each one of the places in which it is indicated in the drawings of the Project, according to the details of installation developed for such job and the documents supplied by the manufacturer. The job includes the mounting of the equipment over the foundation destined for it.

The transformers of Potency will be supplied filled with oil, therefore, once installed THE CONTRACTOR must take the measurement of the dielectric resistance of oil. If the results are inferior to the minimal values prescribed by standards, THE CONTRACTOR must proceed to dry up and oil treatment. The required equipment for the oil treatment must be supplied by THE CONTRACTOR

This equipment consists of barrel, tank that conserves oil, radiators, low voltage insulators, high voltage insulators, control panel, all the elements that constitute part of the transformer indicated in the drawings of the manufacturer must be correctly assembled leveled and tested.

The Partida includes: Connection of electrical wires and of control, with final operational tests, as well s the connection to earth in all points indicated in the corresponding drawings.

  - Partida No.E05-KTABA01 Installation Fixation of Insulating Bar for the Generator en  16.5 KV

This Partida includes but it is not limited to, the use of equipment tools, supply of materials, supervision and labor to install, (place, align and fix) terns of insulating bar ( phase R,S and T), in its supporting structure

Page 32

Or wherever it applies, in each place where it is required, according to what is indicated in the drawings ogf the Project and in the Details of the installation developed for such task. The job includes vertical and horizontal sections, as well as straight and curved sections, connections with all equipment where the bars require connecting, as well as the parts of expansion, gliding, and the connection to earth according to the detailed drawings of the Project.

In this partida it is included: The removal, loading, and transportation of the materials and equipment supplied by THE COMPANY, from the warehouse to the place where they will be unloaded and installed, It is included the support in case it will be needed for the montage.

This Partida also includes the installation of the metallic structures of support for the duct of insulating bars, including the repairing of the electroplating of the connections.

  - Partida No E05-FTABA01 Installation of the Main Switch for the Generator in 16.5 KV

This group of Partidas includes but it is not limited to, the use of equipment tools, supply of materials, supervision and labor to install, ( place, align and fix)a potent main switch, where it applies, in each one of the places indicated in the drawings of the Project, and the details of the installation developed for such task. Electric tests are included, concoction to earth, corresponding supports. The equipment must be stored, transported, installed and placed according to indications supplied in the manufacturer instructions.

In these partidas it is included: The removal, loading, and transportation of the materials and equipment supplied by THE COMPANY, from the warehouse to the place where they will be unloaded and installed, It is included the support in case it will be needed for the montage.

This Partida also includes the installation of the metallic structures of support for the duct of insulating bars, including the repairing of the electroplating of the connections; the installation of platforms, handrails, (“grating”), including repair of  electroplating of the connections.