NOMINAL 340MW

TECHNICAL INFORMATION GE FRAME 7EA

SIMPLE CYCLE POWER PLANT

FOR

Petroleos de Venezuela

340 MW POWER PLANTS

Budgetary Proposal

Introduction:

Our Company proposes to supply a group of gas turbine-based simple cycle power plant equipment nominally rated at 340 MW that contains four (4) GE Frame 7EA (“7EA”) gas turbines never used .

Scope of Supply

Schedule 1

GE Scope of Supply

1 	Gas Turbine Systems

2 	Generator

3 	Gas Turbine-Generator Controls and Electric Auxiliaries

4	Services     …………………………………………………………………………………………………………….

1 Gas Turbine Systems

  - Gas Turbine

Base-mounted gas turbine including:

• Modulating IGV (inlet guide vanes)

  - Combustion System

- Single-nozzle combustion system

- Combustion system features

- Nimonic transition pieces

- Extendor hardware

- Reuter Stokes SiC flame detectors

- Water injection for NOx control

- Liquid fuel

- Off base water injection skid with:

- Enclosure

- Space heater

- Water injection pump with variable frequency drive

- Dual full size water injection pumps with variable frequency drive

- Water filter

- Dual full flow water filters

- Stainless steel water injection piping (GT unit)

  - Fuel Systems

    - Liquid Fuel System

- Dual liquid fuel

- Crude and distillate

- Stainless steel fuel oil piping

- Duplex HP fuel strainers off-base,

- Main liquid fuel filter differential pressure transducer, 96LF

- Shaft driven atomizing air compressor

- Shaft driven main liquid fuel pump

- Main liquid fuel pump inlet pressure transducer, 96LP

- Crude oil electric heater skid (lOOF temperature rise)

- Dual liquid fuel selection/filtration skid

- Duplex basket strainers with differential pressure switches

- Pressure regulator valves with downstream pressure switches

- Fuel flowmeters

- With pulse generators for remote indication of fuel flow

- Fuel selection valve

- Self-cleaning motorized strainer with differential pressure switch and isolation valves

- A second motorized strainer for redundant strainer capability

- Duplex filter with differential pressure switch

- Thermal relief valves

- Fuel additive injection system, includes calibration tube, dosing pumps and control

- Oil based vanadium inhibitor

- Fuel additive storage tank on the fuel selection skid

- Carbon steel fuel oil piping upstream of the duplex filter, stainless steel fuel oil piping downstream, including the injection system

- Structural steel base

- Fuel selection skid weatherproof enclosure

  - Lubricating and Hydraulic Systems

1.4.1	 Pumps

- Shaft driven main lube oil pump

- Shaft driven main hydraulic pump

- AC motor driven, auxiliary lube oil and hydraulic pumps

- DC motor driven, emergency lube oil pump

1.4.2 	Filters and Coolers

- Dual lube oil system filters

- Dual hydraulic oil filters

- Dual lube oil coolers

- With 90-10 copper-nickel U-tubes

• ASME code stamp

- Lube oil coolers

- Lube oil filters

1.4.3 	Lube Oil Piping

- 304L stainless steel lube oil feed pipe

- Carbon steel lube oil drain pipe

- Lube system valve stainless steel trim

- Schedule 10 lube oil piping inside lube oil tank

- Automatic GMAW or GTAW root pass weld, lube oil feed and drain piping.

1.4.4 	Mist Elimination

- Lube vent demister

1.4.5 	Oil Reservoir

- With heater for -20°F (-29°C) ambient temperature

1.4.6 	Instrumentation

- Delta pressure switches for alarm for lubrication and hydraulic oil filters

- Lubrication oil header pressure transmitter

- Lubrication oil tank level transmitter

- Lubrication oil filter differential pressure transmitter

- Hydraulic oil differential pressure transmitter

- Hydraulic oil supply pressure transmitter

1.5 	Inlet System

- Inlet system arrangement

- Up and forward inlet system arrangement

- Inlet compartment

- Self-cleaning inlet filter

- Horizontal Filter Elements

- Compressor bleed air supply for filter cleaning

- Severe duty filter media (high humidity/corrosive environments)

- 50 micron moisture separator

- Coalescing filters

- Inlet compartment local differential pressure indicator (gage) across each stage of filtration and   overall filter compartment system

- Inlet compartment differential pressure alarm

- Three thermocouples for inlet air temperature measurement

- Inlet filter compartment support steel (Seismic Zone 4, <= 120 mph wind speed loads per USC 1997)

- Caged ladder access to inlet filter compartment Left hand access to inlet filter compartment

- Dust collection kit under each module with auger Electric hoist with 500 Ib lift capacity

- Inlet filter compartment interior lighting

  - Air processing unit (APU) for filter cleaning

- With 304 stainless steel piping and dual filters

-  APU heat tracing kit if required due to site minimum ambient temperature rating

- Inlet ducting

- Inlet duct section arrangement per proposal mechanical outline

- Empty unlined inlet ducting

- Including empty ducting for mounting extraction air fans for turbine compartment        pressurization and blowers to supply filtered air to the exhaust frame area

- Inlet silencing

- Inlet 90 degree elbow Inlet transition piece Inlet expansion joint

- Inlet ducting support steel (Seismic Zone 4, <= 120 mph wind speed loads per use 1997) - - - -(Refer to proposal drawing for scope)

- Outdoor unit

- Compressor inlet humidity sensor

- Triple redundant sensors

- Compressor inlet temperature thermocouple

  - Inlet system atmospheric protection

- Zinc rich paint inside and outside of inlet filter compartment

- Two-part epoxy overcoat inside and outside inlet filter compartment

- Zinc rich paint inside and outside of inlet ducting with two-part epoxy overcoat on all inside surfaces exposed to airflow as well as all outside surfaces

- Galvanized, galvannealed or carbon steel with zinc-rich primer for all interior surfaces not exposed to airflow

- Corrosion-resistant inlet silencing perforated sheet

- Galvanized inlet support steel

1.6 Exhaust System

1.6.1 Arrangement

- Exhaust plenum with right side exit (3 Units base and 1 unit option)

- Exhaust plenum with left side exit (3 Units base and 1 unit option)

- Exhaust expansion joint with wing and cowl

- Exhaust system materials and atmospheric protection

- Carbon steel exhaust system shell and stiffeners

- 409 stainless steel internal lagging

- Inorganic zinc primer

1.7 Couplings

- Oil filled accessory coupling

- Rigid load coupling

- Load coupling guard

1.8 Gas Turbine Packaging

- Lagging and enclosures

  - Turbine and accessory compartment lagging (on-base)

  - Load coupling compartment lagging (on-base)

  - Acoustic barrier wall around turbine and accessory compartments

  - Acoustic barrier wall along exhaust plenum and load compartment. Generator and GNAC

    - External junction boxes

      - Stainless steel junction boxes, rated NEMA 4Xor glanded IP56, dependent on whether wiring is compliant with NEC or IEC standards

      - Cast aluminum may be substituted as needed for flame-proof enclosure requirements, as determined by the hazardous area map for the project

        - Compartment ventilation, pressurization and heating

          - Turbine, accessory, and load compartment pressurization

          - Compartment pressurization air from GT inlet

          - Heated turbine and accessory compartments for humidity control

-   Ducting and support works

            - Plant arrangement

              - Turbine designed for installation outdoors In-line accessory module

              - Mounting pads only; exterior unit walkways are not part of the power train scope of supply

              - Mounting pads only; interior walkways are not part of the power train scope of supply

- Base painting

- Standard primer only

- UBC 1997 Seismic Zone 4 loads

- Hazardous area classification

- NEC Class!. Group D, Division 2

- Turbine compartment

- Accessory compartment

- Special features

- Blank set of nameplates for on-site engraving by others

- Dual (metric-English) indicators and gauges

1.9 Fire Protection System

  - Fire detection system - heat detectors

Turbine compartment

- Accessory compartment

- Load coupling compartment

- Number 3 bearing tunnel

  - Smoke detection system

- Control cab/PEECC Compartment warning signs

- Compartment exterior alarms

- Local C02 mechanical lockout

- Local manual fire protection discharge

- C02 supply system

- One low pressure C02 tank per unit

- Tank suitable for 0-120°F (-18 to 49°C)

- Tank to be located in a shelter (not part of the power train scope of supply), for ambient temperature above 120°F (49°C)

  - Fire protection piping

    - Purchaser's connections on left side of the units (4 Units) and right side of unit (4 Units) . The total of 8 units includes the 2 optional units.

    - Turbine compartment

    - Accessory compartment

    - Load coupling compartment

    - Number 3 bearing tunnel

    - FM-200 fire protection piping for the PEECC

- Hazardous atmosphere sensors in compartments ~ CHx sensors - accessory compartment

- CHx sensors - turbine compartment

- Hazardous atmosphere detector readout

  - CHx

1.10 Cleaning Systems

- On system base piping for on and offline compressor water wash

- On base piping for offline turbine water wash system

- Water wash skid

- Turbine water wash capability

- Water storage tank and freeze protection Stainless steel tank

- Capability to heat water to 180°F (82°C)

- Two Water Wash skids for the site ( 6 base Units and 2 Optional units)

  - One skid can be connected to up to four units, washing one unit at a time (on base storage tank sized for one off-line wash)

1.11 Cooling Water System

- Cooling system temperature regulating valve

- Industrial, off-base cooling water system

- Aluminum fin material with carbon steel tubes

- Corrosion protected cooling skid support structure

- System suitable for:

- Water plus additives coolant

1.12 Starting Systems

- AC motor start

- Rotor turning systems

- Rotor indexing (borescope inspection)

- Non self-sequencing, hydraulic ratchet

2.	Generator

2.1 General Information

- Totally enclosed water-to-air cooled (TEWAC) generator

- Outdoor installation

- 60 Hz generator frequency

- Generator voltage 13.8 kV

- 0.80 power factor (lagging)

- Capability to 0.95 power factor (leading)

- Class "F" armature and rotor insulation

- Class "8" temperature rise, armature and rotor winding

- Generator bearings

- Pedestal bearing support

- Tilting pad bearings

- Roll out bearing capability without removing rotor

- Insulated collector end bearing

- Offline bearing insulation check with isolated rotor

  - Monitoring Devices

    - Two (2) velocity vibration probes at turbine end, one (1) at collector end

    - Provisions for key phasor-generator

    - Permanent flux probe

    - Proximity vibration probes

    - Two probes per bearing at 45° angle

      - Generator Field

        - Direct cooled field

        - Two-pole field

        - Finger type amortissuers

2.2 Generator Gas Coolers

- Cooler assembly shipped separate

- Generator gas cooler configuration

- Two (2) horizontally mounted duplex coolers

- Coolers located on generator roof

- Cooler piping connections on left side as viewed from collector end

- ASME code stamp

- Single wall cooler tubes

- Raised cooler face flanges

- Plate fins

  - Generator gas cooling system characteristics

    - Coolant temperature

    - 20°F approach

    - Generator capacity with one section out of service 80% with Class "F" rise

    - TEMA class C coolers

    - Maximum cooler pressure capability -125 psi Coolant 100% fresh water

    - Fouling factor 0.001

      - Generator gas cooler construction materials

        - 90-10 copper-nickel tubes

        - Carbon steel tube sheets

        - Carbon steel waterbox and coupling flanges with epoxy coating

        - Aluminum cooler tube fins

2.3 Generator Lube Oil Systems and Equipment

          - Bearing lube oil system

- Generator lube oil system integral with turbine

- Pre-fabricated factory fitted lube oil pipe

- Sight flow indicator

- Bearing vapor extraction

- Vapor extractor and motor

- Coalescent mist eliminator

          - Lube oil system piping materials

- Stainless steel lube oil feed pipe Stainless steel lube oil drain pipe

- Welded oil piping

2.4 Generator Grounding Equipment

• Neutral grounding equipment

- Neutral ground transformer and secondary resistor

- Mounted in terminal enclosure

2.5 Generator Temperature Devices

- Stator winding temperature devices

- 100 ohm platinum RTDs (resistance temperature detector)

- Single element RTDs

- Grounded RTDs

- Six (6) stator slot RTDs

- Three (3) extra stator RTDs in separate slots

• Gas path temperature devices

- 100 ohm platinum gas path RTDs

- Dual element temperature sensors

- Two (2) cold gas

- Two (2) hot gas

• Bearing temperature devices

- Chromel alumel (type K) thermocouples

- Dual element temperature sensors

- Two (2) bearing metal temperature sensors per bearing

• Lube oil system temperature devices

        - Chromel alumel (type K) thermocouples

        - Dual element temperature sensors

-   One (1) bearing drain temperature sensor per drain

2.6 Packaging, Enclosures, and Compartments

- Paint and preservation

- Epoxy based primer

- Line-side terminal enclosure

- Terminal enclosure shipped separate

- Collector compartment/enclosure

- Collector compartment/enclosure shipped installed

- Generator Terminal Accessories

- Surge capacitors

• Compartment lighting and outlets

-  AC lighting

- Turbine end

- Collector compartment

-  DC lighting

- Turbine end

- Collector compartment

-  Convenience outlets

- Collector compartment

• Foundation hardware

- Generator alignment fixators

- Generator alignment key(s)

- collector end Generator alignment pin(s) - turbine end

2.7 Electrical Equipment

• Motors

- TEFC motors

- Coated with antifungal material for protection in tropical areas

- Energy saver motors

- Extra severe duty motors

- Cast iron motor housings

• Heaters

- Generator stator heaters

- Generator collector heaters

- Terminal enclosure heaters

2.8 Generator Excitation Systems, Static Com ponents

• EX2100 brushless field excitation regulator

- With permanent magnetic generator (PMG)

- With redundant regulator

2.8.1 Excitation Module Features

• Control/monitor/display through turbine control panel

- Voltage matching in turbine control system

- Power factor controller in turbine control system

- Var controller in turbine control system

- Selection of automatic or manual regulator

- Raise lower of the active regulatorsetpoint

- Enter setpoint command

- Display field amps

- Display field volts

- Display transfer volts

- Redundant Ethernet link to turbine control panel

- Built-in diagnostic display panel

- Automatic voltage regulator (AVR)

- Manual voltage regulator (FVR)

- Automatic and manual bi-directional tracking Reactive current compensation (RCC)

- Volts per hertz limiter (V/Hz LlM)

- Volts per hertz protection (24EX) (Backup to 24G) Over excitation limiter (OEL)

- Offline/online over excitation protection (76EX) Loss of excitation protection (40EX)

- Bridge ac phase unbalance protection (47EX) Under excitation limiter (UEL)

- Generator overvoltage protection (59EX)

- Generator field ground detector trip (64FT)

- Dual VT inputs

- Field over-temperature alarm

- Field ground detector alarm (64FA)

- Exciter phase voltage imbalance (47EX)

- Bridge over-temperature (26EX)

- Field voltage, field current, auto/manual transfer voltage, field temperature,

4-20 ma outputs

- Local operator interface, panel mounted

- Dual source internal bulk power supply

- Millivolt shunt for field

- Surge protection

- Two phase current sensing

- Three phase voltage sensing

- Single pole dc field contactor/bridge

- Power system stabilizer

2.8.2 Performance

          - 0.5 response ratio and 140% VFFL (100"C) ceiling @ Vt = 1.0pu

2.9 Generator Medium Voltage Enclosure

- Metal clad switchgear compartment

- 1S00 MVA/SOOOA at 40"C generator breaker

- Ground switches 2 No.

- Kirk-Key Interlocks

- Breaker rollout

- Dual generator breaker trip coils

- Lightning arresters

- Surge capacitors

- Power leads straight through switchgear compartment

- Roof entrance bushings for outgoing power

- Non-segregated bus duct outgoing power connection

2.10 Generator Current Transformers and Voltage Transformers

• Current transformers (CTs) 1 Amps Secondary

- C400 relaying current transformers (CTs) or 100VA-SP20 rating per IEC 60044, as shown on proposal one-line diagram

- Metering Class - 0.3B-1.8 (ANSI CS7.13) or 0.25 (lEC 60044) as shown on proposal one-line diagram

- Line side CTs

- CT 16,17,18 (miscellaneous functions)

- CT 21, 22, 23 (generator differential relay)

- CT 21A. 22A. 23A (second 87G)

- CT 60,61, 62 (breaker failure relay)

- CT 24, 25, 26 (One set for two units)

- CT 27, 28, 29 (One set for two units)

- Neutral CTs

- CT1 through 9

- CT10,CT11,CT12

• Voltage transformers (VTs)

- Draw out

- VT1, breaker high side

- VT2, generator line side

- VT4, generator line side

2.11 Bus duct

- Non-segregated, per proposal outline drawing

- Partial discharge (PDA) coupler in busduct

- One PDA analyzer for two units

3 Gas Turbine-Generator Controls and Electric Auxiliaries

3.1 Control Cab/Packaged Electric and Electronic Control Compartment (PEECC)

- Weatherproof, climate controlled, base mounted enclosure

- Supplemental wall-mounted air conditioner

3.2 Gas Turbine Control System Panel Features

- Triple Module Redundant (TMR) SPEEDTRONIC Mark VI

- Redundant unit data highway (UDH)

- Auto/manual synchronizing module with synchronizing check function

- Generator stator over temperature alarm (49)

- Isochronous control

- Load limiter

- Purge cycle

- Dead load pickup

- Island mode operation for DLN units

- Customer alarm/trip contact for CRT display

- Additional customer input contacts (digital!, as available

- Additional customer output contacts (digital!, as available

- Provision for analog inputs from customer, as available

- Provision for analog outputs to customer, as available

- Maximum of 12 RTDs inputs for customer use

- Power source selector

- Totalizing fuel flows

- Vibration alarm readout and trip

- Electrical over speed protection

- Constant settable droop

- Power factor calculation and display

- Power factor control

- VAR control

- VARS shedding

- Tie-line VAR control

- Manual set point preselected load

- External load set point. 4-20 mA control

- Airflow calculation and readout

- Inhibit/initiate auto synchronization from remote location

- Time synch

- Time input signal for devices on the power train network is not part of the power train scope of supply

3.3 Local Operator Station

- Commercial grade personal computer

- PC table

- Color monitor

- Table top

- 20 in. LCD monitor or equivalent

- Mouse cursor control

- Printer

- Network color inkjet

- Table top keyboard

- Display in English language

- Unit Ethernet equipment

3.4 Generator Protection Panel

3.4.1 Generator Protection Panel Hardware

- Mounted In PEECC

- DGP with redundant internal power supply

- GE Multilin G60 Generator Management Relay

- Second Generator Protection Relay: GE Multilin G60

- GE Multilin T60 Transformer Management Relay

- Second Transformer Protection Relay: GE Multilin T60 U (One set for two units)

- GE Multilin C60 Breaker Management Relay

- Generator Digital Multimeter

- Lockout relays

- Test switches (per one-line)

- Generator breaker trip switch (52G/CS) and lamps

- Gas auxiliary monitoring panel (GAMP)

- Humidity sensor readout

- Hazardous atmosphere detector readout

- Bently Nevada 3500 vibration monitor

3.4.2 Generator Management Relay (G60)

- Generator overexcitation (24)

- Phase undervoltage (27P)

- Reverse power/anti-motoring (32)

- Loss of excitation (40)

- Current unbalance/negative phase sequence (46)

- Phase time overcurrent (51PV)

- Neutral ground overvoltage(stator Earth Fault Protection) (64G)

- Phase overvoltage (59P)

- Stator ground protection. (third harmonic) (27TN)

- Site data required for setting.

- Generator over frequency (810)

- Generator under frequency (81U)

- Phase Distance (21)

- Out of Step (78)

- Stator differential (87S)

- Voltage transformer fuse failure (VTFF)

3.4.3 Breaker Management Relay (C60)

- Inadvertent energization (50/27)

- Breaker failure with timer (50/62BF)

- Breaker failure (50BF)

- Bus ground detection (59BN)

- Voltage transformer fuse failure (VTFF)

3.4.4 Transformer Management Relay (T60)

- Restraints as per one line diagram

- Unit differential (87U) (One for two Units)

- Transformer differential (87T)

- Transformer neutral over current (51TN)

- Latch output contact for transformer fault pressure (63PTX)

3.4.5 Generator Protection Discrete Relays

Note: Refer to proposal one-line diagram for complete discrete relay scope

- Generator protection lock-out relay (86G1A)

- Generator protection lock-out relay (86G2A)

- Generator protection lock-out relay (86G1B)

- Generator protection lock-out relay (86G2B)

- Inadvertent energization lock-out relay (86IE)

- Breaker failure lockout relay (86BF)

- Unit differential lock-out relay (86U) (One for two units)

- Transformer differential lock-out Relay (86T1)

- Transformer differential lock-out Relay (86T2 ) (By other unit)

- Breaker Cross tripping dual breaker trip coils (94GB-1,2)

- Breaker status auxiliary relay (52GX-l)

- Second breaker synchronization for series breaker ~ Breaker/VT selection switch (83LBSX-1,2,3)

- Dead bus (dead load) breaker closure

-  Integral to C60 Breaker Management Relay

          - Synchronization voltage check

- Integral to C60 Breaker Management Relay

- Redundant to turbine control system synch check, integrated with turbine control synchronization system.

3.4.6 Features Integrated Into Gas Turbine Control System

- Gas turbine control system with speed matching, synchronization and check

- Manual synchronization displayed on gas turbine control system operator interface

- Auto/manual synchronizing module with generator voltage matching displayed on gas turbine control system operator interface

- Load control in gas turbine control system

- Temperature indication for generator RTDs

3.4.7 Generator Protection Panel Metering

          - Generator digital multimeter (Nexus) Generator volts

            - Generator Amps: Phase 1,2,3 and Neutral

            - Generator Watts

            - Generator VARs

            - Generator frequency

            - Generator VA

            - Generator power factor

            - MWH ~ Generator Watt-Hours MVAH

            - Generator VA-Hours

            - Generator VAR-Hours

              - Bus digital multimeter

            - Bus volts

            - Bus amps

            - Bus frequency

              - Auxiliary transformer digital multimeter VM - Auxiliary transformer volts

                - AM - Auxiliary transformer Amps: Phase 1.2.3 and Neutral MW

                - Auxiliary transformer Megawatts

                - MVAR - Auxiliary transformer MegaVARs

                - FM - Auxiliary transformer frequency

                - MVA - Auxiliary transformer MVA

                - PF - Auxiliary transformer power factor

                - MWH - Auxiliary transformer MegaWatt Hours MVAH

                - AuxiHary transformer MVA Hours

• Revenue class metering for bus and auxiliary transformer

3.4.8 Generator Protection Panel Outputs

- Nexus meter with KYZ pulse output module (field configurable)

- Generator wattlVAR transducer 4-20 mA output for input to TCP (96GG-ll)

- Generator TCP/droop control transducer 4-20 mA output (96GW-ll)

•   Nexus meter with three modules of 4 configurable channels of 4-20 mA signals

- Generator wattlVAR 4-20mA output (96GG-21

- Generator power factor 4-20 mA output {96GP-ll

- Generator VAR 4-20 mA output (96GR-ll

- Generator volts 4-20 mA output (96GV-1. 2, 31

- Generator frequency 4-20 mA output {96GF-ll

- Watts 4-20 mA output (96GW-ll

- Amps 1 PH 4-20 mA output {96GA-1. 2, 31

3.5 Generator Protection

• Generator electrical protection equipment

-  Ground brush rigging

3.6 Batteries and Accessories

- NiCad battery

- Two Three phase battery charger

- Battery and charger mounted in the control compartment

- 125V DC Panel

3.7 Motor Control Center

- MCC mounted in control compartment

- Silver plated copper bus work

- 65 kA bracing

3.8 Remote Control and Monitoring Systems

- HMI Ethernet communications link using GSM protocol

- Site Ethernet equipment in central control room

- Remote HMI. multi-unit control - Two per site

- Commercial grade personal computer

- Color monitor - Table top

- 20 in. LCD monitor

- Mouse cursor control

- Table top keyboard • Printer

Color laser jet network printer - One

3.9 Rotor, Bearing and Performance Monitoring Systems

• Performance monitoring systems

- Air flow measurement sensors wired to gas turbine control system

- Gas turbine performance monitoring calculations in operator interface

- Generator performance curves on operator interface

- Vibration sensors

- Velocity vibration sensors

- Proximity vibration sensors

- GE proximity vibration sensor monitoring

- In the SPEEDTRONIC Mark VI panel

- HMI display

- Bearing thermocouples

- Bearing drain thermocouples

- Bearing metal thermocouples

- Borescope access holes

• 	Bently Nevada System 1 TGVAS

- Software for gas turbine/generator(s)

3.10 Motor Features

- TEFC motors lessthan or equal to 200 hp

- Coated with antifungal material for protection in tropical areas

- High ambient motor insulation

- Energy saver motors

- Extra severe duty motors

- Cast iron motor housings

- All redundant motors to be lead/lag

- Motor heaters connected to AC power, for all motors greater than 1 hp

- WP motors >200 hp

- NEMA Class F insulation, Class B temperature rise

- Motor service factor 1.15 at 40°C

- WP starting motor

4 Services

- Clearance tools

- Fuel nozzle staking tool Combustion liner tool

- Bearing and coupling disassembly fixture

- Turbine rotor lifting beam (one for every four units)

- Basic maintenance tools and cart (one set per site)

- Hydraulic tools for removal of casing bolts (one set per site)

- Borescope inspection kit (one per site)

- Generator maintenance tools (1 set per site) - Rotor lifting slings

- Rotor removal equipment including shoes, pans, pulling devices

              - Installation equipment

Trunions for generator

- On permanent basis Foundation/installation washer and shim packs

- Turbine flush piping and consumables

- One set of piping for up to four units

- One set of consumables per unit

• Electrical System Studies

- Power system stabilizer tuning study

- Power system stabilizer (PSS) site testing

Commercial

Price

Equipment

Our Company is offering these units, where there are for a price of US$32,000,000 each or a total price for (4) units of US$128,000,000.

ALL EQUIPMENT IS SUBJECT TO PREVIOUS SALE

TURNKEY SERVICES

In addition, we are pleased to also provide a budgetary proposal

for the required balance of plant equipment,  installation,

Startup and commissioning of the plant. This would include providing

total turnkey construction services as well as startup and

Commissioning of all equipment provided see Attachment 2

Scope of Work

Attached is our Technical Scope Document (TSD) which describes in detail, the scope of supply we have included in this proposal. Based on our understanding of the site requirements, our scope includes everything required to complete the construction of the plant at the Plant site. This includes but is not necessarily limited to the following:

• All Civil Works required for the construction and installation of the plant.

• All Mechanical Works required to erect and assemble the equipment including piping,

structural supports, etc. as completely described in the TSD.

• All Electrical Works required to install the interconnect control cabling, power cabling,

testing and commissioning of the plant.

• All Project Management required coordinating the work and maintaining the Project

Schedule as defined in the TSD.

• All Engineering required to design the plant including both conceptual and detailed.

• All startup, commissioning and testing of the plant to prove successful operation prior to putting the plant into commercial operation.

Schedule

Frame 7EA projects, we can complete the construction of this plant in (10) months from

Contract execution and receipt of down payment.

Price

The firm fixed price for the turnkey construction of the plant as described in the attached TSD is

US$ 124,000,000.00

Payment

30% non-refundable payment due immediately

70% on a letter of credit

The letter of credit will be irrevocable and issued by a U.S. bank and on terms acceptable to Our Company.  The terms of the letter of credit will require full payment of the principal amount no later than 15 business days from the date of this offer.  The purchase price shall be net of all banking charges for issuing the letter of credit.

Availability

These units are currently available for immediate purchase.  transport to the nearest port can be completed in less than 30 days (Optional) from date of contract and receipt of payment.

.

Validity

This proposal is valid for a period on 20 days.

Typical Performance Characteristic Curves

| Simple Cycle Performance | 60Hz Power Generation | Mechanical Drive |
| --- | --- | --- |
| Output | 85.4 MW | 115630 hp |
| Heat Rate | 10420 Btu/kWh (10991 kJ/kWh) | 9795 Btu/shp-hr |
| Pressure Ratio | 12.6:1 | 11.9:1 |
| Mass Flow | 643 lb/sec (292 kg/sec) | 659 lb/sec (299 kg/sec) |
| Turbine Speed | 3600 rpm | 3600 rpm |
| Exhaust Temperature | 998°F (537°C) | 998°F (537°C) |
| Model Designation | PG7121EA | M7121EA |

| Combined Cycle Performance | 60Hz (S109EA) | 60Hz (S207EA) |
| --- | --- | --- |
| Net Plant Output | 130.2 MW | 263.6 MW |
| Heat Rate | 6800 Btu/kWh (7175 kJ/kWh) | 6700 Btu/kWh (7070 kJ/kWh) |
| Net Plant Efficiency | 50.2% | 50.9% |
| GT Number & Type | 1 x MS7001EA | 2 x MS7001EA |

TYPICAL DRAWINGS

Section 2.0 Scope of Supply and Technical Schedules

Section 2.0	Scope of Work and Equipment List

The Scope of Work for the proposed project is generally outlined as follows:

Major Equipment – Owner will supply Four (4) GE Model 7121 Frame 7EA Gas Turbine Generators with auxiliaries.  Two (2) 13.8KV to 230KV Generator Step Up Transformer (GSU), 230 KV Breakers and 230KV Disconnect Switch.

Contractor will provide the Balance of Plant which includes the following outlined list of major equipment and deliver them to site:

- Two (2) 7,000 cu meter DFO tank

- Two (2) 1,000 cu meter DFO tank

- DFO transfer and forwarding pumps with fuel filters

- Demin transfer and forwarding pumps with filters

- Demin Fiberglass Storage Tanks

- Oily Water Separator

- Instrument and Service Air Compressor

- Office and Control Building

- DCS System

- 230 KV Expansion Bay to existing plant substation with 3 ea SF6 Breakers and 6 ea Disconnects

- 230 KV Transmission Line from new 7EA Plant to existing 230 KV Substation

The contractor will design and install the facility as described in the following sections of this document.  The design will include the necessary Civil, Foundations, Structural, Mechanical, Electrical, Instrumentation, and Control System to install the above listed equipment.

Balance of Plant – The contractor proposes to furnish and install the Balance of Plant equipment and materials, which comprises the following:

- Complete design of the facility including civil, foundations, structural, buildings, mechanical, electrical, instrumentation and control.

- Contractor will provide site preparation, material and labor for concrete foundations, piers and plant gravel.

- Contractor will provide Installation of the complete Power Plant with the inter-ties as described later in this document.

- Contractor will provide mechanical installation of the various items of equipment with the associated inter-ties of treated water, natural gas, liquid fuel, waste water, and Fire Water.

- Contractor will provide installation of the plant including the 230 KV high voltage GSU, 230KV SF6 breaker, 230KV disconnects, dead end tower, transmission line with relays, poles to Owners substation, grounding, lightning protection, and cathodic protection.

Contractor will provide and install 230 KV Expansion to Owners’ 230 KV Subs

2.1 MECHANICAL SYSTEMS

2.1.1 Codes and Standards

2.1.2 Compressed Air System

2.1.3 Fire Water System

2.1.4 Well and Services Water System

2.1.5 Oily Water Separator System

2.1.6 Piping

2.1.7 Cathodic Protection

2.2 CIVIL AND STRUCTURAL WORKS

2.2.1 Site Preparation

2.2.2 Drainage and Sanitary Sewers

2.2.3 Roads

2.2.4 Concrete, Foundations, and Structural Steel

2.2.5 Buildings and Structures

2.2.6 Plant Site Security Wall

2.3 ELECTRICAL SYSTEMS

2.3.1 Electrical System

2.3.2 Switchyard

2.3.3 Transformers

2.3.4 Non Segregated-Phase Bus

2.3.5 Deleted

2.3.6 Low Voltage Unit Substation

2.3.7 Motor Control Centers

2.3.8 Emergency Diesel Generator

2.4 INSTRUMENTATION AND CONTROLS

2.4.1 Gas Turbine Control System

2.4.2 Distributed Digital Control System

2.4.3 Satellite Control Systems (PLC-Based Control)

2.4.4 Continuous Emissions Monitoring System

2.4.5 Security System

2.5 LIST OF EQUIPMENT AND SERVICES

2.1 Mechanical Systems

The following sections outline the Scope of Supply and technical schedules along with a list of equipment and services to be furnished.

2.1.1 Codes and Standards

The mechanical systems will be provided according to the codes and standards outlined in section 4 of the plant specifications.

2.1.2 Compressed Air System

- The Compressed air system will consist of two (2) each Ingersoll-Rand Model

UP6-20-125 electric motor driven single stage rotary screw compressors rated at

80 scfm at 125 psig. Each compressor is complete with starter, inlet air filter and

Discharge coalescing filter with an automatic drain (Ingersoll-Rand Model

IRGP123). The accumulator is a 120 gallon horizontal tank designed at 150

psig.

- Air dryer - Two (2) each Ingersoll-Rand heatless air dryers are provided to

reduce the dew point of the air to -40°F (-40°C). The dryers are a model TZM88

heatless modular desiccant dryer with a capacity of 88 scfm based on 100 psig

and 100 °F. Each dryer will be equipped with a final dust filter, Ingersoll-Rand

model IRDP123. (Reference Section 8.1 for specification.)

- Instrument air will be piped and distributed as required by the specifications.

2.1.3 Fire Water System

A fire water system will be provided for fire suppression at the facility. The

system will consist of an 180,000 gallon fire water storage tank, two (2) each,

250 HP, 2,000 gpm @ 150 psig UL approved electric driven horizontal split case

fire pump complete with UL/FM approved fire pump controller, relief valves and

one (1) each vertical jockey pump, 5 HP, 460V, 3 phase motor, with automatic

jockey pump controller. The system will include a 10 inch HDPE fire water loop

serving each gas turbine. The loop will include post indicator valves, six (6)

hydrants and six (6) hydrant/monitor units. Each firewater pump will be

independently piped to the firewater tank. The system will be designed and

supplied by Dooley Tackaberry. (Reference Section 8.2 for specification.).

2.1.4 Well and Services Water System

1. Raw water for the facility will be supplied by two (2) water wells to be drilled at

the facility. Each water well will be furnished with a 100 gpm sub-surface pump

and will pump water to the 180,000 gallon fire water tank. The water wells to be

drilled by the Owner.

2. Service water for the facility will be pumped from the firewater tank from an

elevated suction location on the tank to insure adequate storage for fire water.

The pumping station will include two (2) 100% Goulds series 3196 pumps and a

pressurizing tank. The pumps will be controlled on pressure to maintain a

constant pressure on the service water system. Service water outlets will be

located throughout the facility.

2.1.5 Oily Water System

1. Oily Water Separator – Oily water will be treated for separation of oil from skid

drains by a Highland Tank and Manufacturing, Model R-HTC 2000 corrugated

parallel plate oil-water separator having a gravity flow rate capacity of 150

gallons per minute and producing a free oil effluent quality of 10 ppm. Drains will

be piped from all containment areas including the gas turbine skids, generator

step up transformers and other drain locations with a potential for oil

containment. These drains will be piped to a common header and routed to the

oily water separator. (Reference Section 8.3 for specification.)

2. Waste Oil Storage – Waste oil from the oily water separator will be pumped to a

1000 gallon holding tank with facilities to pump the oil to drums for disposal.

3. Waste Water Storage – Waste water from the oily water separator will be

collected in a buried 1000 gallon tank that also collects the water from the facility

drains. Water from this tank will be discharged into a leaching field.

2.1.6 Piping

1. Piping, Piping installation and Piping Insulation – The piping for the facility will be

fabricated and installed per the Power and Boiler Piping Code, ANSI B31.1. The

fuel gas piping shall be installed in accordance with ANSI B31.1 Power Piping.

All pipe welds to be done by individuals certified to ASME Section IX. Piping

materials will be provided according to the piping specifications.

Fuel gas, oil, water, and hydraulic pipe welds will also be performed in

accordance with ASME. Acceptance criteria will be indicated in ANSI B 31.1.

All underground carbon steel piping shall be wrapped or coated and cathodically

protected. Carbon steel piping shall be jeeped prior to cover. Cathodic

protection will be provided by the passive method which utilizes protective

anodes and provides inspection coupons at strategic locations to monitor for

potential corrosion.

All low pressure piping for water service will be carbon steel or fabricated from

fiberglass reinforced plastic (FRP) pipe to meet plant corrosion requirements.

2. Fire Protection Piping – The fire system piping will include a HDPE piping fire

loop, Isolation valves, hydrants and monitors as required.

2.1.7 Cathodic Protection System

1. Cathodic Protection System – The system will be installed to control the

electrochemical corrosion on the exterior surfaces of underground carbon steel,

stainless steel. The bottoms of soil or sand pad mounted steel tanks, the exterior

surfaces of underground ductile or cast iron pipe will be installed with Cathodic

protection will be CP protected as well.

2.2 Civil / Structural

2.2.1 Site Preparation

1. Site Preparation – The Owner will perform removal as required of any existing

buildings and structures on the project site. The Contractor will provide all rough

and final grading. Grades will be established to minimize the amount of

earthwork required to construct the facilities. A substantial quantity of “cut and

fill” will be required. A computer program was utilized by the Contractor to

ascertain the actual quantity based on the topographical drawing furnished by the

Owner. All areas disturbed during construction shall be graded to a smooth

surface and covered with appropriate material as conditions require. Finish

grading shall be performed to conform to the finished design elevations for

surface drainage and to prepare the areas to receive the specified surface

finishes.

2.2.2 Drainage and Sanitary Sewers

1. Storm Water Drainage System – The Contractor will provide a storm water

drainage for all rainwater on the site. Storm water will be managed through use

of swales, ditches, culverts and site grading to drainage locations within the

facility. All rain water collected form active areas that can potentially be contaminated by

oil shall be routed through an oil/water separator.

2. Sewer System – The Contractor will install an underground septic tank with an

underground lateral drainage field. The sanitary sewer pipe from the toilets and

kitchen facilities will tie into the underground sanitary sewer system which is

shown on the plot plan. The drainage areas, channels, and sewer pipe is shown

as follows:

Surface drainage areas, m2

Roof &Equip.	Paved		Unpaved 	Total

Areas

General Svcs Bldg 	 473				  		    473

Firewater Pump Bldg 	   65				    		      65

Parking Lot 		 		130		  		    130

Roadways	           			7248 		544.19		  7792.19

2.2.3 Roads

1. The main access road will consist of 8” of crushed rock with 4” of fine gravel.

The gravel will be compacted and rolled to provide a smooth finish.

2. The low usage road will consist of 6” of crushed rock with 3” of fine gravel. The

gravel will be compacted and rolled.

3. Paved parking, building entries, sidewalks, and turbine removal pads will consist

of 6” of crushed rock with 4” of asphalt concrete.

2.2.4 Concrete, Foundations, and Structural Steel

1. Concrete – Contractor is to provide concrete foundations in accordance with the

following section. Contractor to provide design and anchor bolts.

(1) Codes

Design of structural concrete will be in accordance with the American concrete

Institute (ACI) – “Building Code Requirements for Structural Concrete,” ACI 318,

latest edition, and the UBC Code.

(2) Materials

Minimum concrete strength classes from various structures will be as stated.

Reinforcing bars will conform to ASTM a615, Grade C.

conforming to ASTM A82. Wires gauge No. 11 or smaller shall be galvanized.

Spiral reinforcement will conform to ASTM A82.

(3) Placing of Concrete

Contractor will adhere to good and accepted practices in placing concrete

generally as outlined:

Placing Concrete:

• Conform to ACI

• Place within 60 minutes after mixing, except site weather conditions may

extend the period to 90 minutes (maximum).

• Place in horizontal layers not exceeding 20 inches.

• Vibrate to produce solid mass without honeycomb or surface air bubbles.

Curing Concrete:

• Unless specified to be moist cured, cure with liquid membrane-forming

compound conforming to ASTM C309, Type I. Apply according to

manufacturers recommendations.

• Apply curing compound to all exposed surfaces immediately after

removing from or after finishing concrete.

• Keep formwork wet until stripped.

• Moist curing shall be used for surfaces that will receive a separate finish

or coating.

(4) Testing

Contractor will test concrete and make test cylinders conforming to ASTM C31,

C143, and C172. Contractor will make a minimum of four test cylinders for each

150 cubic yards of concrete or fraction thereof, or every 5000 square feet of

surface area for slabs and walls, for each day concrete is placed.

(5) Equipment Foundations

The types of foundations and allowable bearing values for soil and rock, will be

as recommended by Contractor’s Geotechnical Engineer in accordance with the

Contractor-provided final geotechnical report.

Design of foundations will be in accordance with ACI 318 and the UBC.

(6) Containment Basins

Containment basins will be provided around transformers and other equipment,

which contain oil in case of rupture, spill, or leak. The basins shall be designed

in accordance with the NFPA 850 and Factory Manual recommendations.

2. Structural Steel

Contractor will furnish and install necessary structural steel including:

1) Piping racks and supports

2) Cable Tray supports

3) Walkways and platforms

4) Grating and supports

Pipe racks and cable tray supports may be a combination of concrete and

structural steel. Structural design will be in accordance with the applicable codes

and standards.

(1) Wind and Seismic Loads

All structures, tanks, equipment anchorage, and piping and cable tray supports

will be designed and installed to resist code-specified wind and seismic loads.

Pipe supports shall also be designed for reactions due to pipe stress analyses

and support degree of fixity.

(2) Codes

Design of structural and miscellaneous steel shall be in accordance with the

1997 Uniform Building Code (UBC), the American Institute of Steel Construction

(AISC) “Specification for Structural Steel Buildings,” latest edition and other

applicable Codes and Standards.

2.2.5 Buildings and Sheds

1. General Services Building

The general services building is made up of two separate areas:

Control office – The control and office portion of the building will be 15.5m wide x

15.7m long x 3.65m high. This portion will house the following:

• Control Room

• Three Offices

• Conference Room

• Reception

• Kitchen

• Restrooms

• Storage Room

The control office portion will be masonry walls with concrete floors covered with

vinyl tile. The ceilings will be acoustical tile with fluorescent lighting. The

building will be insulated, air conditioned and heated. It will be equipped with

metal doors and windows.

The warehouse portion of the building will be 15.5m wide x 15.7m long x 6m

high. The warehouse portion will have masonry walls with concrete floors. The

building will be insulated, heated and ventilated. The lighting will be fluorescent.

The warehouse will be equipped with an overhead metal door and two metal

personnel doors.

2. Fire Water Pump and Electrical Building

The fire water building will be 8m wide x 18m long x 6m high. The building will

have masonry walls with concrete floors. The building will be insulated, heated,

and ventilated. The lighting will be fluorescent. The building will be equipped

with two overhead metal doors and three personnel doors.

3. Guard House

The guard house will be 3.5m wide x 4m long x 2.44m high. The building will

have masonry walls with concrete floors. The building will be insulated, air

conditioned, and heated. The lighting will be fluorescent. The building will be

equipped with metal personnel door and windows.

4. Emergency Generator Shed

The emergency generator shed will be a prefabricated metal shed 4m wide x 8m

long x 3.6m high. The shed will have open side walls, concrete floors, and

fluorescent lighting.

2.2.6 Plant Site Security Wall

The plant will have a masonry / concrete security wall built around the perimeter in accordance

with the drawing furnished by Owner. It will have guard towers at various locations as shown on

the drawings. The wall will be in accordance with the specifications as furnished by the Owner.

2.3 Electrical Systems

2.3.1 Electrical System

2.3.1.1 AC Distribution System

The AC Distribution system including a description of starting, stopping and

emergency operation will be provided by the owner.

2.3.1.2 Control System UPS

A 7KVA Uninterruptible Power Supplies (UPS) will provide power for a limited

period of time to DCS equipment as backup to the source power. This UPS is

sized to have about 50% spare capacity. The 7KVA UPS will supply 30 Min. of

runtime at half load.

The UPS system will consist of a hard wired 208/120VAC 60 Hz input with a

bypass switch to provide a 120VAC 60Hz single phase ± 3% regulated output.

There is a RS-232 communications port for alarm and setup in addition to dry

contacts that can be used for alarms. Lighting, surge, and noise protection is

provided internal to the unit.

2.3.1.3 DC Supply System

The DC system for the Gas Turbines and generator breaker is supplied by the

owner with the GE packaged gas turbines. A 125 VDC battery and charger

system for the substation breakers and protective relays will be supplied by

Contractor.

2.3.1.4 Power Station Grounding

Grounding and Lightning Protection – The plant and substation will be equipped

with grounding system that is solidly tied into all plant equipment.

Ground conductors shall be sized in accordance with the NEC; below grade

ground grid shall be a minimum of #4/0 AWG bare copper. Grounded neutral

conductors shall be protected by a non-metallic conduit, where conductors run

exposed above grade.

2.3.1.5 Protection and Metering

(1) Metering:

Two (2) sets (one on each outgoing transmission line) Schweitzer Model SEL

734 Revenue and Power Quality Metering for Utility Applications

(2) Relays:

Two (2) (one on each transmission line) Schweitzer Model 311B Line Relay

Two (2) (one on each GSU) Transformer Differential Relay is supplied as part of

the GE package and will be connected into the system.

2.3.1.6 Mimic Panel

Control of the main electrical distribution substation breakers will be available

from the DCS system and from a mimic control panel located in the main control

room. The mimic panel will be hardwired to control the substation breakers

independent of the DCS system. Breaker status indication will be via pilot lights.

Mimic display will mimic the one line diagram. The manual disconnect switches

will be modeled using a display that operator may manually set the open or

closed status on the mimic display. Layout of the mimic panel is shown on

drawing 60-041.

2.3.1.7 Cabling and Raceway

Cable Tray - The cable tray shall provide support to electrical cable which is

routed throughout the plant either directly to equipment or to areas of

concentrated electrical loads.

All cable trays shall be of ladder type construction with a rung spacing of 9 inches

maximum, nominal depths of 4 to 6 inches, and various widths as required. The

cable tray shall be aluminum. There shall be a maximum spacing of 10 feet

between cable tray supports, except fittings (elbows, tees, etc.), which shall be

supported in accordance with NEMA standards.

Cable tray fittings shall have a radius equal to or greater than the minimum

bending radius of the cables they contain.

Individual tray systems shall be established for the following services:

• 13.8 KV

• 5 KV – 480V Power (Separate Trays or Dividers)

• Control Cables, Special noise-sensitive circuits and instrumentation

cables, (Separate trays, drivers or conduit in tray)

Further division shall be provided where required by individual equipment

manufacturers, particularly the GTG.

Conduit shall be used to extend circuits from cable tray, cable trenches,

manholes, or wireways to equipment or cabinets, and for circuits between

equipment and cabinets.

Conduit shall be used to protect conductors to individual devices, in hazardous

areas, and where the quantity of cable does not economically justify the use of

cable tray. All conduits shall be RGS.

Raceway for communications, lighting, and receptacles, and installed in finished,

indoor, non-hazardous locations, may be EMT.

PVC conduit shall be used for roadway lighting, duct banks, and for some below

grade runs. Type EB PVC conduit shall be concrete encased. Schedule 40 PVC

conduit shall be concrete encased or direct buried.

Rigid galvanized steel (RGS) shall be utilized for underground service, duct bank

risers and bends, and elsewhere as specified.

Duct Bank - Duct bank shall be utilized when other types of raceway are not

practical due to interferences with equipment or maintenance access and to

route cables to remote areas.

All underground duct banks shall consist of PVC or RGS conduit encased in

concrete. Reinforcing shall be furnished under all roadways, driveways, and as

determined by the Contractor during detailed design. The nominal diameter of

the ducts shall be no less than 2 inches and no greater than 5 inches.

Galvanized steel conduit shall be installed where required for digital and analog

low-level circuits requiring noise immunity from adjacent power circuits.

2.3.1.8 Communication Systems

Telephone and Paging – Contractor will not provide phone or paging systems as

part of this contract.

2.3.1.9 Lighting System

(1) Area Lighting

Contractor will provide the plant and substation area lighting as described below.

• Exterior area lighting will consist of six (12) 40 ft. metal poles with three (3)

400-watt metal-halide lights equal to that manufactured by GE or Appleton.

• Interior lighting in the Utility/Control Building will be fluorescent fixtures. They

shall be rapid start lamps. Fluorescent lamps shall be warm white or daylight

color.

• All other building lighting will be of vapor-type incandescent lights.

(2) Building Lighting

Indoor illumination shall be provided in accordance with the current minimum

average maintained foot-candle levels as published by the Illuminating

Engineering Society.

The emergency lighting system shall be powered from battery packs.

Exterior building lighting and wall-mounted type fixtures shall be high pressure

sodium lamps with integral ballast.

All lighting fixtures shall be energy efficient. Fixtures shall be installed per NEC.

All lighting fixtures shall be UL listed and stamped.

All lamps shall be of the proper type, wattage and voltage rating for their

respective fixtures. They shall be supplied new, and installed in the fixtures just

prior to the completion of the project. Fluorescent lamps shall be cool-white,

rapid start.

2.3.2 Switchyard

Reference drawings:

10-001 Sheet 1 General Arrangement Plant

10-001 Sheet 2 General Arrangement Substation

60-010 Sheet 1 Substation One Line Diagram

The substation for the Electroandes Sur Chico Project is rated 220 KV. It is a “low profile”design, double bus arrangement, to accommodate two gas turbine generators and two outgoing.

transmission line connections. Design includes provisions for two future outgoing lines and one future steam turbine generator. Disconnect switches are provided to select one of the main buses for each node of the substation. SF6 circuit breakers are provided for each Generator Step Up Transformer (GSU) and for each outgoing transmission line. Capactive coupled  Voltage Transformers (CVT) and Current Transformers (CT) are provided for revenue metering on the outgoing lines and for relaying. Impedance relays are provided for transmission lines, bus differential relays for the busses and transformers, and sync check for the transformer breakers (Impedance relays can be provided with sync check features and with transfer trip feature if desired for the outgoing transmission line breakers). A wave trap is provided on each of the two transmission line connections to allow for Utility data transmission. All busses are four

(4) inch aluminum ALCOA 6063-T6, schedule 80 pipe installed on station post insulators. Steel will be hot dipped galvanized. Connections and terminations will be bolted style, Sefcor or equal. Bus spacing and clearances are in accordance with NEMA SG-6-1995 for outdoor electrical substation. Two (2) dead end towers will be provided for the utility line connections for the distribution into the existing transmission line network. Data from the substation will be sent to the power plant DCS which will include the breaker control and status, KW, Vars, amps, volts on each line and circuit. A local small control house will be provided to contain protective relays, metering, DCS interface, 125 VDC battery and charger, space for owners RTU (if provided).

2.3.3 Transformers

Generator Step Up Transformers (GSU) will be manufactured by Siemens or similar.

Auxiliary Transformers will be manufactured by Areva or similar Preliminary data for each is given below.

a 	Quantity					4		      4

b 	MVA 					    75/100/125                    4

c	Voltage pri/sec 			      220/13.8 		 13.8/400

d	 Impedance %; base MVA 	                     804		     6.0

e 	Number of phases			           3 		      3

f 	Number of windings 			           2 	                  2

g 	Method of Neutral Grounding 	       Solid 	               Solid

h 	Taps (No-Load) 8 4

• 	Steps: Plus/minus 		               8 x 1.25                   4 x 2.5

i 	Cooling System Type 	                              Fan                       None

j 	Maximum Total Losses, kW

(Exclusive of Auxiliary Power

To Cooling Equipment):

2.3.4 Non-Segregated-Phase Bus Duct

The connection from the GE Packaged generator breaker to the Generator Step Up

Transformer (GSU) will be by a non segregated-phase bus, metal enclosed, duct rated at 5000 amps, 15 KV. The conductors will be copper. Connection to the GSU will be by flexible connectors. The duct will be outdoor, ventilated and be equal to Calvert Company.

2.3.5 Not Used

This section was intentionally left blank.

2.3.6 Low Voltage Unit Substation

The 4160 Volt and 480 Volt substations are supplied as part of the GE package with the gas turbine generator.

2.3.7 Motor Control Centers

The MCC’s for the gas turbine auxiliaries are supplied as part of the GE package. The BOP MCC as supplied by Wood Group will be manufactured by GE and be similar to those for the gas turbines. Typical features are supplied below for reference.

a Quantity 1

b Type Designation NEMA 1

c Rated Voltage 480V

d Bus bracing (50,000 A Min) 62,000

e Type of:

• Circuit breakers Thermal Magnetic

• Contactors Electric

f Continuous Current Rating

of Buses, Size and Material

• Rated current 600A

• Material Copper

g Accessories Standard ANSI

2.3.8 Emergency Diesel Generator

Emergency power for plant stand by power is furnished by a 250 KW Caterpillar diesel fueled generator set. The generator is sized to provide minimum power for lighting and maintenance of the facility. Specifications for a similar generator set are included in Section 8, Equipment Specifications.

2.4 Instrumentation and Controls

2.4.1 Gas Turbine Control Panels

The gas turbine control panels are included with the GE VII gas turbine packages furnished by the Owner. The turbine control panels are located in the PEEC control modules associated with each gas turbine.

2.4.2 Plant Distributive Control System

The plant DCS system is provided and further described in Section 8.11. The DCS connects the two gas turbine control panels and balance of plant equipment to the central PLC computer based control system.

2.4.3 Plant Satellite Control System

The satellite control system is part of the plant DCS system and described in Section 8.11.

2.4.4 Plant Security System

1. The plant will be enclosed by a masonry concrete wall as described in 2.2.6. The

entry will be secured by a twenty (20) foot wide electrically operated gate that is

controlled at the control room and accessible via a local key pad to allow workers

entry via operation of the key pad at the gate.

2. A color TV camera and intercom system will be located at the gate. A TV monitor

will be located in the control room that will allow an operator to view visitors and

to operate the gate remotely for those desiring entry. Also included are two (2)

hand held remote controls which will operate the gate.

The system will be comprised of the following:

1 Aiphone 2 station Intercom system

1 Speco CVC-770 Color Board Camera

1 Panasonic WVCK1420 14” color Monitor

RG59 95% copper shield coax up to 1000ft

1 Linear Programmable Keypad

1 Vertical Pivot Lift Gate Model 2002 20 foot long X 6 foot tall square picket

wrought iron, operates on commercial 12 Volt operator, includes auto reverse,

time to close module, safety loop detector and Omron infra-red safety beam,

Miller safety edge, free exit for power failure, trickle charger, radio receiver and

two hand held remotes

- Exceptions and Clarifications

- For clarification of the project the following exceptions and assumptions are

stated:

- The Scope of Supply of this document does not include the following

outlined items:

- Real estate property on which the Power Project is to be sited.

- Local, state, and/or government taxes associated with the Owner’s corporations.

- Local, state, and/or government taxes associated with the Contractor furnished equipment.

- Any site environmental cleanup.

- Environmental permits. (Note: Contractor will assist in obtaining all permits where applicable.)

- Local county or state construction permit. (Contractor will assist in obtaining.)

- Fuel gas for blow down, flushing, commissioning, start-up, and operation.

- Supply of Owner furnished items as outlined in Section 2.0 of this Proposal.

- Operating spares. (Contractor will submit a list of recommended spare parts.)

This proposal is also based on the following assumptions:

- Owner to supply to Contractor or receive the items outlined in Section 2.16

- Owner to supply to Contractor all the exhaust

- Owner will provide all authority required to make the proposed utility interconnects.

- Owner will provide complete site for use as described in the TSD and associated drawings.

- Contractor to furnish and install “first fill” lubricants and chemicals for the plant.

- Contractor will provide soil borings to be utilized for site design.

- Owner to provide site survey as necessary

- Owner to provide custody transfer fuel metering and interconnect point at sit boundary as shown on drawings.

- Owner to provide fuel for plant commissioning and start-up.

- Owner to provide rights-of-way for roadways, entrances, pipeline, and transmission line to the Power Project.

- Performance guarantees, administration of warranty conditions will be discussed and agreed upon and inserted into the appropriate sections of this document at contract signing.

- Contractor will transfer software licenses to the Owner at the completion of the project. This will include the license documentation passwords and keys. It will be the responsibility of the owner to maintain these licensing articles for the time when the software needs to be reinstalled.

- The Contractor supplied DCS shall allow for system expansion through the addition of controllers, operator stations in the control panels, process I/O systems and / or process controllers while the equipment associated with the controller/computer are in manual mode. Modifications can be preformed while the Power Plant is operational and the equipment in question is in manual mode. Proper safety precautions must be adhered to. “Tag out” procedures may be required.

- Operator stations in the control room can be expanded while in remote mode and the Power Plant is operational.

- Various vendor supplied PLCs for the major equipment will use either function block or ladder logic programming. The Balance of Plant PLC will use ladder logic programming. The Gas Turbines will utilize a GE designed control system.